## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2405-3_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2405-3_0_3_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_2405-3_0_3_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_2405-3_0_3_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_2405-3_0_3_node_13 | 0.4 | n |  | TRUE
5 | bus_LV_2405-3_0_3_node_10 | 0.4 | n |  | TRUE
6 | bus_LV_2405-3_0_3_node_60 | 0.4 | n |  | TRUE
7 | bus_LV_2405-3_0_3_node_24 | 0.4 | n |  | TRUE
8 | bus_LV_2405-3_0_3_node_32 | 0.4 | n |  | TRUE
9 | bus_LV_2405-3_0_3_node_11 | 0.4 | n |  | TRUE
10 | bus_LV_2405-3_0_3_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_2405-3_0_3_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_2405-3_0_3_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_2405-3_0_3_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_2405-3_0_3_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_2405-3_0_3_node_46 | 0.4 | n |  | TRUE
16 | bus_LV_2405-3_0_3_node_47 | 0.4 | n |  | TRUE
17 | bus_LV_2405-3_0_3_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_2405-3_0_3_node_29 | 0.4 | n |  | TRUE
19 | bus_LV_2405-3_0_3_node_21 | 0.4 | n |  | TRUE
20 | bus_LV_2405-3_0_3_node_33 | 0.4 | n |  | TRUE
21 | bus_LV_2405-3_0_3_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_2405-3_0_3_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_2405-3_0_3_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_2405-3_0_3_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_2405-3_0_3_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_2405-3_0_3_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_2405-3_0_3_node_43 | 0.4 | n |  | TRUE
28 | bus_LV_2405-3_0_3_node_40 | 0.4 | n |  | TRUE
29 | bus_LV_2405-3_0_3_node_76 | 0.4 | n |  | TRUE
30 | bus_LV_2405-3_0_3_node_41 | 0.4 | n |  | TRUE
31 | bus_LV_2405-3_0_3_node_38 | 0.4 | n |  | TRUE
32 | bus_LV_2405-3_0_3_node_20 | 0.4 | n |  | TRUE
33 | bus_LV_2405-3_0_3_node_22 | 0.4 | n |  | TRUE
34 | bus_LV_2405-3_0_3_node_23 | 0.4 | n |  | TRUE
35 | bus_LV_2405-3_0_3_node_25 | 0.4 | n |  | TRUE
36 | bus_LV_2405-3_0_3_node_26 | 0.4 | n |  | TRUE
37 | bus_LV_2405-3_0_3_node_31 | 0.4 | n |  | TRUE
38 | bus_LV_2405-3_0_3_node_30 | 0.4 | n |  | TRUE
39 | bus_LV_2405-3_0_3_node_27 | 0.4 | n |  | TRUE
40 | bus_LV_2405-3_0_3_node_62 | 0.4 | n |  | TRUE
41 | bus_LV_2405-3_0_3_node_55 | 0.4 | n |  | TRUE
42 | bus_LV_2405-3_0_3_node_28 | 0.4 | n |  | TRUE
43 | bus_LV_2405-3_0_3_node_63 | 0.4 | n |  | TRUE
44 | bus_LV_2405-3_0_3_node_39 | 0.4 | n |  | TRUE
45 | bus_LV_2405-3_0_3_node_56 | 0.4 | n |  | TRUE
46 | bus_LV_2405-3_0_3_node_34 | 0.4 | n |  | TRUE
47 | bus_LV_2405-3_0_3_node_35 | 0.4 | n |  | TRUE
48 | bus_LV_2405-3_0_3_node_36 | 0.4 | n |  | TRUE
49 | bus_LV_2405-3_0_3_node_49 | 0.4 | n |  | TRUE
50 | bus_LV_2405-3_0_3_node_37 | 0.4 | n |  | TRUE
51 | bus_LV_2405-3_0_3_node_48 | 0.4 | n |  | TRUE
52 | bus_LV_2405-3_0_3_node_57 | 0.4 | n |  | TRUE
53 | bus_LV_2405-3_0_3_node_45 | 0.4 | n |  | TRUE
54 | bus_LV_2405-3_0_3_node_42 | 0.4 | n |  | TRUE
55 | bus_LV_2405-3_0_3_node_44 | 0.4 | n |  | TRUE
56 | bus_LV_2405-3_0_3_node_58 | 0.4 | n |  | TRUE
57 | bus_LV_2405-3_0_3_node_59 | 0.4 | n |  | TRUE
58 | bus_LV_2405-3_0_3_node_66 | 0.4 | n |  | TRUE
59 | bus_LV_2405-3_0_3_node_67 | 0.4 | n |  | TRUE
60 | bus_LV_2405-3_0_3_node_64 | 0.4 | n |  | TRUE
61 | bus_LV_2405-3_0_3_node_65 | 0.4 | n |  | TRUE
62 | bus_LV_2405-3_0_3_node_73 | 0.4 | n |  | TRUE
63 | bus_LV_2405-3_0_3_node_74 | 0.4 | n |  | TRUE
64 | bus_LV_2405-3_0_3_node_68 | 0.4 | n |  | TRUE
65 | bus_LV_2405-3_0_3_node_69 | 0.4 | n |  | TRUE
66 | bus_LV_2405-3_0_3_node_70 | 0.4 | n |  | TRUE
67 | bus_MV_334_0_node_139 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2405-3_0_3_load_0 | 0 | 0.0003452 | 8.6515e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2405-3_0_3_load_4 | 3 | 0.0098197 | 0.002461 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2405-3_0_3_load_10 | 5 | 0.0016581 | 0.00041557 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2405-3_0_3_load_60 | 6 | 0.0064167 | 0.0016082 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2405-3_0_3_load_24 | 7 | 0.0022591 | 0.00056618 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2405-3_0_3_load_32 | 8 | 0.0014796 | 0.00037083 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2405-3_0_3_load_11 | 9 | 0.0018969 | 0.00047541 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2405-3_0_3_load_5 | 10 | 0.0017224 | 0.00043167 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2405-3_0_3_load_6 | 11 | 0.0018604 | 0.00046626 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2405-3_0_3_load_7 | 12 | 0.0025291 | 0.00063386 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2405-3_0_3_load_8 | 13 | 0.0020405 | 0.00051139 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2405-3_0_3_load_9 | 14 | 0.0017222 | 0.00043162 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2405-3_0_3_load_46 | 15 | 0.0010948 | 0.00027437 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2405-3_0_3_load_47 | 16 | 0.0011012 | 0.00027598 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2405-3_0_3_load_29 | 18 | 0.0021159 | 0.00053028 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2405-3_0_3_load_33 | 20 | 0.00085736 | 0.00021488 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2405-3_0_3_load_14 | 21 | 0.001834 | 0.00045963 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2405-3_0_3_load_15 | 22 | 0.0015785 | 0.00039561 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2405-3_0_3_load_17 | 24 | 0.0015421 | 0.0003865 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2405-3_0_3_load_18 | 25 | 0.0016248 | 0.00040721 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2405-3_0_3_load_19 | 26 | 0.0013447 | 0.00033702 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2405-3_0_3_load_43 | 27 | 0.0035373 | 0.00088654 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2405-3_0_3_load_40 | 28 | 0.0011716 | 0.00029364 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2405-3_0_3_load_76 | 29 | 0.0021489 | 0.00053857 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2405-3_0_3_load_41 | 30 | 0.0022312 | 0.0005592 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2405-3_0_3_load_20 | 32 | 0.00174 | 0.0004361 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2405-3_0_3_load_25 | 35 | 0.0014934 | 0.00037427 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2405-3_0_3_load_26 | 36 | 0.0014754 | 0.00036977 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2405-3_0_3_load_31 | 37 | 0.00088585 | 0.00022201 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2405-3_0_3_load_30 | 38 | 0.0018502 | 0.00046371 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2405-3_0_3_load_62 | 40 | 0.0010427 | 0.00026132 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2405-3_0_3_load_55 | 41 | 0.0013406 | 0.00033597 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2405-3_0_3_load_28 | 42 | 0.003218 | 0.00080651 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2405-3_0_3_load_63 | 43 | 0.00066187 | 0.00016588 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2405-3_0_3_load_39 | 44 | 0.0010681 | 0.0002677 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2405-3_0_3_load_56 | 45 | 0.00059335 | 0.00014871 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2405-3_0_3_load_34 | 46 | 0.0076151 | 0.0019085 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2405-3_0_3_load_35 | 47 | 0.00069215 | 0.00017347 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2405-3_0_3_load_49 | 49 | 0.0028494 | 0.00071413 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2405-3_0_3_load_37 | 50 | 0.0020349 | 0.00050999 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2405-3_0_3_load_48 | 51 | 0.0026282 | 0.00065869 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2405-3_0_3_load_57 | 52 | 0.0010241 | 0.00025666 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2405-3_0_3_load_45 | 53 | 0.001164 | 0.00029172 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2405-3_0_3_load_42 | 54 | 0.00086353 | 0.00021642 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2405-3_0_3_load_44 | 55 | 0.00099159 | 0.00024852 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2405-3_0_3_load_58 | 56 | 0.0054697 | 0.0013708 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2405-3_0_3_load_66 | 58 | 0.0010234 | 0.00025649 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2405-3_0_3_load_67 | 59 | 0.00073459 | 0.00018411 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2405-3_0_3_load_64 | 60 | 0.00088373 | 0.00022148 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2405-3_0_3_load_65 | 61 | 0.00097199 | 0.0002436 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2405-3_0_3_load_73 | 62 | 0.0008585 | 0.00021516 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2405-3_0_3_load_74 | 63 | 0.0008232 | 0.00020631 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2405-3_0_3_load_68 | 64 | 0.00050838 | 0.00012741 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2405-3_0_3_load_69 | 65 | 0.0008041 | 0.00020153 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2405-3_0_3_load_70 | 66 | 0.00050764 | 0.00012723 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 52 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2405-3_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.023253 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2405-3_0_3_line_1 | NAYY 4x150 SE | 1 | 2 | 0.024577 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2405-3_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.03213 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2405-3_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.048648 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2405-3_0_3_line_4 | NAYY 4x150 SE | 2 | 5 | 0.02097 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2405-3_0_3_line_5 | NAYY 4x150 SE | 3 | 6 | 0.027393 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2405-3_0_3_line_6 | NAYY 4x150 SE | 4 | 7 | 0.0036519 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2405-3_0_3_line_7 | NAYY 4x150 SE | 4 | 8 | 0.016866 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2405-3_0_3_line_8 | NAYY 4x150 SE | 5 | 9 | 0.0040509 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2405-3_0_3_line_9 | NAYY 4x150 SE | 7 | 19 | 0.027376 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2405-3_0_3_line_10 | NAYY 4x150 SE | 8 | 20 | 0.038874 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2405-3_0_3_line_11 | NAYY 4x150 SE | 9 | 17 | 0.02584 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2405-3_0_3_line_12 | NAYY 4x150 SE | 10 | 11 | 0.025692 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2405-3_0_3_line_13 | NAYY 4x150 SE | 10 | 12 | 0.027514 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2405-3_0_3_line_14 | NAYY 4x150 SE | 11 | 13 | 0.0076846 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2405-3_0_3_line_15 | NAYY 4x150 SE | 12 | 14 | 0.0052563 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2405-3_0_3_line_16 | NAYY 4x150 SE | 14 | 15 | 0.019675 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2405-3_0_3_line_17 | NAYY 4x150 SE | 15 | 16 | 0.0020785 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2405-3_0_3_line_18 | NAYY 4x150 SE | 16 | 58 | 0.0023205 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2405-3_0_3_line_19 | NAYY 4x150 SE | 17 | 18 | 0.032637 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2405-3_0_3_line_20 | NAYY 4x150 SE | 19 | 34 | 0.010246 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
21 | LV_2405-3_0_3_line_21 | NAYY 4x150 SE | 19 | 32 | 0.019456 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
22 | LV_2405-3_0_3_line_22 | NAYY 4x150 SE | 21 | 22 | 0.010323 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2405-3_0_3_line_23 | NAYY 4x150 SE | 21 | 23 | 0.010978 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2405-3_0_3_line_24 | NAYY 4x150 SE | 22 | 24 | 0.010717 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2405-3_0_3_line_25 | NAYY 4x150 SE | 23 | 25 | 0.011007 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2405-3_0_3_line_26 | NAYY 4x150 SE | 23 | 26 | 0.017873 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2405-3_0_3_line_27 | NAYY 4x150 SE | 24 | 27 | 0.011721 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2405-3_0_3_line_28 | NAYY 4x150 SE | 25 | 28 | 0.025638 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2405-3_0_3_line_29 | NAYY 4x150 SE | 26 | 29 | 0.0071288 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2405-3_0_3_line_30 | NAYY 4x150 SE | 27 | 30 | 0.009074 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2405-3_0_3_line_31 | NAYY 4x150 SE | 28 | 31 | 0.026347 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2405-3_0_3_line_32 | NAYY 4x150 SE | 30 | 54 | 0.021773 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2405-3_0_3_line_33 | NAYY 4x150 SE | 31 | 44 | 0.023409 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2405-3_0_3_line_34 | NAYY 4x150 SE | 31 | 42 | 0.03918 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2405-3_0_3_line_35 | NAYY 4x150 SE | 32 | 33 | 0.037656 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
36 | LV_2405-3_0_3_line_36 | NAYY 4x150 SE | 33 | 35 | 0.041007 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2405-3_0_3_line_37 | NAYY 4x150 SE | 33 | 36 | 0.013971 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2405-3_0_3_line_38 | NAYY 4x150 SE | 34 | 37 | 0.020875 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
39 | LV_2405-3_0_3_line_39 | NAYY 4x150 SE | 34 | 38 | 0.012235 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_2405-3_0_3_line_40 | NAYY 4x150 SE | 35 | 39 | 0.034204 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_2405-3_0_3_line_41 | NAYY 4x150 SE | 36 | 40 | 0.012501 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_2405-3_0_3_line_42 | NAYY 4x150 SE | 37 | 41 | 0.030414 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
43 | LV_2405-3_0_3_line_43 | NAYY 4x150 SE | 39 | 42 | 0.001184 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_2405-3_0_3_line_44 | NAYY 4x150 SE | 40 | 43 | 0.015699 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_2405-3_0_3_line_45 | NAYY 4x150 SE | 41 | 45 | 0.031969 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
46 | LV_2405-3_0_3_line_46 | NAYY 4x150 SE | 43 | 64 | 0.0071392 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_2405-3_0_3_line_47 | NAYY 4x150 SE | 44 | 53 | 0.022012 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_2405-3_0_3_line_48 | NAYY 4x150 SE | 45 | 52 | 0.026704 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
49 | LV_2405-3_0_3_line_49 | NAYY 4x150 SE | 46 | 47 | 0.041266 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_2405-3_0_3_line_50 | NAYY 4x150 SE | 46 | 48 | 0.024669 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_2405-3_0_3_line_51 | NAYY 4x150 SE | 46 | 49 | 0.18084 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_2405-3_0_3_line_52 | NAYY 4x150 SE | 48 | 50 | 0.049597 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_2405-3_0_3_line_53 | NAYY 4x150 SE | 49 | 51 | 0.14765 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_2405-3_0_3_line_54 | NAYY 4x150 SE | 50 | 52 | 0.19986 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_2405-3_0_3_line_55 | NAYY 4x150 SE | 54 | 55 | 0.0065941 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_2405-3_0_3_line_56 | NAYY 4x150 SE | 55 | 56 | 0.039918 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_2405-3_0_3_line_57 | NAYY 4x150 SE | 56 | 57 | 0.018058 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_2405-3_0_3_line_58 | NAYY 4x150 SE | 57 | 60 | 0.014711 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_2405-3_0_3_line_59 | NAYY 4x150 SE | 57 | 61 | 0.017278 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_2405-3_0_3_line_60 | NAYY 4x150 SE | 58 | 59 | 0.01805 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_2405-3_0_3_line_61 | NAYY 4x150 SE | 59 | 62 | 0.0054318 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_2405-3_0_3_line_62 | NAYY 4x150 SE | 60 | 62 | 0.013614 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_2405-3_0_3_line_63 | NAYY 4x150 SE | 61 | 63 | 0.0044786 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_2405-3_0_3_line_64 | NAYY 4x150 SE | 64 | 65 | 0.0078202 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_2405-3_0_3_line_65 | NAYY 4x150 SE | 65 | 66 | 0.0020868 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2405-3_0_3_trafo_57 | 0.25 MVA 20/0.4 kV | 67 | 52 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2625317.9302 | 1238486.799 | 2625309.5933 | 1238488.9871 | 2625305.4998 | 1238491.1377 | 2625302.5965 | 1238492.6597 | 2625297.5929 | 1238497.1634
1 | 2625321.9754 | 1238464.0242 | 2625316.6539 | 1238472.1289 | 2625316.1771 | 1238479.3091 | 2625317.9302 | 1238486.799
2 | 2625317.9302 | 1238486.799 | 2625325.6626 | 1238486.2427 | 2625330.7128 | 1238486.7867 | 2625336.1976 | 1238488.2999 | 2625348.7169 | 1238493.6341
3 | 2625321.9754 | 1238464.0242 | 2625340.6009 | 1238445.403 | 2625357.6508 | 1238430.8999
4 | 2625321.9754 | 1238464.0242 | 2625305.0226 | 1238451.6808
5 | 2625373.9174 | 1238504.3714 | 2625348.7169 | 1238493.6341
6 | 2625357.6508 | 1238430.8999 | 2625360.5512 | 1238428.6809
7 | 2625357.6508 | 1238430.8999 | 2625344.8383 | 1238419.9311
8 | 2625305.0226 | 1238451.6808 | 2625301.7478 | 1238449.2963
9 | 2625382.7945 | 1238412.7402 | 2625370.1946 | 1238421.3029 | 2625360.5512 | 1238428.6809
10 | 2625315.0993 | 1238394.8963 | 2625335.6978 | 1238412.1058 | 2625344.8383 | 1238419.9311
11 | 2625280.858 | 1238434.0863 | 2625301.7478 | 1238449.2963
12 | 2625716.0306 | 1238152.5294 | 2625728.8481 | 1238130.2626
13 | 2625716.0306 | 1238152.5294 | 2625708.1328 | 1238166.2497 | 2625701.9956 | 1238176.1913
14 | 2625728.8481 | 1238130.2626 | 2625732.6818 | 1238123.6026
15 | 2625699.2346 | 1238180.6639 | 2625701.9956 | 1238176.1913
16 | 2625699.2346 | 1238180.6639 | 2625688.8995 | 1238197.4056
17 | 2625687.8077 | 1238199.1742 | 2625688.8995 | 1238197.4056
18 | 2625687.8077 | 1238199.1742 | 2625686.5887 | 1238201.1488
19 | 2625280.858 | 1238434.0863 | 2625255.2218 | 1238413.8882
20 | 2625382.7945 | 1238412.7402 | 2625381.7991 | 1238406.6989 | 2625381.598 | 1238404.1965 | 2625381.5898 | 1238402.5843
21 | 2625382.7945 | 1238412.7402 | 2625398.2324 | 1238409.1261 | 2625401.7383 | 1238408.3062
22 | 2625590.9324 | 1238353.6053 | 2625596.3277 | 1238344.8039
23 | 2625585.195 | 1238362.9648 | 2625590.9324 | 1238353.6053
24 | 2625601.9289 | 1238335.6666 | 2625596.3277 | 1238344.8039
25 | 2625585.195 | 1238362.9648 | 2625579.0799 | 1238372.1164
26 | 2625585.195 | 1238362.9648 | 2625600.9637 | 1238371.378
27 | 2625601.9289 | 1238335.6666 | 2625607.3005 | 1238326.9041 | 2625608.0816 | 1238325.6904
28 | 2625579.0799 | 1238372.1164 | 2625564.8354 | 1238393.4336
29 | 2625607.2533 | 1238374.7337 | 2625600.9637 | 1238371.378
30 | 2625612.9926 | 1238318.0602 | 2625608.0816 | 1238325.6904
31 | 2625548.0355 | 1238413.6702 | 2625561.2452 | 1238398.8065 | 2625564.8354 | 1238393.4336
32 | 2625612.9926 | 1238318.0602 | 2625624.7766 | 1238299.7515
33 | 2625548.0355 | 1238413.6702 | 2625553.9024 | 1238417.7979 | 2625568.7436 | 1238422.8092 | 2625569.2349 | 1238423.1006
34 | 2625548.0355 | 1238413.6702 | 2625540.7179 | 1238419.7759 | 2625533.887 | 1238423.4933 | 2625525.8706 | 1238424.9932 | 2625518.473 | 1238425.0504 | 2625512.2737 | 1238423.8253
35 | 2625438.9512 | 1238403.074 | 2625426.0668 | 1238403.8527 | 2625409.9982 | 1238406.3746 | 2625401.7383 | 1238408.3062
36 | 2625438.9512 | 1238403.074 | 2625446.8062 | 1238403.9526 | 2625458.2856 | 1238406.2698 | 2625478.5816 | 1238413.0307
37 | 2625438.9512 | 1238403.074 | 2625439.6028 | 1238397.5178 | 2625441.1129 | 1238392.8213 | 2625443.2506 | 1238390.1214
38 | 2625381.5898 | 1238402.5843 | 2625383.2974 | 1238397.6996 | 2625385.3986 | 1238394.5066 | 2625388.6 | 1238390.5067 | 2625393.2397 | 1238385.5976
39 | 2625381.5898 | 1238402.5843 | 2625373.2264 | 1238393.6543
40 | 2625511.1122 | 1238423.5957 | 2625494.2604 | 1238418.2535 | 2625478.5816 | 1238413.0307
41 | 2625443.2506 | 1238390.1214 | 2625451.0109 | 1238380.3204
42 | 2625414.1307 | 1238363.4938 | 2625393.2397 | 1238385.5976
43 | 2625511.1122 | 1238423.5957 | 2625512.2737 | 1238423.8253
44 | 2625451.0109 | 1238380.3204 | 2625460.7564 | 1238368.012 | 2625460.7564 | 1238368.012
45 | 2625414.1307 | 1238363.4938 | 2625428.2547 | 1238348.5498 | 2625435.9102 | 1238340.0942
46 | 2625466.3641 | 1238372.4303 | 2625460.7564 | 1238368.012
47 | 2625569.2349 | 1238423.1006 | 2625588.1683 | 1238434.3288
48 | 2625435.9102 | 1238340.0942 | 2625446.4941 | 1238328.4041 | 2625449.2031 | 1238324.6022 | 2625451.3978 | 1238320.7981 | 2625452.042 | 1238319.0378
49 | 2625278.8466 | 1238109.4768 | 2625254.7986 | 1238096.1983 | 2625246.0983 | 1238091.2138 | 2625242.8275 | 1238089.3409
50 | 2625298.9021 | 1238123.6027 | 2625295.0983 | 1238119.8064 | 2625290.5975 | 1238116.2962 | 2625281.6036 | 1238110.9991 | 2625278.8466 | 1238109.4768
51 | 2625278.8466 | 1238109.4768 | 2625359.1847 | 1237947.4652
52 | 2625298.9021 | 1238123.6027 | 2625302.0998 | 1238127.5965 | 2625304.2029 | 1238131.0965 | 2625306.7988 | 1238136.0996 | 2625309.798 | 1238142.3051 | 2625315.7978 | 1238154.4048 | 2625319.399 | 1238163.1033 | 2625321.8572 | 1238167.3984
53 | 2625359.1847 | 1237947.4652 | 2625223.0109 | 1237890.382
54 | 2625452.042 | 1238319.0378 | 2625321.8572 | 1238167.3984
55 | 2625628.3454 | 1238294.2066 | 2625624.7766 | 1238299.7515
56 | 2625628.3454 | 1238294.2066 | 2625628.9799 | 1238293.2208 | 2625649.7119 | 1238260.4885
57 | 2625659.3745 | 1238245.233 | 2625649.7119 | 1238260.4885
58 | 2625659.3745 | 1238245.233 | 2625667.1023 | 1238232.7148
59 | 2625659.3745 | 1238245.233 | 2625674.0941 | 1238254.2817
60 | 2625686.5887 | 1238201.1488 | 2625677.1069 | 1238216.5083
61 | 2625674.2536 | 1238221.1303 | 2625677.1069 | 1238216.5083
62 | 2625674.2536 | 1238221.1303 | 2625667.1023 | 1238232.7148
63 | 2625674.0941 | 1238254.2817 | 2625677.9094 | 1238256.6271
64 | 2625466.3641 | 1238372.4303 | 2625472.5068 | 1238377.2699
65 | 2625474.146 | 1238378.5614 | 2625472.5068 | 1238377.2699

## bus_geodata
| x | y | coords
0 | 2625297.5929 | 1238497.1634
1 | 2625317.9302 | 1238486.799
2 | 2625321.9754 | 1238464.0242
3 | 2625348.7169 | 1238493.6341
4 | 2625357.6508 | 1238430.8999
5 | 2625305.0226 | 1238451.6808
6 | 2625373.9174 | 1238504.3714
7 | 2625360.5512 | 1238428.6809
8 | 2625344.8383 | 1238419.9311
9 | 2625301.7478 | 1238449.2963
10 | 2625716.0306 | 1238152.5294
11 | 2625728.8481 | 1238130.2626
12 | 2625701.9956 | 1238176.1913
13 | 2625732.6818 | 1238123.6026
14 | 2625699.2346 | 1238180.6639
15 | 2625688.8995 | 1238197.4056
16 | 2625687.8077 | 1238199.1742
17 | 2625280.858 | 1238434.0863
18 | 2625255.2218 | 1238413.8882
19 | 2625382.7945 | 1238412.7402
20 | 2625315.0993 | 1238394.8963
21 | 2625590.9324 | 1238353.6053
22 | 2625596.3277 | 1238344.8039
23 | 2625585.195 | 1238362.9648
24 | 2625601.9289 | 1238335.6666
25 | 2625579.0799 | 1238372.1164
26 | 2625600.9637 | 1238371.378
27 | 2625608.0816 | 1238325.6904
28 | 2625564.8354 | 1238393.4336
29 | 2625607.2533 | 1238374.7337
30 | 2625612.9926 | 1238318.0602
31 | 2625548.0355 | 1238413.6702
32 | 2625401.7383 | 1238408.3062
33 | 2625438.9512 | 1238403.074
34 | 2625381.5898 | 1238402.5843
35 | 2625478.5816 | 1238413.0307
36 | 2625443.2506 | 1238390.1214
37 | 2625393.2397 | 1238385.5976
38 | 2625373.2264 | 1238393.6543
39 | 2625511.1122 | 1238423.5957
40 | 2625451.0109 | 1238380.3204
41 | 2625414.1307 | 1238363.4938
42 | 2625512.2737 | 1238423.8253
43 | 2625460.7564 | 1238368.012
44 | 2625569.2349 | 1238423.1006
45 | 2625435.9102 | 1238340.0942
46 | 2625278.8466 | 1238109.4768
47 | 2625242.8275 | 1238089.3409
48 | 2625298.9021 | 1238123.6027
49 | 2625359.1847 | 1237947.4652
50 | 2625321.8572 | 1238167.3984
51 | 2625223.0109 | 1237890.382
52 | 2625452.042 | 1238319.0378
53 | 2625588.1683 | 1238434.3288
54 | 2625624.7766 | 1238299.7515
55 | 2625628.3454 | 1238294.2066
56 | 2625649.7119 | 1238260.4885
57 | 2625659.3745 | 1238245.233
58 | 2625686.5887 | 1238201.1488
59 | 2625677.1069 | 1238216.5083
60 | 2625667.1023 | 1238232.7148
61 | 2625674.0941 | 1238254.2817
62 | 2625674.2536 | 1238221.1303
63 | 2625677.9094 | 1238256.6271
64 | 2625466.3641 | 1238372.4303
65 | 2625472.5068 | 1238377.2699
66 | 2625474.146 | 1238378.5614
67 | 2625381.5898 | 1238402.5843

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9892 | -0.075297 | 0.0003452 | 8.6515e-05
1 | 0.98921 | -0.075215 | 0 | 0
2 | 0.9898 | -0.071059 | 0 | 0
3 | 0.98846 | -0.080541 | 0.0098197 | 0.002461
4 | 0.99136 | -0.060038 | 0 | 0
5 | 0.98963 | -0.072272 | 0.0016581 | 0.00041557
6 | 0.98821 | -0.082337 | 0.0064167 | 0.0016082
7 | 0.99149 | -0.059125 | 0.0022591 | 0.00056618
8 | 0.99131 | -0.060439 | 0.0014796 | 0.00037083
9 | 0.98961 | -0.072438 | 0.0018969 | 0.00047541
10 | 0.97167 | -0.1996 | 0.0017224 | 0.00043167
11 | 0.97152 | -0.20066 | 0.0018604 | 0.00046626
12 | 0.97189 | -0.19796 | 0.0025291 | 0.00063386
13 | 0.9715 | -0.20083 | 0.0020405 | 0.00051139
14 | 0.97196 | -0.19751 | 0.0017222 | 0.00043162
15 | 0.97224 | -0.19546 | 0.0010948 | 0.00027437
16 | 0.97227 | -0.19522 | 0.0011012 | 0.00027598
17 | 0.98953 | -0.072996 | 0 | 0
18 | 0.98943 | -0.0737 | 0.0021159 | 0.00053028
19 | 0.99255 | -0.051663 | 0 | 0
20 | 0.99126 | -0.060778 | 0.00085736 | 0.00021488
21 | 0.9781 | -0.15342 | 0.001834 | 0.00045963
22 | 0.9776 | -0.15704 | 0.0015785 | 0.00039561
23 | 0.97867 | -0.14936 | 0 | 0
24 | 0.97709 | -0.16063 | 0.0015421 | 0.0003865
25 | 0.9793 | -0.1449 | 0.0016248 | 0.00040721
26 | 0.97858 | -0.15001 | 0.0013447 | 0.00033702
27 | 0.97657 | -0.16437 | 0.0035373 | 0.00088654
28 | 0.98082 | -0.13409 | 0.0011716 | 0.00029364
29 | 0.97856 | -0.15017 | 0.0021489 | 0.00053857
30 | 0.97621 | -0.16692 | 0.0022312 | 0.0005592
31 | 0.98243 | -0.1227 | 0 | 0
32 | 0.99177 | -0.057132 | 0.00174 | 0.0004361
33 | 0.99029 | -0.067408 | 0 | 0
34 | 0.99316 | -0.047392 | 0 | 0
35 | 0.98738 | -0.087791 | 0.0014934 | 0.00037427
36 | 0.99019 | -0.06812 | 0.0014754 | 0.00036977
37 | 0.99444 | -0.038512 | 0.00088585 | 0.00022201
38 | 0.99313 | -0.047621 | 0.0018502 | 0.00046371
39 | 0.98502 | -0.10436 | 0 | 0
40 | 0.99013 | -0.068569 | 0.0010427 | 0.00026132
41 | 0.99631 | -0.025479 | 0.0013406 | 0.00033597
42 | 0.98494 | -0.10493 | 0.003218 | 0.00080651
43 | 0.99007 | -0.068966 | 0.00066187 | 0.00016588
44 | 0.98235 | -0.12325 | 0.0010681 | 0.0002677
45 | 0.99832 | -0.011617 | 0.00059335 | 0.00014871
46 | 0.994 | -0.042159 | 0.0076151 | 0.0019085
47 | 0.99396 | -0.042448 | 0.00069215 | 0.00017347
48 | 0.99448 | -0.038717 | 0 | 0
49 | 0.99257 | -0.052221 | 0.0028494 | 0.00071413
50 | 0.99547 | -0.031804 | 0.0020349 | 0.00050999
51 | 0.99202 | -0.056165 | 0.0026282 | 0.00065869
52 | 1 | 0 | -0.10515 | -0.026344
53 | 0.98231 | -0.12351 | 0.001164 | 0.00029172
54 | 0.97543 | -0.17256 | 0.00086353 | 0.00021642
55 | 0.9752 | -0.17421 | 0.00099159 | 0.00024852
56 | 0.97386 | -0.1838 | 0.0054697 | 0.0013708
57 | 0.9734 | -0.18711 | 0 | 0
58 | 0.97231 | -0.19492 | 0.0010234 | 0.00025649
59 | 0.97266 | -0.19242 | 0.00073459 | 0.00018411
60 | 0.97306 | -0.18952 | 0.00088373 | 0.00022148
61 | 0.97336 | -0.18743 | 0.00097199 | 0.0002436
62 | 0.97277 | -0.19163 | 0.0008585 | 0.00021516
63 | 0.97335 | -0.18747 | 0.0008232 | 0.00020631
64 | 0.99005 | -0.069098 | 0.00050838 | 0.00012741
65 | 0.99004 | -0.069203 | 0.0008041 | 0.00020153
66 | 0.99004 | -0.069213 | 0.00050764 | 0.00012723
67 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0003452 | -8.6515e-05 | 0.0003452 | 8.6218e-05 | 3.9117e-09 | -2.9701e-07 | 0.00051927 | 0.00051916 | 0.00051927 | 0.9892 | -0.075297 | 0.98921 | -0.075215 | 0.19232
1 | -0.016595 | -0.0041599 | 0.016605 | 0.0041632 | 9.5569e-06 | 3.36e-06 | 0.024963 | 0.024963 | 0.024963 | 0.98921 | -0.075215 | 0.9898 | -0.071059 | 9.2457
2 | 0.01625 | 0.0040737 | -0.016238 | -0.0040695 | 1.198e-05 | 4.1954e-06 | 0.024444 | 0.024444 | 0.024444 | 0.98921 | -0.075215 | 0.98846 | -0.080541 | 9.0534
3 | -0.022277 | -0.005584 | 0.022311 | 0.0055965 | 3.4048e-05 | 1.2469e-05 | 0.03349 | 0.03349 | 0.03349 | 0.9898 | -0.071059 | 0.99136 | -0.060038 | 12.4038
4 | 0.0056723 | 0.0014207 | -0.0056714 | -0.0014206 | 9.515e-07 | 9.6473e-08 | 0.0085272 | 0.0085273 | 0.0085273 | 0.9898 | -0.071059 | 0.98963 | -0.072272 | 3.1583
5 | 0.0064183 | 0.0016084 | -0.0064167 | -0.0016082 | 1.5957e-06 | 2.6269e-07 | 0.0096619 | 0.009662 | 0.009662 | 0.98846 | -0.080541 | 0.98821 | -0.082337 | 3.5785
6 | -0.024648 | -0.0061815 | 0.024651 | 0.0061827 | 3.1193e-06 | 1.1527e-06 | 0.036998 | 0.036998 | 0.036998 | 0.99136 | -0.060038 | 0.99149 | -0.059125 | 13.7029
7 | 0.0023372 | 0.00058505 | -0.002337 | -0.00058522 | 1.295e-07 | -1.6765e-07 | 0.0035078 | 0.0035079 | 0.0035079 | 0.99136 | -0.060038 | 0.99131 | -0.060439 | 1.2992
8 | 0.0040132 | 0.0010051 | -0.0040132 | -0.0010051 | 9.2037e-08 | -1.6649e-08 | 0.0060341 | 0.0060341 | 0.0060341 | 0.98963 | -0.072272 | 0.98961 | -0.072438 | 2.2349
9 | -0.02691 | -0.0067488 | 0.026938 | 0.0067592 | 2.7866e-05 | 1.0364e-05 | 0.040388 | 0.040388 | 0.040388 | 0.99149 | -0.059125 | 0.99255 | -0.051663 | 14.9586
10 | 0.0008574 | 0.00021439 | -0.00085736 | -0.00021488 | 4.0175e-08 | -4.857e-07 | 0.0012868 | 0.001287 | 0.001287 | 0.99131 | -0.060439 | 0.99126 | -0.060778 | 0.47667
11 | 0.0021162 | 0.00052968 | -0.0021161 | -0.00052994 | 1.6325e-07 | -2.6919e-07 | 0.0031818 | 0.0031819 | 0.0031819 | 0.98961 | -0.072438 | 0.98953 | -0.072996 | 1.1785
12 | 0.0039015 | 0.00097748 | -0.0039009 | -0.00097757 | 5.723e-07 | -9.8072e-08 | 0.0059747 | 0.0059748 | 0.0059748 | 0.97167 | -0.1996 | 0.97152 | -0.20066 | 2.2129
13 | -0.0056239 | -0.0014091 | 0.0056251 | 0.0014093 | 1.2734e-06 | 1.489e-07 | 0.0086123 | 0.0086122 | 0.0086123 | 0.97167 | -0.1996 | 0.97189 | -0.19796 | 3.1897
14 | 0.0020405 | 0.00051131 | -0.0020405 | -0.00051139 | 4.6837e-08 | -7.7138e-08 | 0.0031253 | 0.0031253 | 0.0031253 | 0.97152 | -0.20066 | 0.9715 | -0.20083 | 1.1575
15 | -0.0081543 | -0.0020432 | 0.0081548 | 0.0020433 | 5.1121e-07 | 1.3148e-07 | 0.012484 | 0.012484 | 0.012484 | 0.97189 | -0.19796 | 0.97196 | -0.19751 | 4.6239
16 | -0.009877 | -0.0024749 | 0.0098798 | 0.0024757 | 2.807e-06 | 8.3572e-07 | 0.015121 | 0.015121 | 0.015121 | 0.97196 | -0.19751 | 0.97224 | -0.19546 | 5.6004
17 | -0.010975 | -0.0027501 | 0.010975 | 0.0027502 | 3.6591e-07 | 1.1496e-07 | 0.016796 | 0.016796 | 0.016796 | 0.97224 | -0.19546 | 0.97227 | -0.19522 | 6.2209
18 | -0.012076 | -0.0030262 | 0.012077 | 0.0030264 | 4.946e-07 | 1.6145e-07 | 0.018482 | 0.018482 | 0.018482 | 0.97227 | -0.19522 | 0.97231 | -0.19492 | 6.8451
19 | 0.0021161 | 0.00052994 | -0.0021159 | -0.00053028 | 2.062e-07 | -3.399e-07 | 0.0031819 | 0.0031821 | 0.0031821 | 0.98953 | -0.072996 | 0.98943 | -0.0737 | 1.1785
20 | -0.083129 | -0.02094 | 0.083179 | 0.020959 | 4.9681e-05 | 1.8843e-05 | 0.12466 | 0.12466 | 0.12466 | 0.99255 | -0.051663 | 0.99316 | -0.047392 | 23.0858
21 | 0.056191 | 0.014181 | -0.056148 | -0.014165 | 4.3113e-05 | 1.6079e-05 | 0.084275 | 0.084275 | 0.084275 | 0.99255 | -0.051663 | 0.99177 | -0.057132 | 15.6065
22 | 0.033723 | 0.0084674 | -0.033706 | -0.008461 | 1.6959e-05 | 6.3933e-06 | 0.05131 | 0.05131 | 0.05131 | 0.9781 | -0.15342 | 0.9776 | -0.15704 | 19.0036
23 | -0.035557 | -0.0089271 | 0.035577 | 0.0089346 | 2.0049e-05 | 7.5735e-06 | 0.0541 | 0.0541 | 0.0541 | 0.9781 | -0.15342 | 0.97867 | -0.14936 | 20.037
24 | 0.032128 | 0.0080654 | -0.032112 | -0.0080594 | 1.5996e-05 | 6.0181e-06 | 0.048907 | 0.048907 | 0.048907 | 0.9776 | -0.15704 | 0.97709 | -0.16063 | 18.1138
25 | -0.039071 | -0.00981 | 0.039096 | 0.0098192 | 2.4243e-05 | 9.1859e-06 | 0.059412 | 0.059412 | 0.059412 | 0.97867 | -0.14936 | 0.9793 | -0.1449 | 22.0045
26 | 0.003494 | 0.00087541 | -0.0034937 | -0.00087552 | 3.1474e-07 | -1.0351e-07 | 0.0053123 | 0.0053124 | 0.0053124 | 0.97867 | -0.14936 | 0.97858 | -0.15001 | 1.9676
27 | 0.03057 | 0.0076729 | -0.030554 | -0.007667 | 1.5855e-05 | 5.9513e-06 | 0.046559 | 0.046559 | 0.046559 | 0.97709 | -0.16063 | 0.97657 | -0.16437 | 17.244
28 | -0.04072 | -0.010226 | 0.040782 | 0.01025 | 6.1261e-05 | 2.3239e-05 | 0.061881 | 0.061881 | 0.061881 | 0.9793 | -0.1449 | 0.98082 | -0.13409 | 22.9188
29 | 0.002149 | 0.0005385 | -0.0021489 | -0.00053857 | 4.7498e-08 | -7.1292e-08 | 0.0032676 | 0.0032677 | 0.0032677 | 0.97858 | -0.15001 | 0.97856 | -0.15017 | 1.2102
30 | 0.027017 | 0.0067804 | -0.027007 | -0.0067768 | 9.5967e-06 | 3.5775e-06 | 0.041169 | 0.041169 | 0.041169 | 0.97657 | -0.16437 | 0.97621 | -0.16692 | 15.2477
31 | -0.041953 | -0.010543 | 0.04202 | 0.010569 | 6.6624e-05 | 2.5291e-05 | 0.063658 | 0.063658 | 0.063658 | 0.98082 | -0.13409 | 0.98243 | -0.1227 | 23.5771
32 | 0.024776 | 0.0062176 | -0.024756 | -0.0062105 | 1.938e-05 | 7.1818e-06 | 0.037768 | 0.037768 | 0.037768 | 0.97621 | -0.16692 | 0.97543 | -0.17256 | 13.9881
33 | 0.0022323 | 0.00055892 | -0.0022321 | -0.00055915 | 1.6698e-07 | -2.3217e-07 | 0.0033809 | 0.003381 | 0.003381 | 0.98243 | -0.1227 | 0.98235 | -0.12325 | 1.2522
34 | -0.044252 | -0.011128 | 0.044362 | 0.011169 | 0.00010988 | 4.1762e-05 | 0.067039 | 0.067039 | 0.067039 | 0.98243 | -0.1227 | 0.98494 | -0.10493 | 24.8293
35 | 0.054408 | 0.013729 | -0.054329 | -0.0137 | 7.8353e-05 | 2.9166e-05 | 0.081665 | 0.081665 | 0.081665 | 0.99177 | -0.057132 | 0.99029 | -0.067408 | 15.1231
36 | 0.049328 | 0.012447 | -0.049188 | -0.012394 | 0.00014069 | 5.3587e-05 | 0.074151 | 0.074151 | 0.074151 | 0.99029 | -0.067408 | 0.98738 | -0.087791 | 27.4633
37 | 0.005001 | 0.0012527 | -0.0050005 | -0.0012527 | 4.9226e-07 | 9.598e-09 | 0.0075143 | 0.0075143 | 0.0075143 | 0.99029 | -0.067408 | 0.99019 | -0.06812 | 2.7831
38 | -0.085029 | -0.021423 | 0.085135 | 0.021463 | 0.00010577 | 4.0139e-05 | 0.12744 | 0.12744 | 0.12744 | 0.99316 | -0.047392 | 0.99444 | -0.038512 | 23.5992
39 | 0.0018503 | 0.00046358 | -0.0018502 | -0.00046371 | 5.8672e-08 | -1.3575e-07 | 0.0027722 | 0.0027722 | 0.0027722 | 0.99316 | -0.047392 | 0.99313 | -0.047621 | 1.0267
40 | 0.047694 | 0.012019 | -0.047584 | -0.011977 | 0.00011034 | 4.2001e-05 | 0.0719 | 0.071901 | 0.071901 | 0.98738 | -0.087791 | 0.98502 | -0.10436 | 26.6298
41 | 0.0035251 | 0.00088294 | -0.0035249 | -0.00088302 | 2.1889e-07 | -7.6607e-08 | 0.0052971 | 0.0052972 | 0.0052972 | 0.99019 | -0.06812 | 0.99013 | -0.068569 | 1.9619
42 | -0.086021 | -0.021685 | 0.086178 | 0.021745 | 0.00015732 | 5.9718e-05 | 0.12876 | 0.12876 | 0.12876 | 0.99444 | -0.038512 | 0.99631 | -0.025479 | 23.8446
43 | 0.047584 | 0.011977 | -0.04758 | -0.011976 | 3.8195e-06 | 1.454e-06 | 0.071901 | 0.071901 | 0.071901 | 0.98502 | -0.10436 | 0.98494 | -0.10493 | 26.6298
44 | 0.0024822 | 0.0006217 | -0.002482 | -0.00062185 | 1.3631e-07 | -1.4948e-07 | 0.0037302 | 0.0037303 | 0.0037303 | 0.99013 | -0.068569 | 0.99007 | -0.068966 | 1.3816
45 | -0.087519 | -0.022081 | 0.087689 | 0.022145 | 0.00017055 | 6.4761e-05 | 0.13076 | 0.13076 | 0.13076 | 0.99631 | -0.025479 | 0.99832 | -0.011617 | 24.2153
46 | 0.0018202 | 0.00045597 | -0.0018201 | -0.00045604 | 3.3336e-08 | -7.8987e-08 | 0.0027355 | 0.0027356 | 0.0027356 | 0.99007 | -0.068966 | 0.99005 | -0.069098 | 1.0132
47 | 0.001164 | 0.00029145 | -0.001164 | -0.00029172 | 4.2699e-08 | -2.6225e-07 | 0.0017631 | 0.0017632 | 0.0017632 | 0.98235 | -0.12325 | 0.98231 | -0.12351 | 0.65303
48 | -0.088282 | -0.022294 | 0.088427 | 0.022349 | 0.00014439 | 5.4837e-05 | 0.13165 | 0.13165 | 0.13165 | 0.99832 | -0.011617 | 1 | 0 | 24.379
49 | 0.00069217 | 0.00017294 | -0.00069215 | -0.00017347 | 2.7643e-08 | -5.2425e-07 | 0.001036 | 0.0010362 | 0.0010362 | 0.994 | -0.042159 | 0.99396 | -0.042448 | 0.38377
50 | -0.013794 | -0.0034535 | 0.013801 | 0.0034557 | 6.5631e-06 | 2.2043e-06 | 0.020648 | 0.020648 | 0.020648 | 0.994 | -0.042159 | 0.99448 | -0.038717 | 7.6475
51 | 0.0054867 | 0.001372 | -0.005479 | -0.0013715 | 7.6114e-06 | 5.8675e-07 | 0.0082125 | 0.0082133 | 0.0082133 | 0.994 | -0.042159 | 0.99257 | -0.052221 | 3.042
52 | -0.013801 | -0.0034557 | 0.013814 | 0.0034602 | 1.3195e-05 | 4.4308e-06 | 0.020648 | 0.020648 | 0.020648 | 0.99448 | -0.038717 | 0.99547 | -0.031804 | 7.6475
53 | 0.0026296 | 0.00065733 | -0.0026282 | -0.00065869 | 1.4317e-06 | -1.3567e-06 | 0.0039416 | 0.0039423 | 0.0039423 | 0.99257 | -0.052221 | 0.99202 | -0.056165 | 1.4601
54 | -0.015849 | -0.0039702 | 0.015919 | 0.0039945 | 6.9985e-05 | 2.4307e-05 | 0.02369 | 0.023689 | 0.02369 | 0.99547 | -0.031804 | 1 | 0 | 8.774
55 | 0.023893 | 0.005994 | -0.023887 | -0.005992 | 5.467e-06 | 2.0204e-06 | 0.036451 | 0.036451 | 0.036451 | 0.97543 | -0.17256 | 0.9752 | -0.17421 | 13.5002
56 | 0.022896 | 0.0057435 | -0.022865 | -0.0057323 | 3.0405e-05 | 1.1197e-05 | 0.034938 | 0.034938 | 0.034938 | 0.9752 | -0.17421 | 0.97386 | -0.1838 | 12.9399
57 | 0.017396 | 0.0043615 | -0.017388 | -0.0043586 | 7.9612e-06 | 2.8374e-06 | 0.02658 | 0.02658 | 0.02658 | 0.97386 | -0.1838 | 0.9734 | -0.18711 | 9.8446
58 | 0.015592 | 0.0039089 | -0.015587 | -0.0039071 | 5.2157e-06 | 1.8232e-06 | 0.023836 | 0.023836 | 0.023836 | 0.9734 | -0.18711 | 0.97306 | -0.18952 | 8.8282
59 | 0.0017953 | 0.00044968 | -0.0017952 | -0.00044986 | 8.1202e-08 | -1.8354e-07 | 0.0027443 | 0.0027444 | 0.0027444 | 0.9734 | -0.18711 | 0.97336 | -0.18743 | 1.0164
60 | -0.0131 | -0.0032829 | 0.013104 | 0.0032844 | 4.527e-06 | 1.5172e-06 | 0.020048 | 0.020048 | 0.020048 | 0.97231 | -0.19492 | 0.97266 | -0.19242 | 7.4251
61 | -0.013839 | -0.0034685 | 0.013841 | 0.003469 | 1.5193e-06 | 5.1691e-07 | 0.021172 | 0.021172 | 0.021172 | 0.97266 | -0.19242 | 0.97277 | -0.19163 | 7.8413
62 | 0.014703 | 0.0036856 | -0.014699 | -0.0036842 | 4.2949e-06 | 1.4828e-06 | 0.022485 | 0.022485 | 0.022485 | 0.97306 | -0.18952 | 0.97277 | -0.19163 | 8.3277
63 | 0.00082321 | 0.00020626 | -0.0008232 | -0.00020631 | 4.4259e-09 | -5.3964e-08 | 0.0012585 | 0.0012585 | 0.0012585 | 0.97336 | -0.18743 | 0.97335 | -0.18747 | 0.4661
64 | 0.0013118 | 0.00032863 | -0.0013117 | -0.00032873 | 1.8967e-08 | -9.3268e-08 | 0.0019715 | 0.0019715 | 0.0019715 | 0.99005 | -0.069098 | 0.99004 | -0.069203 | 0.73019
65 | 0.00050764 | 0.0001272 | -0.00050764 | -0.00012723 | 7.5803e-10 | -2.6543e-08 | 0.00076297 | 0.00076298 | 0.00076298 | 0.99004 | -0.069203 | 0.99004 | -0.069213 | 0.28258

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.10617 | 0.0266

## res_load
| p_mw | q_mvar
0 | 0.0003452 | 8.6515e-05
1 | 0.0098197 | 0.002461
2 | 0.0016581 | 0.00041557
3 | 0.0064167 | 0.0016082
4 | 0.0022591 | 0.00056618
5 | 0.0014796 | 0.00037083
6 | 0.0018969 | 0.00047541
7 | 0.0017224 | 0.00043167
8 | 0.0018604 | 0.00046626
9 | 0.0025291 | 0.00063386
10 | 0.0020405 | 0.00051139
11 | 0.0017222 | 0.00043162
12 | 0.0010948 | 0.00027437
13 | 0.0011012 | 0.00027598
14 | 0.0021159 | 0.00053028
15 | 0.00085736 | 0.00021488
16 | 0.001834 | 0.00045963
17 | 0.0015785 | 0.00039561
18 | 0.0015421 | 0.0003865
19 | 0.0016248 | 0.00040721
20 | 0.0013447 | 0.00033702
21 | 0.0035373 | 0.00088654
22 | 0.0011716 | 0.00029364
23 | 0.0021489 | 0.00053857
24 | 0.0022312 | 0.0005592
25 | 0.00174 | 0.0004361
26 | 0.0014934 | 0.00037427
27 | 0.0014754 | 0.00036977
28 | 0.00088585 | 0.00022201
29 | 0.0018502 | 0.00046371
30 | 0.0010427 | 0.00026132
31 | 0.0013406 | 0.00033597
32 | 0.003218 | 0.00080651
33 | 0.00066187 | 0.00016588
34 | 0.0010681 | 0.0002677
35 | 0.00059335 | 0.00014871
36 | 0.0076151 | 0.0019085
37 | 0.00069215 | 0.00017347
38 | 0.0028494 | 0.00071413
39 | 0.0020349 | 0.00050999
40 | 0.0026282 | 0.00065869
41 | 0.0010241 | 0.00025666
42 | 0.001164 | 0.00029172
43 | 0.00086353 | 0.00021642
44 | 0.00099159 | 0.00024852
45 | 0.0054697 | 0.0013708
46 | 0.0010234 | 0.00025649
47 | 0.00073459 | 0.00018411
48 | 0.00088373 | 0.00022148
49 | 0.00097199 | 0.0002436
50 | 0.0008585 | 0.00021516
51 | 0.0008232 | 0.00020631
52 | 0.00050838 | 0.00012741
53 | 0.0008041 | 0.00020153
54 | 0.00050764 | 0.00012723

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1