## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2405-5_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2405-5_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2405-5_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2405-5_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2405-5_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2405-5_0_3_node_9 | 0.4 | n |  | TRUE
6 | bus_LV_2405-5_0_3_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_2405-5_0_3_node_31 | 0.4 | n |  | TRUE
8 | bus_LV_2405-5_0_3_node_32 | 0.4 | n |  | TRUE
9 | bus_LV_2405-5_0_3_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_2405-5_0_3_node_53 | 0.4 | n |  | TRUE
11 | bus_LV_2405-5_0_3_node_30 | 0.4 | n |  | TRUE
12 | bus_LV_2405-5_0_3_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_2405-5_0_3_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_2405-5_0_3_node_36 | 0.4 | n |  | TRUE
15 | bus_LV_2405-5_0_3_node_34 | 0.4 | n |  | TRUE
16 | bus_LV_2405-5_0_3_node_23 | 0.4 | n |  | TRUE
17 | bus_LV_2405-5_0_3_node_35 | 0.4 | n |  | TRUE
18 | bus_LV_2405-5_0_3_node_33 | 0.4 | n |  | TRUE
19 | bus_LV_2405-5_0_3_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_2405-5_0_3_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_2405-5_0_3_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_2405-5_0_3_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_2405-5_0_3_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_2405-5_0_3_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_2405-5_0_3_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_2405-5_0_3_node_57 | 0.4 | n |  | TRUE
27 | bus_LV_2405-5_0_3_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_2405-5_0_3_node_16 | 0.4 | n |  | TRUE
29 | bus_LV_2405-5_0_3_node_38 | 0.4 | n |  | TRUE
30 | bus_LV_2405-5_0_3_node_17 | 0.4 | n |  | TRUE
31 | bus_LV_2405-5_0_3_node_58 | 0.4 | n |  | TRUE
32 | bus_LV_2405-5_0_3_node_21 | 0.4 | n |  | TRUE
33 | bus_LV_2405-5_0_3_node_22 | 0.4 | n |  | TRUE
34 | bus_LV_2405-5_0_3_node_44 | 0.4 | n |  | TRUE
35 | bus_LV_2405-5_0_3_node_48 | 0.4 | n |  | TRUE
36 | bus_LV_2405-5_0_3_node_51 | 0.4 | n |  | TRUE
37 | bus_LV_2405-5_0_3_node_25 | 0.4 | n |  | TRUE
38 | bus_LV_2405-5_0_3_node_26 | 0.4 | n |  | TRUE
39 | bus_LV_2405-5_0_3_node_28 | 0.4 | n |  | TRUE
40 | bus_LV_2405-5_0_3_node_43 | 0.4 | n |  | TRUE
41 | bus_LV_2405-5_0_3_node_29 | 0.4 | n |  | TRUE
42 | bus_LV_2405-5_0_3_node_41 | 0.4 | n |  | TRUE
43 | bus_LV_2405-5_0_3_node_45 | 0.4 | n |  | TRUE
44 | bus_LV_2405-5_0_3_node_54 | 0.4 | n |  | TRUE
45 | bus_LV_2405-5_0_3_node_39 | 0.4 | n |  | TRUE
46 | bus_LV_2405-5_0_3_node_56 | 0.4 | n |  | TRUE
47 | bus_LV_2405-5_0_3_node_55 | 0.4 | n |  | TRUE
48 | bus_LV_2405-5_0_3_node_42 | 0.4 | n |  | TRUE
49 | bus_LV_2405-5_0_3_node_37 | 0.4 | n |  | TRUE
50 | bus_LV_2405-5_0_3_node_46 | 0.4 | n |  | TRUE
51 | bus_LV_2405-5_0_3_node_52 | 0.4 | n |  | TRUE
52 | bus_LV_2405-5_0_3_node_47 | 0.4 | n |  | TRUE
53 | bus_MV_334_0_node_146 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2405-5_0_3_load_0 | 0 | 0.0016364 | 0.00041011 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2405-5_0_3_load_1 | 1 | 0.0022357 | 0.00056031 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2405-5_0_3_load_2 | 2 | 0.0016993 | 0.00042589 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2405-5_0_3_load_4 | 4 | 0.001862 | 0.00046666 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2405-5_0_3_load_9 | 5 | 0.0032467 | 0.00081369 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2405-5_0_3_load_5 | 6 | 0.0080564 | 0.0020191 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2405-5_0_3_load_32 | 8 | 0.016175 | 0.0040539 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2405-5_0_3_load_53 | 10 | 0.00092882 | 0.00023278 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2405-5_0_3_load_8 | 13 | 0.02506 | 0.0062806 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2405-5_0_3_load_36 | 14 | 0.0070637 | 0.0017703 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2405-5_0_3_load_34 | 15 | 0.0076551 | 0.0019185 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2405-5_0_3_load_10 | 19 | 0.0011581 | 0.00029024 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2405-5_0_3_load_11 | 20 | 0.0053301 | 0.0013358 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2405-5_0_3_load_14 | 23 | 0.0088858 | 0.002227 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2405-5_0_3_load_15 | 24 | 0.003954 | 0.00099097 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2405-5_0_3_load_57 | 26 | 0.0035242 | 0.00088325 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2405-5_0_3_load_16 | 28 | 0.001553 | 0.00038922 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2405-5_0_3_load_38 | 29 | 0.0017214 | 0.00043142 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2405-5_0_3_load_17 | 30 | 0.004308 | 0.0010797 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2405-5_0_3_load_58 | 31 | 0.02386 | 0.0059798 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2405-5_0_3_load_21 | 32 | 0.0058452 | 0.001465 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2405-5_0_3_load_22 | 33 | 0.0058395 | 0.0014635 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2405-5_0_3_load_51 | 36 | 0.0024069 | 0.00060323 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2405-5_0_3_load_25 | 37 | 0.0020659 | 0.00051777 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2405-5_0_3_load_26 | 38 | 0.0059009 | 0.0014789 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2405-5_0_3_load_29 | 41 | 0.0082229 | 0.0020608 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2405-5_0_3_load_54 | 44 | 0.0082199 | 0.0020601 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2405-5_0_3_load_39 | 45 | 0.01126 | 0.0028221 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2405-5_0_3_load_56 | 46 | 0.0015335 | 0.00038433 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2405-5_0_3_load_55 | 47 | 0.0082196 | 0.00206 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2405-5_0_3_load_37 | 49 | 0.0035785 | 0.00089685 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2405-5_0_3_load_46 | 50 | 0.0076419 | 0.0019152 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2405-5_0_3_load_52 | 51 | 0.0018234 | 0.00045698 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2405-5_0_3_load_47 | 52 | 0.0076583 | 0.0019193 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 2 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2405-5_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.025228 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
1 | LV_2405-5_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.052073 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
2 | LV_2405-5_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.012016 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
3 | LV_2405-5_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.027064 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2405-5_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.019366 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2405-5_0_3_line_5 | NAYY 4x150 SE | 3 | 6 | 0.045368 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2405-5_0_3_line_6 | NAYY 4x150 SE | 4 | 7 | 0.038294 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2405-5_0_3_line_7 | NAYY 4x150 SE | 5 | 8 | 0.0055911 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2405-5_0_3_line_8 | NAYY 4x150 SE | 6 | 9 | 0.018847 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2405-5_0_3_line_9 | NAYY 4x150 SE | 7 | 10 | 0.017987 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2405-5_0_3_line_10 | NAYY 4x150 SE | 7 | 11 | 0.027499 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2405-5_0_3_line_11 | NAYY 4x150 SE | 8 | 18 | 0.0078814 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2405-5_0_3_line_12 | NAYY 4x150 SE | 9 | 12 | 0.013763 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2405-5_0_3_line_13 | NAYY 4x150 SE | 9 | 13 | 0.025081 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2405-5_0_3_line_14 | NAYY 4x150 SE | 11 | 29 | 0.014054 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2405-5_0_3_line_15 | NAYY 4x150 SE | 11 | 23 | 0.017121 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2405-5_0_3_line_16 | NAYY 4x150 SE | 12 | 14 | 0.02692 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2405-5_0_3_line_17 | NAYY 4x150 SE | 12 | 15 | 0.059015 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2405-5_0_3_line_18 | NAYY 4x150 SE | 14 | 16 | 0.0041123 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2405-5_0_3_line_19 | NAYY 4x150 SE | 15 | 17 | 0.016727 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2405-5_0_3_line_20 | NAYY 4x150 SE | 16 | 34 | 0.026684 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2405-5_0_3_line_21 | NAYY 4x150 SE | 16 | 33 | 0.020472 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2405-5_0_3_line_22 | NAYY 4x150 SE | 17 | 49 | 0.016766 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2405-5_0_3_line_23 | NAYY 4x150 SE | 18 | 43 | 0.03449 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2405-5_0_3_line_24 | NAYY 4x150 SE | 19 | 20 | 0.042128 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2405-5_0_3_line_25 | NAYY 4x150 SE | 19 | 21 | 0.054938 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2405-5_0_3_line_26 | NAYY 4x150 SE | 20 | 22 | 0.018996 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2405-5_0_3_line_27 | NAYY 4x150 SE | 21 | 23 | 0.0055744 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2405-5_0_3_line_28 | NAYY 4x150 SE | 21 | 24 | 0.013843 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2405-5_0_3_line_29 | NAYY 4x150 SE | 22 | 25 | 0.034259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2405-5_0_3_line_30 | NAYY 4x150 SE | 24 | 26 | 0.017568 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2405-5_0_3_line_31 | NAYY 4x150 SE | 25 | 27 | 0.049316 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2405-5_0_3_line_32 | NAYY 4x150 SE | 25 | 28 | 0.033323 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2405-5_0_3_line_33 | NAYY 4x150 SE | 27 | 31 | 0.028316 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2405-5_0_3_line_34 | NAYY 4x150 SE | 28 | 30 | 0.017995 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2405-5_0_3_line_35 | NAYY 4x150 SE | 29 | 46 | 0.017706 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2405-5_0_3_line_36 | NAYY 4x150 SE | 32 | 33 | 0.00064657 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2405-5_0_3_line_37 | NAYY 4x150 SE | 34 | 35 | 0.00714 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2405-5_0_3_line_38 | NAYY 4x150 SE | 34 | 36 | 0.015837 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_2405-5_0_3_line_39 | NAYY 4x150 SE | 35 | 50 | 0.05313 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_2405-5_0_3_line_40 | NAYY 4x150 SE | 36 | 51 | 0.014831 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_2405-5_0_3_line_41 | NAYY 4x150 SE | 37 | 38 | 0.015278 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_2405-5_0_3_line_42 | NAYY 4x150 SE | 38 | 39 | 0.022812 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_2405-5_0_3_line_43 | NAYY 4x150 SE | 39 | 40 | 0.033082 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_2405-5_0_3_line_44 | NAYY 4x150 SE | 40 | 44 | 0.0080966 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_2405-5_0_3_line_45 | NAYY 4x150 SE | 40 | 42 | 0.016604 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_2405-5_0_3_line_46 | NAYY 4x150 SE | 41 | 42 | 0.019879 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_2405-5_0_3_line_47 | NAYY 4x150 SE | 42 | 45 | 0.066265 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_2405-5_0_3_line_48 | NAYY 4x150 SE | 43 | 47 | 0.024246 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_2405-5_0_3_line_49 | NAYY 4x150 SE | 43 | 48 | 0.003424 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_2405-5_0_3_line_50 | NAYY 4x150 SE | 44 | 48 | 0.036818 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_2405-5_0_3_line_51 | NAYY 4x150 SE | 50 | 52 | 0.032549 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2405-5_0_3_trafo_2 | 0.25 MVA 20/0.4 kV | 53 | 2 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2625232.7658 | 1238787.9004 | 2625233.2032 | 1238791.396 | 2625233.2018 | 1238793.4973 | 2625232.8025 | 1238796.6976 | 2625231.204 | 1238800.9046 | 2625225.1747 | 1238811.1394
1 | 2625232.7658 | 1238787.9004 | 2625232.6033 | 1238786.6016 | 2625232.1976 | 1238782.3972 | 2625232.5969 | 1238779.1969 | 2625233.2005 | 1238775.9975 | 2625234.9989 | 1238772.8031 | 2625244.8022 | 1238754.7001 | 2625250.5003 | 1238743.306 | 2625251.7776 | 1238740.5181
2 | 2625218.1032 | 1238820.8059 | 2625220.9001 | 1238817.6047 | 2625222.9002 | 1238815.0004 | 2625225.1747 | 1238811.1394
3 | 2625251.7776 | 1238740.5181 | 2625263.0501 | 1238715.9131
4 | 2625218.1032 | 1238820.8059 | 2625212.0016 | 1238814.9987 | 2625203.5232 | 1238808.0809
5 | 2625218.1032 | 1238820.8059 | 2625222.004 | 1238824.8027 | 2625225.2985 | 1238829.0972 | 2625229.0987 | 1238835.4061 | 2625232.4018 | 1238844.8038 | 2625234.2036 | 1238851.5045 | 2625236.3677 | 1238861.3752
6 | 2625278.9003 | 1238681.0988 | 2625273.6021 | 1238690.9047 | 2625266.4022 | 1238708.5963 | 2625263.0501 | 1238715.9131
7 | 2625199.1361 | 1238804.615 | 2625203.3037 | 1238807.9018 | 2625203.5232 | 1238808.0809
8 | 2625239.203 | 1238879.9991 | 2625237.0972 | 1238864.7028 | 2625236.3677 | 1238861.3752
9 | 2625278.9003 | 1238681.0988 | 2625294.4253 | 1238690.1822
10 | 2625278.9003 | 1238681.0988 | 2625257.4279 | 1238668.6221 | 2625255.1267 | 1238667.2781
11 | 2625192.9084 | 1238799.7861 | 2625194.3033 | 1238800.8037 | 2625199.1361 | 1238804.615
12 | 2625239.203 | 1238879.9991 | 2625252.6037 | 1238876.6983
13 | 2625239.203 | 1238879.9991 | 2625240.8735 | 1238905.0245
14 | 2625255.1267 | 1238667.2781 | 2625248.8211 | 1238679.8385
15 | 2625255.1267 | 1238667.2781 | 2625240.3227 | 1238658.677
16 | 2625252.6037 | 1238876.6983 | 2625259.0583 | 1238872.3785 | 2625263.6618 | 1238867.6173 | 2625269.8467 | 1238856.7196
17 | 2625252.6037 | 1238876.6983 | 2625254.8007 | 1238879.3982 | 2625257.8002 | 1238881.9014 | 2625261.4044 | 1238884.4961 | 2625302.6996 | 1238907.3267
18 | 2625271.8764 | 1238853.1432 | 2625269.8467 | 1238856.7196
19 | 2625317.3383 | 1238915.4198 | 2625302.6996 | 1238907.3267
20 | 2625271.8764 | 1238853.1432 | 2625284.9085 | 1238829.8395
21 | 2625271.8764 | 1238853.1432 | 2625289.9008 | 1238862.8507
22 | 2625317.3383 | 1238915.4198 | 2625325.2855 | 1238900.6571
23 | 2625164.9346 | 1238779.4995 | 2625192.9084 | 1238799.7861
24 | 2625240.7865 | 1238612.1824 | 2625249.2837 | 1238596.9761 | 2625259.8975 | 1238574.6635
25 | 2625235.5027 | 1238655.8767 | 2625225.5133 | 1238650.0751 | 2625224.1944 | 1238648.9688 | 2625223.3006 | 1238647.4975 | 2625222.922 | 1238645.8059 | 2625223.1032 | 1238644.0945 | 2625223.8284 | 1238642.5299 | 2625240.7865 | 1238612.1824
26 | 2625268.0576 | 1238557.5089 | 2625259.8975 | 1238574.6635
27 | 2625235.5027 | 1238655.8767 | 2625240.3227 | 1238658.677
28 | 2625235.5027 | 1238655.8767 | 2625228.474 | 1238667.803
29 | 2625268.0576 | 1238557.5089 | 2625274.8468 | 1238567.0882 | 2625294.1141 | 1238578.8552
30 | 2625219.5544 | 1238682.9378 | 2625228.474 | 1238667.803
31 | 2625294.1141 | 1238578.8552 | 2625328.4429 | 1238600.6482 | 2625332.5605 | 1238605.2463 | 2625332.9884 | 1238607.7831
32 | 2625294.1141 | 1238578.8552 | 2625311.9778 | 1238550.7247
33 | 2625323.4846 | 1238633.6032 | 2625331.8137 | 1238618.9851 | 2625333.6819 | 1238611.8886 | 2625332.9884 | 1238607.7831
34 | 2625327.2939 | 1238560.1718 | 2625311.9778 | 1238550.7247 | 2625311.9778 | 1238550.7247
35 | 2625248.8211 | 1238679.8385 | 2625240.8772 | 1238695.6621
36 | 2625290.47 | 1238863.1573 | 2625289.9008 | 1238862.8507
37 | 2625288.399 | 1238823.606 | 2625284.9085 | 1238829.8395
38 | 2625284.9085 | 1238829.8395 | 2625270.5364 | 1238823.1872
39 | 2625288.399 | 1238823.606 | 2625335.199 | 1238848.7576
40 | 2625257.0777 | 1238816.9577 | 2625270.5364 | 1238823.1872
41 | 2625224.1931 | 1238736.1787 | 2625230.9362 | 1238722.4691
42 | 2625214.1247 | 1238756.649 | 2625224.1931 | 1238736.1787
43 | 2625185.9802 | 1238739.13 | 2625214.1247 | 1238756.649
44 | 2625185.9802 | 1238739.13 | 2625181.7123 | 1238746.0104
45 | 2625185.9802 | 1238739.13 | 2625194.7454 | 1238725.0138
46 | 2625194.7454 | 1238725.0138 | 2625205.2242 | 1238708.1206
47 | 2625194.7454 | 1238725.0138 | 2625168.6409 | 1238709.7382 | 2625179.09 | 1238689.114 | 2625167.6326 | 1238683.187
48 | 2625164.9346 | 1238779.4995 | 2625177.4342 | 1238758.7236
49 | 2625162.3044 | 1238777.2981 | 2625164.9346 | 1238779.4995
50 | 2625162.3044 | 1238777.2981 | 2625181.7123 | 1238746.0104
51 | 2625335.199 | 1238848.7576 | 2625363.8701 | 1238864.1662

## bus_geodata
| x | y | coords
0 | 2625232.7658 | 1238787.9004
1 | 2625225.1747 | 1238811.1394
2 | 2625251.7776 | 1238740.5181
3 | 2625218.1032 | 1238820.8059
4 | 2625263.0501 | 1238715.9131
5 | 2625203.5232 | 1238808.0809
6 | 2625236.3677 | 1238861.3752
7 | 2625278.9003 | 1238681.0988
8 | 2625199.1361 | 1238804.615
9 | 2625239.203 | 1238879.9991
10 | 2625294.4253 | 1238690.1822
11 | 2625255.1267 | 1238667.2781
12 | 2625252.6037 | 1238876.6983
13 | 2625240.8735 | 1238905.0245
14 | 2625269.8467 | 1238856.7196
15 | 2625302.6996 | 1238907.3267
16 | 2625271.8764 | 1238853.1432
17 | 2625317.3383 | 1238915.4198
18 | 2625192.9084 | 1238799.7861
19 | 2625240.7865 | 1238612.1824
20 | 2625259.8975 | 1238574.6635
21 | 2625235.5027 | 1238655.8767
22 | 2625268.0576 | 1238557.5089
23 | 2625240.3227 | 1238658.677
24 | 2625228.474 | 1238667.803
25 | 2625294.1141 | 1238578.8552
26 | 2625219.5544 | 1238682.9378
27 | 2625332.9884 | 1238607.7831
28 | 2625311.9778 | 1238550.7247
29 | 2625248.8211 | 1238679.8385
30 | 2625327.2939 | 1238560.1718
31 | 2625323.4846 | 1238633.6032
32 | 2625290.47 | 1238863.1573
33 | 2625289.9008 | 1238862.8507
34 | 2625284.9085 | 1238829.8395
35 | 2625288.399 | 1238823.606
36 | 2625270.5364 | 1238823.1872
37 | 2625230.9362 | 1238722.4691
38 | 2625224.1931 | 1238736.1787
39 | 2625214.1247 | 1238756.649
40 | 2625185.9802 | 1238739.13
41 | 2625205.2242 | 1238708.1206
42 | 2625194.7454 | 1238725.0138
43 | 2625164.9346 | 1238779.4995
44 | 2625181.7123 | 1238746.0104
45 | 2625167.6326 | 1238683.187
46 | 2625240.8772 | 1238695.6621
47 | 2625177.4342 | 1238758.7236
48 | 2625162.3044 | 1238777.2981
49 | 2625325.2855 | 1238900.6571
50 | 2625335.199 | 1238848.7576
51 | 2625257.0777 | 1238816.9577
52 | 2625363.8701 | 1238864.1662
53 | 2625278.9003 | 1238681.0988

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99434 | -0.039171 | 0.0016364 | 0.00041011
1 | 0.99163 | -0.058099 | 0.0022357 | 0.00056031
2 | 1 | 0 | -0.21262 | -0.053525
3 | 0.99036 | -0.067014 | 0 | 0
4 | 0.99771 | -0.015882 | 0.001862 | 0.00046666
5 | 0.98858 | -0.079518 | 0.0032467 | 0.00081369
6 | 0.98491 | -0.10539 | 0.0080564 | 0.0020191
7 | 0.99456 | -0.037758 | 0 | 0
8 | 0.9881 | -0.082951 | 0.016175 | 0.0040539
9 | 0.98287 | -0.11988 | 0 | 0
10 | 0.99454 | -0.037927 | 0.00092882 | 0.00023278
11 | 0.99234 | -0.053293 | 0 | 0
12 | 0.98187 | -0.12693 | 0 | 0
13 | 0.98195 | -0.12638 | 0.02506 | 0.0062806
14 | 0.98037 | -0.13762 | 0.0070637 | 0.0017703
15 | 0.98091 | -0.13381 | 0.0076551 | 0.0019185
16 | 0.98019 | -0.13896 | 0 | 0
17 | 0.98082 | -0.13443 | 0 | 0
18 | 0.98759 | -0.086491 | 0 | 0
19 | 0.9878 | -0.085211 | 0.0011581 | 0.00029024
20 | 0.98565 | -0.10036 | 0.0053301 | 0.0013358
21 | 0.99068 | -0.06491 | 0 | 0
22 | 0.98483 | -0.10616 | 0 | 0
23 | 0.99104 | -0.062433 | 0.0088858 | 0.002227
24 | 0.99053 | -0.065963 | 0.003954 | 0.00099097
25 | 0.98335 | -0.11666 | 0 | 0
26 | 0.99045 | -0.066593 | 0.0035242 | 0.00088325
27 | 0.98164 | -0.12883 | 0 | 0
28 | 0.98307 | -0.11868 | 0.001553 | 0.00038922
29 | 0.99227 | -0.053757 | 0.0017214 | 0.00043142
30 | 0.98296 | -0.11948 | 0.004308 | 0.0010797
31 | 0.98066 | -0.13583 | 0.02386 | 0.0059798
32 | 0.97983 | -0.14148 | 0.0058452 | 0.001465
33 | 0.97984 | -0.14144 | 0.0058395 | 0.0014635
34 | 0.97943 | -0.14438 | 0 | 0
35 | 0.97927 | -0.14552 | 0 | 0
36 | 0.97933 | -0.14508 | 0.0024069 | 0.00060323
37 | 0.9823 | -0.12404 | 0.0020659 | 0.00051777
38 | 0.98235 | -0.12372 | 0.0059009 | 0.0014789
39 | 0.98261 | -0.12184 | 0 | 0
40 | 0.98299 | -0.11911 | 0 | 0
41 | 0.98229 | -0.12415 | 0.0082229 | 0.0020608
42 | 0.98252 | -0.12246 | 0 | 0
43 | 0.9854 | -0.10202 | 0 | 0
44 | 0.98332 | -0.11682 | 0.0082199 | 0.0020601
45 | 0.98144 | -0.13018 | 0.01126 | 0.0028221
46 | 0.99224 | -0.054032 | 0.0015335 | 0.00038433
47 | 0.98511 | -0.10407 | 0.0082196 | 0.00206
48 | 0.98522 | -0.10328 | 0 | 0
49 | 0.98074 | -0.13505 | 0.0035785 | 0.00089685
50 | 0.97808 | -0.15399 | 0.0076419 | 0.0019152
51 | 0.97929 | -0.14536 | 0.0018234 | 0.00045698
52 | 0.97772 | -0.15659 | 0.0076583 | 0.0019193
53 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.14991 | 0.037792 | -0.14951 | -0.03764 | 0.00039641 | 0.00015181 | 0.22441 | 0.22441 | 0.22441 | 0.99434 | -0.039171 | 0.99163 | -0.058099 | 41.5579
1 | -0.15154 | -0.038202 | 0.15238 | 0.038523 | 0.00083615 | 0.00032024 | 0.22686 | 0.22686 | 0.22686 | 0.99434 | -0.039171 | 1 | 0 | 42.0113
2 | 0.14728 | 0.03708 | -0.14709 | -0.03701 | 0.0001832 | 7.0151e-05 | 0.22106 | 0.22106 | 0.22106 | 0.99163 | -0.058099 | 0.99036 | -0.067014 | 40.9366
3 | 0.059443 | 0.015002 | -0.059311 | -0.014952 | 0.00013224 | 5.0507e-05 | 0.088489 | 0.088489 | 0.088489 | 1 | 0 | 0.99771 | -0.015882 | 32.7738
4 | 0.06368 | 0.016005 | -0.063569 | -0.015963 | 0.00011066 | 4.2315e-05 | 0.095696 | 0.095696 | 0.095696 | 0.99036 | -0.067014 | 0.98858 | -0.079518 | 35.4429
5 | 0.083412 | 0.021005 | -0.082967 | -0.020834 | 0.0004449 | 0.00017054 | 0.12536 | 0.12536 | 0.12536 | 0.99036 | -0.067014 | 0.98491 | -0.10539 | 46.4304
6 | 0.057449 | 0.014485 | -0.057273 | -0.014418 | 0.00017555 | 6.7021e-05 | 0.085712 | 0.085712 | 0.085712 | 0.99771 | -0.015882 | 0.99456 | -0.037758 | 31.7453
7 | 0.060323 | 0.015149 | -0.060294 | -0.015138 | 2.877e-05 | 1.0994e-05 | 0.090809 | 0.090809 | 0.090809 | 0.98858 | -0.079518 | 0.9881 | -0.082951 | 33.633
8 | 0.07491 | 0.018815 | -0.07476 | -0.018757 | 0.00015068 | 5.7714e-05 | 0.11319 | 0.11319 | 0.11319 | 0.98491 | -0.10539 | 0.98287 | -0.11988 | 41.9224
9 | 0.00092884 | 0.00023256 | -0.00092882 | -0.00023278 | 2.1675e-08 | -2.2508e-07 | 0.0013896 | 0.0013897 | 0.0013897 | 0.99456 | -0.037758 | 0.99454 | -0.037927 | 0.5147
10 | 0.056345 | 0.014185 | -0.056223 | -0.014139 | 0.00012201 | 4.657e-05 | 0.084323 | 0.084323 | 0.084323 | 0.99456 | -0.037758 | 0.99234 | -0.053293 | 31.2307
11 | 0.044119 | 0.011084 | -0.044097 | -0.011076 | 2.1716e-05 | 8.2515e-06 | 0.06645 | 0.06645 | 0.06645 | 0.9881 | -0.082951 | 0.98759 | -0.086491 | 24.6112
12 | 0.049677 | 0.012469 | -0.049629 | -0.01245 | 4.8587e-05 | 1.8513e-05 | 0.075216 | 0.075216 | 0.075216 | 0.98287 | -0.11988 | 0.98187 | -0.12693 | 27.8577
13 | 0.025082 | 0.006289 | -0.02506 | -0.0062806 | 2.2569e-05 | 8.363e-06 | 0.037975 | 0.037975 | 0.037975 | 0.98287 | -0.11988 | 0.98195 | -0.12638 | 14.0647
14 | 0.0032552 | 0.00081545 | -0.003255 | -0.00081555 | 2.0894e-07 | -1.012e-07 | 0.004881 | 0.0048811 | 0.0048811 | 0.99234 | -0.053293 | 0.99227 | -0.053757 | 1.8078
15 | 0.052967 | 0.013323 | -0.0529 | -0.013298 | 6.7425e-05 | 2.5712e-05 | 0.079442 | 0.079442 | 0.079442 | 0.99234 | -0.053293 | 0.99104 | -0.062433 | 29.4229
16 | 0.038384 | 0.0096314 | -0.038327 | -0.0096099 | 5.6849e-05 | 2.1525e-05 | 0.058174 | 0.058174 | 0.058174 | 0.98187 | -0.12693 | 0.98037 | -0.13762 | 21.5461
17 | 0.011245 | 0.0028186 | -0.011234 | -0.0028152 | 1.0695e-05 | 3.3677e-06 | 0.017042 | 0.017042 | 0.017042 | 0.98187 | -0.12693 | 0.98091 | -0.13381 | 6.3118
18 | 0.031263 | 0.0078396 | -0.031258 | -0.0078374 | 5.7783e-06 | 2.1706e-06 | 0.047453 | 0.047453 | 0.047453 | 0.98037 | -0.13762 | 0.98019 | -0.13896 | 17.5752
19 | 0.0035791 | 0.00089667 | -0.0035788 | -0.00089676 | 3.0767e-07 | -9.2792e-08 | 0.0054293 | 0.0054294 | 0.0054294 | 0.98091 | -0.13381 | 0.98082 | -0.13443 | 2.0109
20 | 0.019569 | 0.0049076 | -0.019554 | -0.0049023 | 1.4696e-05 | 5.3162e-06 | 0.029708 | 0.029709 | 0.029709 | 0.98019 | -0.13896 | 0.97943 | -0.14438 | 11.0032
21 | 0.011689 | 0.0029298 | -0.011685 | -0.0029285 | 4.0224e-06 | 1.2891e-06 | 0.017745 | 0.017745 | 0.017745 | 0.98019 | -0.13896 | 0.97984 | -0.14144 | 6.5722
22 | 0.0035788 | 0.00089676 | -0.0035785 | -0.00089685 | 3.084e-07 | -9.2967e-08 | 0.0054294 | 0.0054294 | 0.0054294 | 0.98082 | -0.13443 | 0.98074 | -0.13505 | 2.0109
23 | 0.044097 | 0.011076 | -0.044002 | -0.01104 | 9.5033e-05 | 3.6111e-05 | 0.06645 | 0.06645 | 0.06645 | 0.98759 | -0.086491 | 0.9854 | -0.10202 | 24.6113
24 | 0.035258 | 0.0088614 | -0.035184 | -0.0088334 | 7.4182e-05 | 2.7993e-05 | 0.053122 | 0.053122 | 0.053122 | 0.9878 | -0.085211 | 0.98565 | -0.10036 | 19.6747
25 | -0.036416 | -0.0091517 | 0.036519 | 0.0091907 | 0.0001032 | 3.8985e-05 | 0.054866 | 0.054866 | 0.054866 | 0.9878 | -0.085211 | 0.99068 | -0.06491 | 20.3208
26 | 0.029854 | 0.0074976 | -0.02983 | -0.0074886 | 2.4084e-05 | 9.0212e-06 | 0.045075 | 0.045075 | 0.045075 | 0.98565 | -0.10036 | 0.98483 | -0.10616 | 16.6945
27 | -0.043999 | -0.011065 | 0.044014 | 0.011071 | 1.5198e-05 | 5.7736e-06 | 0.0661 | 0.0661 | 0.0661 | 0.99068 | -0.06491 | 0.99104 | -0.062433 | 24.4816
28 | 0.0074796 | 0.0018743 | -0.0074785 | -0.0018741 | 1.0902e-06 | 2.4111e-07 | 0.011234 | 0.011234 | 0.011234 | 0.99068 | -0.06491 | 0.99053 | -0.065963 | 4.1609
29 | 0.02983 | 0.0074886 | -0.029786 | -0.0074723 | 4.3435e-05 | 1.627e-05 | 0.045075 | 0.045075 | 0.045075 | 0.98483 | -0.10616 | 0.98335 | -0.11666 | 16.6946
30 | 0.0035245 | 0.00088314 | -0.0035242 | -0.00088325 | 3.073e-07 | -1.0792e-07 | 0.0052946 | 0.0052947 | 0.0052947 | 0.99053 | -0.065963 | 0.99045 | -0.066593 | 1.961
31 | 0.023923 | 0.0060032 | -0.023883 | -0.0059883 | 4.0334e-05 | 1.4889e-05 | 0.036203 | 0.036204 | 0.036204 | 0.98335 | -0.11666 | 0.98164 | -0.12883 | 13.4087
32 | 0.0058631 | 0.0014691 | -0.0058615 | -0.0014689 | 1.6367e-06 | 2.069e-07 | 0.008872 | 0.0088721 | 0.0088721 | 0.98335 | -0.11666 | 0.98307 | -0.11868 | 3.286
33 | 0.023883 | 0.0059883 | -0.02386 | -0.0059798 | 2.3159e-05 | 8.5497e-06 | 0.036204 | 0.036204 | 0.036204 | 0.98164 | -0.12883 | 0.98066 | -0.13583 | 13.4088
34 | 0.0043085 | 0.0010796 | -0.004308 | -0.0010797 | 4.7757e-07 | -4.4453e-08 | 0.0065214 | 0.0065215 | 0.0065215 | 0.98307 | -0.11868 | 0.98296 | -0.11948 | 2.4154
35 | 0.0015336 | 0.00038413 | -0.0015335 | -0.00038433 | 5.8431e-08 | -2.0623e-07 | 0.0022997 | 0.0022997 | 0.0022997 | 0.99227 | -0.053757 | 0.99224 | -0.054032 | 0.85176
36 | -0.0058452 | -0.001465 | 0.0058453 | 0.001465 | 3.1792e-08 | 4.0836e-09 | 0.0088768 | 0.0088768 | 0.0088768 | 0.97983 | -0.14148 | 0.97984 | -0.14144 | 3.2877
37 | 0.015323 | 0.0038423 | -0.015321 | -0.0038415 | 2.4148e-06 | 8.3894e-07 | 0.023281 | 0.023281 | 0.023281 | 0.97943 | -0.14438 | 0.97927 | -0.14552 | 8.6226
38 | 0.0042308 | 0.00106 | -0.0042303 | -0.00106 | 4.0827e-07 | -4.2261e-08 | 0.0064275 | 0.0064276 | 0.0064276 | 0.97943 | -0.14438 | 0.97933 | -0.14508 | 2.3806
39 | 0.015321 | 0.0038415 | -0.015303 | -0.0038352 | 1.797e-05 | 6.2437e-06 | 0.023281 | 0.023281 | 0.023281 | 0.97927 | -0.14552 | 0.97808 | -0.15399 | 8.6227
40 | 0.0018234 | 0.00045682 | -0.0018234 | -0.00045698 | 7.1035e-08 | -1.5928e-07 | 0.0027705 | 0.0027706 | 0.0027706 | 0.97933 | -0.14508 | 0.97929 | -0.14536 | 1.0261
41 | -0.0020659 | -0.00051777 | 0.002066 | 0.00051761 | 9.3369e-08 | -1.5751e-07 | 0.0031295 | 0.0031294 | 0.0031295 | 0.9823 | -0.12404 | 0.98235 | -0.12372 | 1.1591
42 | -0.0079669 | -0.0019965 | 0.007969 | 0.001997 | 2.0731e-06 | 5.0845e-07 | 0.012068 | 0.012068 | 0.012068 | 0.98235 | -0.12372 | 0.98261 | -0.12184 | 4.4696
43 | -0.007969 | -0.001997 | 0.007972 | 0.0019978 | 3.0063e-06 | 7.3705e-07 | 0.012068 | 0.012068 | 0.012068 | 0.98261 | -0.12184 | 0.98299 | -0.11911 | 4.4696
44 | -0.027478 | -0.0068883 | 0.027487 | 0.0068916 | 8.7417e-06 | 3.2595e-06 | 0.041596 | 0.041596 | 0.041596 | 0.98299 | -0.11911 | 0.98332 | -0.11682 | 15.406
45 | 0.019506 | 0.0048905 | -0.019497 | -0.0048873 | 9.0341e-06 | 3.2643e-06 | 0.029529 | 0.029529 | 0.029529 | 0.98299 | -0.11911 | 0.98252 | -0.12246 | 10.9365
46 | -0.0082229 | -0.0020608 | 0.0082248 | 0.0020613 | 1.9247e-06 | 4.8857e-07 | 0.012456 | 0.012456 | 0.012456 | 0.98229 | -0.12415 | 0.98252 | -0.12246 | 4.6135
47 | 0.011273 | 0.0028259 | -0.01126 | -0.0028221 | 1.2052e-05 | 3.7971e-06 | 0.017072 | 0.017073 | 0.017073 | 0.98252 | -0.12246 | 0.98144 | -0.13018 | 6.3232
48 | 0.0082219 | 0.0020606 | -0.0082196 | -0.00206 | 2.3322e-06 | 5.8823e-07 | 0.012416 | 0.012416 | 0.012416 | 0.9854 | -0.10202 | 0.98511 | -0.10407 | 4.5984
49 | 0.03578 | 0.0089793 | -0.035774 | -0.008977 | 6.2383e-06 | 2.3557e-06 | 0.054035 | 0.054035 | 0.054035 | 0.9854 | -0.10202 | 0.98522 | -0.10328 | 20.0129
50 | -0.035707 | -0.0089517 | 0.035774 | 0.008977 | 6.7081e-05 | 2.5332e-05 | 0.054035 | 0.054035 | 0.054035 | 0.98332 | -0.11682 | 0.98522 | -0.10328 | 20.013
51 | 0.007661 | 0.00192 | -0.0076583 | -0.0019193 | 2.7591e-06 | 6.5284e-07 | 0.011655 | 0.011655 | 0.011655 | 0.97808 | -0.15399 | 0.97772 | -0.15659 | 4.3168

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.21432 | 0.053951

## res_load
| p_mw | q_mvar
0 | 0.0016364 | 0.00041011
1 | 0.0022357 | 0.00056031
2 | 0.0016993 | 0.00042589
3 | 0.001862 | 0.00046666
4 | 0.0032467 | 0.00081369
5 | 0.0080564 | 0.0020191
6 | 0.016175 | 0.0040539
7 | 0.00092882 | 0.00023278
8 | 0.02506 | 0.0062806
9 | 0.0070637 | 0.0017703
10 | 0.0076551 | 0.0019185
11 | 0.0011581 | 0.00029024
12 | 0.0053301 | 0.0013358
13 | 0.0088858 | 0.002227
14 | 0.003954 | 0.00099097
15 | 0.0035242 | 0.00088325
16 | 0.001553 | 0.00038922
17 | 0.0017214 | 0.00043142
18 | 0.004308 | 0.0010797
19 | 0.02386 | 0.0059798
20 | 0.0058452 | 0.001465
21 | 0.0058395 | 0.0014635
22 | 0.0024069 | 0.00060323
23 | 0.0020659 | 0.00051777
24 | 0.0059009 | 0.0014789
25 | 0.0082229 | 0.0020608
26 | 0.0082199 | 0.0020601
27 | 0.01126 | 0.0028221
28 | 0.0015335 | 0.00038433
29 | 0.0082196 | 0.00206
30 | 0.0035785 | 0.00089685
31 | 0.0076419 | 0.0019152
32 | 0.0018234 | 0.00045698
33 | 0.0076583 | 0.0019193

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1