## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2406-10_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2406-10_0_3_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_2406-10_0_3_node_30 | 0.4 | n |  | TRUE
3 | bus_LV_2406-10_0_3_node_1 | 0.4 | n |  | TRUE
4 | bus_LV_2406-10_0_3_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_2406-10_0_3_node_66 | 0.4 | n |  | TRUE
6 | bus_LV_2406-10_0_3_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_2406-10_0_3_node_14 | 0.4 | n |  | TRUE
8 | bus_LV_2406-10_0_3_node_15 | 0.4 | n |  | TRUE
9 | bus_LV_2406-10_0_3_node_16 | 0.4 | n |  | TRUE
10 | bus_LV_2406-10_0_3_node_114 | 0.4 | n |  | TRUE
11 | bus_LV_2406-10_0_3_node_17 | 0.4 | n |  | TRUE
12 | bus_LV_2406-10_0_3_node_23 | 0.4 | n |  | TRUE
13 | bus_LV_2406-10_0_3_node_22 | 0.4 | n |  | TRUE
14 | bus_LV_2406-10_0_3_node_29 | 0.4 | n |  | TRUE
15 | bus_LV_2406-10_0_3_node_28 | 0.4 | n |  | TRUE
16 | bus_LV_2406-10_0_3_node_31 | 0.4 | n |  | TRUE
17 | bus_LV_2406-10_0_3_node_67 | 0.4 | n |  | TRUE
18 | bus_LV_2406-10_0_3_node_80 | 0.4 | n |  | TRUE
19 | bus_LV_2406-10_0_3_node_37 | 0.4 | n |  | TRUE
20 | bus_LV_2406-10_0_3_node_38 | 0.4 | n |  | TRUE
21 | bus_LV_2406-10_0_3_node_65 | 0.4 | n |  | TRUE
22 | bus_LV_2406-10_0_3_node_96 | 0.4 | n |  | TRUE
23 | bus_LV_2406-10_0_3_node_81 | 0.4 | n |  | TRUE
24 | bus_LV_2406-10_0_3_node_82 | 0.4 | n |  | TRUE
25 | bus_LV_2406-10_0_3_node_93 | 0.4 | n |  | TRUE
26 | bus_LV_2406-10_0_3_node_87 | 0.4 | n |  | TRUE
27 | bus_LV_2406-10_0_3_node_88 | 0.4 | n |  | TRUE
28 | bus_LV_2406-10_0_3_node_89 | 0.4 | n |  | TRUE
29 | bus_LV_2406-10_0_3_node_90 | 0.4 | n |  | TRUE
30 | bus_LV_2406-10_0_3_node_106 | 0.4 | n |  | TRUE
31 | bus_LV_2406-10_0_3_node_94 | 0.4 | n |  | TRUE
32 | bus_LV_2406-10_0_3_node_113 | 0.4 | n |  | TRUE
33 | bus_MV_0_node_29 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2406-10_0_3_load_0 | 0 | 0.00046217 | 0.00011583 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2406-10_0_3_load_2 | 1 | 0.00038721 | 9.7043e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2406-10_0_3_load_30 | 2 | 0.0022082 | 0.00055343 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2406-10_0_3_load_1 | 3 | 0.0011402 | 0.00028577 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2406-10_0_3_load_3 | 4 | 0.0014932 | 0.00037422 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2406-10_0_3_load_66 | 5 | 0.0018692 | 0.00046848 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2406-10_0_3_load_4 | 6 | 0.0091804 | 0.0023008 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2406-10_0_3_load_14 | 7 | 0.0033724 | 0.0008452 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2406-10_0_3_load_15 | 8 | 0.0021107 | 0.00052898 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2406-10_0_3_load_23 | 12 | 0.0020207 | 0.00050643 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2406-10_0_3_load_22 | 13 | 0.0013586 | 0.0003405 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2406-10_0_3_load_29 | 14 | 0.0022434 | 0.00056226 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2406-10_0_3_load_28 | 15 | 0.0021326 | 0.00053448 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2406-10_0_3_load_67 | 17 | 0.00058291 | 0.00014609 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2406-10_0_3_load_80 | 18 | 0.0015971 | 0.00040028 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2406-10_0_3_load_37 | 19 | 0.0010539 | 0.00026412 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2406-10_0_3_load_38 | 20 | 0.0021444 | 0.00053744 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2406-10_0_3_load_65 | 21 | 0.0012893 | 0.00032312 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2406-10_0_3_load_96 | 22 | 0.00070004 | 0.00017545 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2406-10_0_3_load_93 | 25 | 0.0069926 | 0.0017525 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2406-10_0_3_load_87 | 26 | 0.0010021 | 0.00025116 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2406-10_0_3_load_88 | 27 | 0.0020207 | 0.00050643 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2406-10_0_3_load_89 | 28 | 0.0035816 | 0.00089762 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2406-10_0_3_load_90 | 29 | 0.0019728 | 0.00049443 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2406-10_0_3_load_106 | 30 | 0.0012717 | 0.00031871 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2406-10_0_3_load_94 | 31 | 0.005616 | 0.0014075 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2406-10_0_3_load_113 | 32 | 0.0014826 | 0.00037158 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 14 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2406-10_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.010562 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2406-10_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.047451 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2406-10_0_3_line_2 | NAYY 4x150 SE | 1 | 6 | 0.0038452 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2406-10_0_3_line_3 | NAYY 4x150 SE | 2 | 16 | 0.034017 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2406-10_0_3_line_4 | NAYY 4x150 SE | 2 | 15 | 0.024374 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2406-10_0_3_line_5 | NAYY 4x150 SE | 3 | 4 | 0.025454 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2406-10_0_3_line_6 | NAYY 4x150 SE | 3 | 5 | 0.03346 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2406-10_0_3_line_7 | NAYY 4x150 SE | 5 | 17 | 0.01218 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2406-10_0_3_line_8 | NAYY 4x150 SE | 7 | 8 | 0.0065144 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2406-10_0_3_line_9 | NAYY 4x150 SE | 7 | 9 | 0.0058579 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2406-10_0_3_line_10 | NAYY 4x150 SE | 8 | 10 | 0.57306 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2406-10_0_3_line_11 | NAYY 4x150 SE | 9 | 11 | 0.012442 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2406-10_0_3_line_12 | NAYY 4x150 SE | 10 | 32 | 0.013609 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2406-10_0_3_line_13 | NAYY 4x150 SE | 11 | 12 | 0.039754 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2406-10_0_3_line_14 | NAYY 4x150 SE | 12 | 14 | 0.62013 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
15 | LV_2406-10_0_3_line_15 | NAYY 4x150 SE | 12 | 13 | 0.0033857 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2406-10_0_3_line_16 | NAYY 4x150 SE | 14 | 15 | 0.03637 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2406-10_0_3_line_17 | NAYY 4x150 SE | 16 | 17 | 0.010751 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2406-10_0_3_line_18 | NAYY 4x150 SE | 16 | 18 | 0.030813 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2406-10_0_3_line_19 | NAYY 4x150 SE | 18 | 23 | 0.016539 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2406-10_0_3_line_20 | NAYY 4x150 SE | 19 | 20 | 0.022115 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2406-10_0_3_line_21 | NAYY 4x150 SE | 20 | 21 | 0.0091149 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2406-10_0_3_line_22 | NAYY 4x150 SE | 21 | 22 | 0.019386 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2406-10_0_3_line_23 | NAYY 4x150 SE | 22 | 29 | 0.024917 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2406-10_0_3_line_24 | NAYY 4x150 SE | 23 | 24 | 0.004738 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2406-10_0_3_line_25 | NAYY 4x150 SE | 24 | 25 | 0.023061 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2406-10_0_3_line_26 | NAYY 4x150 SE | 25 | 31 | 0.03001 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2406-10_0_3_line_27 | NAYY 4x150 SE | 26 | 27 | 0.076119 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2406-10_0_3_line_28 | NAYY 4x150 SE | 26 | 28 | 0.034832 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2406-10_0_3_line_29 | NAYY 4x150 SE | 27 | 29 | 0.028686 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2406-10_0_3_line_30 | NAYY 4x150 SE | 29 | 30 | 0.032074 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2406-10_0_3_line_31 | NAYY 4x150 SE | 30 | 32 | 0.025738 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2406-10_0_3_trafo_29 | 0.25 MVA 20/0.4 kV | 33 | 14 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2625069.5295 | 1240558.4087 | 2625071.5263 | 1240560.8554 | 2625076.7793 | 1240566.0731
1 | 2625100.7717 | 1240522.6943 | 2625069.5295 | 1240558.4087
2 | 2625079.5075 | 1240568.7829 | 2625076.7793 | 1240566.0731
3 | 2625073.8029 | 1240503.3066 | 2625074.4007 | 1240504.999 | 2625075.6011 | 1240507.2055 | 2625077.6031 | 1240509.4042 | 2625079.9029 | 1240510.9037 | 2625086.3016 | 1240513.9993 | 2625092.8032 | 1240517.7958 | 2625100.7717 | 1240522.6943
4 | 2625100.7717 | 1240522.6943 | 2625121.5362 | 1240535.4588
5 | 2625033.5131 | 1240525.5675 | 2625017.3021 | 1240518.7562 | 2625011.6771 | 1240513.2513 | 2625011.6771 | 1240513.2513
6 | 2625052.0601 | 1240497.7188 | 2625033.5131 | 1240525.5675
7 | 2625052.0601 | 1240497.7188 | 2625063.2079 | 1240502.6251
8 | 2625514.4086 | 1241008.7918 | 2625513.5365 | 1241009.6842 | 2625508.9588 | 1241012.2885
9 | 2625518.5028 | 1241004.6023 | 2625514.4086 | 1241008.7918
10 | 2625064.6996 | 1240650.3052 | 2625508.9588 | 1241012.2885
11 | 2625518.5028 | 1241004.6023 | 2625521.0662 | 1241004.5133 | 2625526.5016 | 1241002.88 | 2625530.1474 | 1241000.7276
12 | 2625064.6996 | 1240650.3052 | 2625062.0983 | 1240646.8031 | 2625058.9014 | 1240642.8983 | 2625055.9573 | 1240639.9032
13 | 2625530.1474 | 1241000.7276 | 2625542.8989 | 1241006.6973 | 2625558.8012 | 1241013.1029 | 2625565.4015 | 1241016.6002 | 2625566.3432 | 1241017.0882
14 | 2625151.1229 | 1240556.483 | 2625566.3432 | 1241017.0882
15 | 2625566.3432 | 1241017.0882 | 2625569.3491 | 1241018.646
16 | 2625151.1229 | 1240556.483 | 2625146.8003 | 1240552.7013 | 2625142.2041 | 1240548.9017 | 2625137.7037 | 1240545.7029 | 2625129.8996 | 1240540.6001 | 2625121.5362 | 1240535.4588
17 | 2625073.8029 | 1240503.3066 | 2625069.8014 | 1240503.7011 | 2625066.8001 | 1240503.5995 | 2625063.5976 | 1240502.7966 | 2625063.2079 | 1240502.6251
18 | 2625073.8029 | 1240503.3066 | 2625079.6968 | 1240500.5964 | 2625086.2994 | 1240496.5995 | 2625092.9041 | 1240492.1023 | 2625097.7975 | 1240488.1982 | 2625099.532 | 1240486.6024
19 | 2625111.7034 | 1240475.4044 | 2625099.532 | 1240486.6024
20 | 2624962.6891 | 1240545.5641 | 2624970.3986 | 1240551.7021 | 2624979.6978 | 1240559.1013 | 2624979.9877 | 1240559.3413
21 | 2624987.009 | 1240565.1537 | 2624979.9877 | 1240559.3413
22 | 2624987.009 | 1240565.1537 | 2625001.202 | 1240576.9029 | 2625001.829 | 1240577.631
23 | 2625017.8748 | 1240596.4742 | 2625008.8978 | 1240587.9978 | 2625006.5993 | 1240584.3969 | 2625003.7001 | 1240579.8041 | 2625001.829 | 1240577.631
24 | 2625115.481 | 1240472.5297 | 2625111.7034 | 1240475.4044
25 | 2625115.481 | 1240472.5297 | 2625120.8971 | 1240468.4055 | 2625132.235 | 1240456.7589
26 | 2625132.235 | 1240456.7589 | 2625142.8972 | 1240445.8065 | 2625152.9468 | 1240435.0438
27 | 2624951.1107 | 1240655.1581 | 2624951.3819 | 1240654.5759 | 2624951.5754 | 1240646.2826 | 2624953.6369 | 1240639.7205 | 2624959.2017 | 1240630.7048 | 2624970.6989 | 1240609.8066 | 2624976.0907 | 1240602.4023 | 2624981.2738 | 1240601.4902 | 2624986.6038 | 1240603.3915 | 2624992.0156 | 1240605.4069
28 | 2624932.4605 | 1240635.718 | 2624934.9395 | 1240644.9565 | 2624937.5874 | 1240649.9818 | 2624942.5802 | 1240656.5736 | 2624947.1213 | 1240659.0942 | 2624949.6347 | 1240658.3265 | 2624951.1107 | 1240655.1581
29 | 2625017.8748 | 1240596.4742 | 2625003.7991 | 1240604.798 | 2624999.6262 | 1240606.4148 | 2624995.542 | 1240606.7201 | 2624992.0156 | 1240605.4069
30 | 2625017.8748 | 1240596.4742 | 2625031.1041 | 1240613.1959 | 2625038.3137 | 1240621.1719
31 | 2625055.9573 | 1240639.9032 | 2625047.104 | 1240630.8966 | 2625038.3137 | 1240621.1719

## bus_geodata
| x | y | coords
0 | 2625069.5295 | 1240558.4087
1 | 2625076.7793 | 1240566.0731
2 | 2625100.7717 | 1240522.6943
3 | 2625033.5131 | 1240525.5675
4 | 2625011.6771 | 1240513.2513
5 | 2625052.0601 | 1240497.7187
6 | 2625079.5075 | 1240568.7829
7 | 2625514.4086 | 1241008.7918
8 | 2625508.9588 | 1241012.2885
9 | 2625518.5028 | 1241004.6023
10 | 2625064.6996 | 1240650.3052
11 | 2625530.1474 | 1241000.7276
12 | 2625566.3432 | 1241017.0882
13 | 2625569.3491 | 1241018.646
14 | 2625151.1229 | 1240556.483
15 | 2625121.5362 | 1240535.4588
16 | 2625073.8029 | 1240503.3066
17 | 2625063.2079 | 1240502.6251
18 | 2625099.532 | 1240486.6024
19 | 2624962.6891 | 1240545.5641
20 | 2624979.9877 | 1240559.3413
21 | 2624987.009 | 1240565.1537
22 | 2625001.829 | 1240577.631
23 | 2625111.7034 | 1240475.4044
24 | 2625115.481 | 1240472.5297
25 | 2625132.235 | 1240456.7589
26 | 2624951.1107 | 1240655.1581
27 | 2624992.0156 | 1240605.4069
28 | 2624932.4605 | 1240635.718
29 | 2625017.8748 | 1240596.4742
30 | 2625038.3137 | 1240621.1719
31 | 2625152.9468 | 1240435.0438
32 | 2625055.9573 | 1240639.9032
33 | 2625151.1229 | 1240556.483

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99647 | -0.024746 | 0.00046217 | 0.00011583
1 | 0.99632 | -0.025762 | 0.00038721 | 9.7043e-05
2 | 0.99715 | -0.019964 | 0.0022082 | 0.00055343
3 | 0.99592 | -0.028555 | 0.0011402 | 0.00028577
4 | 0.99587 | -0.028937 | 0.0014932 | 0.00037422
5 | 0.99605 | -0.027667 | 0.0018692 | 0.00046848
6 | 0.99627 | -0.026117 | 0.0091804 | 0.0023008
7 | 0.98665 | -0.093035 | 0.0033724 | 0.0008452
8 | 0.98647 | -0.094285 | 0.0021107 | 0.00052898
9 | 0.98683 | -0.091709 | 0 | 0
10 | 0.97257 | -0.19308 | 0 | 0
11 | 0.98723 | -0.088894 | 0 | 0
12 | 0.98851 | -0.079914 | 0.0020207 | 0.00050643
13 | 0.98851 | -0.079961 | 0.0013586 | 0.0003405
14 | 1 | 0 | -0.060574 | -0.015046
15 | 0.99825 | -0.012252 | 0.0021326 | 0.00053448
16 | 0.99621 | -0.026564 | 0 | 0
17 | 0.99613 | -0.027114 | 0.00058291 | 0.00014609
18 | 0.99558 | -0.030971 | 0.0015971 | 0.00040028
19 | 0.97063 | -0.20707 | 0.0010539 | 0.00026412
20 | 0.97066 | -0.20683 | 0.0021444 | 0.00053744
21 | 0.9707 | -0.20652 | 0.0012893 | 0.00032312
22 | 0.97083 | -0.20559 | 0.00070004 | 0.00017545
23 | 0.99528 | -0.033072 | 0 | 0
24 | 0.9952 | -0.033675 | 0 | 0
25 | 0.99478 | -0.036607 | 0.0069926 | 0.0017525
26 | 0.97023 | -0.20994 | 0.0010021 | 0.00025116
27 | 0.97074 | -0.20623 | 0.0020207 | 0.00050643
28 | 0.97005 | -0.21126 | 0.0035816 | 0.00089762
29 | 0.97102 | -0.20422 | 0.0019728 | 0.00049443
30 | 0.97167 | -0.19955 | 0.0012717 | 0.00031871
31 | 0.99454 | -0.038307 | 0.005616 | 0.0014075
32 | 0.97224 | -0.19545 | 0.0014826 | 0.00037158
33 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0095694 | 0.0023984 | -0.0095681 | -0.002398 | 1.3459e-06 | 3.8007e-07 | 0.01429 | 0.01429 | 0.01429 | 0.99647 | -0.024746 | 0.99632 | -0.025762 | 5.2926
1 | -0.010032 | -0.0025142 | 0.010038 | 0.0025161 | 6.6444e-06 | 1.937e-06 | 0.01498 | 0.01498 | 0.01498 | 0.99647 | -0.024746 | 0.99715 | -0.019964 | 5.5482
2 | 0.0091809 | 0.002301 | -0.0091804 | -0.0023008 | 4.5112e-07 | 1.2343e-07 | 0.013712 | 0.013712 | 0.013712 | 0.99632 | -0.025762 | 0.99627 | -0.026117 | 5.0784
3 | 0.01933 | 0.0048468 | -0.019312 | -0.0048405 | 1.7663e-05 | 6.35e-06 | 0.028846 | 0.028846 | 0.028846 | 0.99715 | -0.019964 | 0.99621 | -0.026564 | 10.6838
4 | -0.031576 | -0.0079164 | 0.03161 | 0.0079291 | 3.3771e-05 | 1.2671e-05 | 0.047121 | 0.047121 | 0.047121 | 0.99715 | -0.019964 | 0.99825 | -0.012252 | 17.4524
5 | 0.0014932 | 0.00037392 | -0.0014932 | -0.00037422 | 7.9057e-08 | -3.008e-07 | 0.0022309 | 0.002231 | 0.002231 | 0.99592 | -0.028555 | 0.99587 | -0.028937 | 0.82631
6 | -0.0026335 | -0.00065969 | 0.0026338 | 0.00065938 | 3.2321e-07 | -3.1114e-07 | 0.0039346 | 0.0039344 | 0.0039346 | 0.99592 | -0.028555 | 0.99605 | -0.027667 | 1.4572
7 | -0.004503 | -0.0011279 | 0.0045034 | 0.0011278 | 3.4391e-07 | -2.6268e-08 | 0.0067269 | 0.0067268 | 0.0067269 | 0.99605 | -0.027667 | 0.99613 | -0.027114 | 2.4914
8 | 0.018892 | 0.004759 | -0.018888 | -0.0047578 | 3.3018e-06 | 1.1868e-06 | 0.0285 | 0.0285 | 0.0285 | 0.98665 | -0.093035 | 0.98647 | -0.094285 | 10.5557
9 | -0.022264 | -0.0056042 | 0.022268 | 0.0056057 | 4.1234e-06 | 1.5111e-06 | 0.033586 | 0.033586 | 0.033586 | 0.98665 | -0.093035 | 0.98683 | -0.091709 | 12.4394
10 | 0.016778 | 0.0042288 | -0.016549 | -0.0041479 | 0.00022921 | 8.0945e-05 | 0.025317 | 0.025319 | 0.025319 | 0.98647 | -0.094285 | 0.97257 | -0.19308 | 9.3775
11 | -0.022268 | -0.0056057 | 0.022277 | 0.0056089 | 8.7579e-06 | 3.2094e-06 | 0.033586 | 0.033586 | 0.033586 | 0.98683 | -0.091709 | 0.98723 | -0.088894 | 12.4394
12 | 0.016549 | 0.0041479 | -0.016543 | -0.0041459 | 5.4439e-06 | 1.925e-06 | 0.025319 | 0.025319 | 0.025319 | 0.97257 | -0.19308 | 0.97224 | -0.19545 | 9.3775
13 | -0.022277 | -0.0056089 | 0.022305 | 0.0056191 | 2.7982e-05 | 1.0254e-05 | 0.033586 | 0.033586 | 0.033586 | 0.98723 | -0.088894 | 0.98851 | -0.079914 | 12.4394
14 | -0.025684 | -0.006466 | 0.025974 | 0.0065612 | 0.00028933 | 9.5195e-05 | 0.038673 | 0.038667 | 0.038673 | 0.98851 | -0.079914 | 1 | 0 | 7.1617
15 | 0.0013586 | 0.00034046 | -0.0013586 | -0.0003405 | 8.8364e-09 | -4.0004e-08 | 0.0020451 | 0.0020451 | 0.0020451 | 0.98851 | -0.079914 | 0.98851 | -0.079961 | 0.75746
16 | 0.0338 | 0.0084852 | -0.033743 | -0.0084635 | 5.742e-05 | 2.1608e-05 | 0.0503 | 0.0503 | 0.0503 | 1 | 0 | 0.99825 | -0.012252 | 18.6297
17 | 0.0050867 | 0.0012739 | -0.0050863 | -0.0012739 | 3.8725e-07 | 8.9723e-09 | 0.0075975 | 0.0075976 | 0.0075976 | 0.99621 | -0.026564 | 0.99613 | -0.027114 | 2.8139
18 | 0.014226 | 0.0035665 | -0.014217 | -0.0035636 | 8.6813e-06 | 2.938e-06 | 0.021249 | 0.021249 | 0.021249 | 0.99621 | -0.026564 | 0.99558 | -0.030971 | 7.87
19 | 0.01262 | 0.0031633 | -0.012616 | -0.0031621 | 3.6717e-06 | 1.1972e-06 | 0.018862 | 0.018862 | 0.018862 | 0.99558 | -0.030971 | 0.99528 | -0.033072 | 6.9859
20 | -0.0010539 | -0.00026412 | 0.0010539 | 0.00026386 | 3.6018e-08 | -2.5949e-07 | 0.0016156 | 0.0016155 | 0.0016156 | 0.97063 | -0.20707 | 0.97066 | -0.20683 | 0.59838
21 | -0.0031983 | -0.00080131 | 0.0031985 | 0.00080125 | 1.3672e-07 | -6.0087e-08 | 0.0049029 | 0.0049029 | 0.0049029 | 0.97066 | -0.20683 | 0.9707 | -0.20652 | 1.8159
22 | -0.0044877 | -0.0011244 | 0.0044883 | 0.0011244 | 5.7246e-07 | -1.9501e-08 | 0.0068792 | 0.0068792 | 0.0068792 | 0.9707 | -0.20652 | 0.97083 | -0.20559 | 2.5479
23 | -0.0051884 | -0.0012998 | 0.0051893 | 0.0012999 | 9.8321e-07 | 6.999e-08 | 0.0079521 | 0.007952 | 0.0079521 | 0.97083 | -0.20559 | 0.97102 | -0.20422 | 2.9452
24 | 0.012616 | 0.0031621 | -0.012615 | -0.0031618 | 1.0518e-06 | 3.4299e-07 | 0.018862 | 0.018862 | 0.018862 | 0.99528 | -0.033072 | 0.9952 | -0.033675 | 6.9859
25 | 0.012615 | 0.0031618 | -0.01261 | -0.0031601 | 5.1197e-06 | 1.6696e-06 | 0.018862 | 0.018862 | 0.018862 | 0.9952 | -0.033675 | 0.99478 | -0.036607 | 6.986
26 | 0.0056173 | 0.0014076 | -0.005616 | -0.0014075 | 1.3221e-06 | 1.1899e-07 | 0.0084024 | 0.0084026 | 0.0084026 | 0.99478 | -0.036607 | 0.99454 | -0.038307 | 3.1121
27 | -0.0045843 | -0.0011486 | 0.0045867 | 0.0011486 | 2.3478e-06 | -3.7557e-08 | 0.0070307 | 0.0070304 | 0.0070307 | 0.97023 | -0.20994 | 0.97074 | -0.20623 | 2.604
28 | 0.0035822 | 0.00089745 | -0.0035816 | -0.00089762 | 6.5603e-07 | -1.7777e-07 | 0.0054938 | 0.005494 | 0.005494 | 0.97023 | -0.20994 | 0.97005 | -0.21126 | 2.0348
29 | -0.0066074 | -0.001655 | 0.0066092 | 0.0016553 | 1.8361e-06 | 3.5143e-07 | 0.010128 | 0.010128 | 0.010128 | 0.97074 | -0.20623 | 0.97102 | -0.20422 | 3.7511
30 | -0.013771 | -0.0034496 | 0.01378 | 0.0034527 | 8.9128e-06 | 3.031e-06 | 0.021103 | 0.021103 | 0.021103 | 0.97102 | -0.20422 | 0.97167 | -0.19955 | 7.8159
31 | -0.015052 | -0.0037714 | 0.01506 | 0.0037744 | 8.5331e-06 | 2.963e-06 | 0.02305 | 0.02305 | 0.02305 | 0.97167 | -0.19955 | 0.97224 | -0.19545 | 8.5371

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.062817 | 0.015609

## res_load
| p_mw | q_mvar
0 | 0.00046217 | 0.00011583
1 | 0.00038721 | 9.7043e-05
2 | 0.0022082 | 0.00055343
3 | 0.0011402 | 0.00028577
4 | 0.0014932 | 0.00037422
5 | 0.0018692 | 0.00046848
6 | 0.0091804 | 0.0023008
7 | 0.0033724 | 0.0008452
8 | 0.0021107 | 0.00052898
9 | 0.0020207 | 0.00050643
10 | 0.0013586 | 0.0003405
11 | 0.0022434 | 0.00056226
12 | 0.0021326 | 0.00053448
13 | 0.00058291 | 0.00014609
14 | 0.0015971 | 0.00040028
15 | 0.0010539 | 0.00026412
16 | 0.0021444 | 0.00053744
17 | 0.0012893 | 0.00032312
18 | 0.00070004 | 0.00017545
19 | 0.0069926 | 0.0017525
20 | 0.0010021 | 0.00025116
21 | 0.0020207 | 0.00050643
22 | 0.0035816 | 0.00089762
23 | 0.0019728 | 0.00049443
24 | 0.0012717 | 0.00031871
25 | 0.005616 | 0.0014075
26 | 0.0014826 | 0.00037158

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1