## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2406-2_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2406-2_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2406-2_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2406-2_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2406-2_0_5_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_2406-2_0_5_node_92 | 0.4 | n |  | TRUE
6 | bus_LV_2406-2_0_5_node_24 | 0.4 | n |  | TRUE
7 | bus_LV_2406-2_0_5_node_18 | 0.4 | n |  | TRUE
8 | bus_LV_2406-2_0_5_node_19 | 0.4 | n |  | TRUE
9 | bus_LV_2406-2_0_5_node_20 | 0.4 | n |  | TRUE
10 | bus_LV_2406-2_0_5_node_23 | 0.4 | n |  | TRUE
11 | bus_LV_2406-2_0_5_node_25 | 0.4 | n |  | TRUE
12 | bus_LV_2406-2_0_5_node_4 | 0.4 | n |  | TRUE
13 | bus_LV_2406-2_0_5_node_44 | 0.4 | n |  | TRUE
14 | bus_LV_2406-2_0_5_node_103 | 0.4 | n |  | TRUE
15 | bus_LV_2406-2_0_5_node_112 | 0.4 | n |  | TRUE
16 | bus_LV_2406-2_0_5_node_42 | 0.4 | n |  | TRUE
17 | bus_LV_2406-2_0_5_node_102 | 0.4 | n |  | TRUE
18 | bus_LV_2406-2_0_5_node_27 | 0.4 | n |  | TRUE
19 | bus_LV_2406-2_0_5_node_70 | 0.4 | n |  | TRUE
20 | bus_LV_2406-2_0_5_node_63 | 0.4 | n |  | TRUE
21 | bus_LV_2406-2_0_5_node_64 | 0.4 | n |  | TRUE
22 | bus_LV_2406-2_0_5_node_62 | 0.4 | n |  | TRUE
23 | bus_LV_2406-2_0_5_node_93 | 0.4 | n |  | TRUE
24 | bus_LV_2406-2_0_5_node_94 | 0.4 | n |  | TRUE
25 | bus_LV_2406-2_0_5_node_26 | 0.4 | n |  | TRUE
26 | bus_LV_2406-2_0_5_node_59 | 0.4 | n |  | TRUE
27 | bus_LV_2406-2_0_5_node_61 | 0.4 | n |  | TRUE
28 | bus_LV_2406-2_0_5_node_57 | 0.4 | n |  | TRUE
29 | bus_LV_2406-2_0_5_node_6 | 0.4 | n |  | TRUE
30 | bus_LV_2406-2_0_5_node_7 | 0.4 | n |  | TRUE
31 | bus_LV_2406-2_0_5_node_8 | 0.4 | n |  | TRUE
32 | bus_LV_2406-2_0_5_node_9 | 0.4 | n |  | TRUE
33 | bus_LV_2406-2_0_5_node_10 | 0.4 | n |  | TRUE
34 | bus_LV_2406-2_0_5_node_11 | 0.4 | n |  | TRUE
35 | bus_LV_2406-2_0_5_node_72 | 0.4 | n |  | TRUE
36 | bus_LV_2406-2_0_5_node_53 | 0.4 | n |  | TRUE
37 | bus_LV_2406-2_0_5_node_110 | 0.4 | n |  | TRUE
38 | bus_LV_2406-2_0_5_node_73 | 0.4 | n |  | TRUE
39 | bus_LV_2406-2_0_5_node_54 | 0.4 | n |  | TRUE
40 | bus_LV_2406-2_0_5_node_91 | 0.4 | n |  | TRUE
41 | bus_LV_2406-2_0_5_node_12 | 0.4 | n |  | TRUE
42 | bus_LV_2406-2_0_5_node_13 | 0.4 | n |  | TRUE
43 | bus_LV_2406-2_0_5_node_14 | 0.4 | n |  | TRUE
44 | bus_LV_2406-2_0_5_node_15 | 0.4 | n |  | TRUE
45 | bus_LV_2406-2_0_5_node_16 | 0.4 | n |  | TRUE
46 | bus_LV_2406-2_0_5_node_17 | 0.4 | n |  | TRUE
47 | bus_LV_2406-2_0_5_node_80 | 0.4 | n |  | TRUE
48 | bus_LV_2406-2_0_5_node_78 | 0.4 | n |  | TRUE
49 | bus_LV_2406-2_0_5_node_83 | 0.4 | n |  | TRUE
50 | bus_LV_2406-2_0_5_node_113 | 0.4 | n |  | TRUE
51 | bus_LV_2406-2_0_5_node_98 | 0.4 | n |  | TRUE
52 | bus_LV_2406-2_0_5_node_114 | 0.4 | n |  | TRUE
53 | bus_LV_2406-2_0_5_node_97 | 0.4 | n |  | TRUE
54 | bus_LV_2406-2_0_5_node_21 | 0.4 | n |  | TRUE
55 | bus_LV_2406-2_0_5_node_22 | 0.4 | n |  | TRUE
56 | bus_LV_2406-2_0_5_node_67 | 0.4 | n |  | TRUE
57 | bus_LV_2406-2_0_5_node_52 | 0.4 | n |  | TRUE
58 | bus_LV_2406-2_0_5_node_82 | 0.4 | n |  | TRUE
59 | bus_LV_2406-2_0_5_node_50 | 0.4 | n |  | TRUE
60 | bus_LV_2406-2_0_5_node_68 | 0.4 | n |  | TRUE
61 | bus_LV_2406-2_0_5_node_28 | 0.4 | n |  | TRUE
62 | bus_LV_2406-2_0_5_node_29 | 0.4 | n |  | TRUE
63 | bus_LV_2406-2_0_5_node_30 | 0.4 | n |  | TRUE
64 | bus_LV_2406-2_0_5_node_31 | 0.4 | n |  | TRUE
65 | bus_LV_2406-2_0_5_node_32 | 0.4 | n |  | TRUE
66 | bus_LV_2406-2_0_5_node_33 | 0.4 | n |  | TRUE
67 | bus_LV_2406-2_0_5_node_86 | 0.4 | n |  | TRUE
68 | bus_LV_2406-2_0_5_node_34 | 0.4 | n |  | TRUE
69 | bus_LV_2406-2_0_5_node_35 | 0.4 | n |  | TRUE
70 | bus_LV_2406-2_0_5_node_87 | 0.4 | n |  | TRUE
71 | bus_LV_2406-2_0_5_node_85 | 0.4 | n |  | TRUE
72 | bus_LV_2406-2_0_5_node_66 | 0.4 | n |  | TRUE
73 | bus_LV_2406-2_0_5_node_77 | 0.4 | n |  | TRUE
74 | bus_LV_2406-2_0_5_node_90 | 0.4 | n |  | TRUE
75 | bus_LV_2406-2_0_5_node_89 | 0.4 | n |  | TRUE
76 | bus_LV_2406-2_0_5_node_65 | 0.4 | n |  | TRUE
77 | bus_LV_2406-2_0_5_node_48 | 0.4 | n |  | TRUE
78 | bus_LV_2406-2_0_5_node_76 | 0.4 | n |  | TRUE
79 | bus_LV_2406-2_0_5_node_117 | 0.4 | n |  | TRUE
80 | bus_LV_2406-2_0_5_node_36 | 0.4 | n |  | TRUE
81 | bus_LV_2406-2_0_5_node_37 | 0.4 | n |  | TRUE
82 | bus_LV_2406-2_0_5_node_38 | 0.4 | n |  | TRUE
83 | bus_LV_2406-2_0_5_node_39 | 0.4 | n |  | TRUE
84 | bus_LV_2406-2_0_5_node_40 | 0.4 | n |  | TRUE
85 | bus_LV_2406-2_0_5_node_56 | 0.4 | n |  | TRUE
86 | bus_LV_2406-2_0_5_node_45 | 0.4 | n |  | TRUE
87 | bus_LV_2406-2_0_5_node_41 | 0.4 | n |  | TRUE
88 | bus_LV_2406-2_0_5_node_43 | 0.4 | n |  | TRUE
89 | bus_LV_2406-2_0_5_node_111 | 0.4 | n |  | TRUE
90 | bus_LV_2406-2_0_5_node_71 | 0.4 | n |  | TRUE
91 | bus_LV_2406-2_0_5_node_101 | 0.4 | n |  | TRUE
92 | bus_LV_2406-2_0_5_node_69 | 0.4 | n |  | TRUE
93 | bus_LV_2406-2_0_5_node_100 | 0.4 | n |  | TRUE
94 | bus_LV_2406-2_0_5_node_99 | 0.4 | n |  | TRUE
95 | bus_LV_2406-2_0_5_node_46 | 0.4 | n |  | TRUE
96 | bus_LV_2406-2_0_5_node_47 | 0.4 | n |  | TRUE
97 | bus_LV_2406-2_0_5_node_84 | 0.4 | n |  | TRUE
98 | bus_LV_2406-2_0_5_node_49 | 0.4 | n |  | TRUE
99 | bus_LV_2406-2_0_5_node_51 | 0.4 | n |  | TRUE
100 | bus_LV_2406-2_0_5_node_58 | 0.4 | n |  | TRUE
101 | bus_LV_2406-2_0_5_node_60 | 0.4 | n |  | TRUE
102 | bus_LV_2406-2_0_5_node_55 | 0.4 | n |  | TRUE
103 | bus_LV_2406-2_0_5_node_88 | 0.4 | n |  | TRUE
104 | bus_LV_2406-2_0_5_node_75 | 0.4 | n |  | TRUE
105 | bus_LV_2406-2_0_5_node_104 | 0.4 | n |  | TRUE
106 | bus_LV_2406-2_0_5_node_74 | 0.4 | n |  | TRUE
107 | bus_LV_2406-2_0_5_node_79 | 0.4 | n |  | TRUE
108 | bus_LV_2406-2_0_5_node_81 | 0.4 | n |  | TRUE
109 | bus_LV_2406-2_0_5_node_107 | 0.4 | n |  | TRUE
110 | bus_LV_2406-2_0_5_node_106 | 0.4 | n |  | TRUE
111 | bus_LV_2406-2_0_5_node_108 | 0.4 | n |  | TRUE
112 | bus_LV_2406-2_0_5_node_115 | 0.4 | n |  | TRUE
113 | bus_LV_2406-2_0_5_node_116 | 0.4 | n |  | TRUE
114 | bus_LV_2406-2_0_5_node_95 | 0.4 | n |  | TRUE
115 | bus_LV_2406-2_0_5_node_96 | 0.4 | n |  | TRUE
116 | bus_LV_2406-2_0_5_node_105 | 0.4 | n |  | TRUE
117 | bus_MV_334_0_node_278 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2406-2_0_5_load_0 | 0 | 0.0016951 | 0.00042484 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2406-2_0_5_load_1 | 1 | 0.0011448 | 0.00028691 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2406-2_0_5_load_3 | 3 | 0.0017065 | 0.00042768 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2406-2_0_5_load_5 | 4 | 0.0015266 | 0.0003826 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2406-2_0_5_load_92 | 5 | 0.0060365 | 0.0015129 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2406-2_0_5_load_24 | 6 | 0.0022604 | 0.00056651 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2406-2_0_5_load_18 | 7 | 0.0013522 | 0.00033888 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2406-2_0_5_load_19 | 8 | 0.0018898 | 0.00047363 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2406-2_0_5_load_20 | 9 | 0.0038111 | 0.00095515 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2406-2_0_5_load_23 | 10 | 0.0025328 | 0.00063477 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2406-2_0_5_load_25 | 11 | 0.0026781 | 0.0006712 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2406-2_0_5_load_44 | 13 | 0.0024235 | 0.00060739 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2406-2_0_5_load_103 | 14 | 0.0024093 | 0.00060383 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2406-2_0_5_load_112 | 15 | 0.0020606 | 0.00051643 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2406-2_0_5_load_42 | 16 | 0.0021529 | 0.00053956 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2406-2_0_5_load_102 | 17 | 0.0012891 | 0.00032308 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2406-2_0_5_load_27 | 18 | 0.0020544 | 0.00051488 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2406-2_0_5_load_70 | 19 | 0.0010828 | 0.00027138 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2406-2_0_5_load_63 | 20 | 0.00079964 | 0.00020041 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2406-2_0_5_load_64 | 21 | 0.0012231 | 0.00030655 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2406-2_0_5_load_62 | 22 | 0.0016458 | 0.00041249 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2406-2_0_5_load_93 | 23 | 0.0021968 | 0.00055057 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2406-2_0_5_load_94 | 24 | 0.0012175 | 0.00030514 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2406-2_0_5_load_26 | 25 | 0.0043694 | 0.0010951 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2406-2_0_5_load_59 | 26 | 0.0063751 | 0.0015978 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2406-2_0_5_load_57 | 28 | 0.0030868 | 0.00077362 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2406-2_0_5_load_6 | 29 | 0.0030949 | 0.00077566 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2406-2_0_5_load_7 | 30 | 0.0017749 | 0.00044483 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2406-2_0_5_load_9 | 32 | 0.0030011 | 0.00075215 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2406-2_0_5_load_10 | 33 | 0.0026889 | 0.0006739 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2406-2_0_5_load_11 | 34 | 0.0021147 | 0.00052999 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2406-2_0_5_load_72 | 35 | 0.0037407 | 0.00093751 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2406-2_0_5_load_53 | 36 | 0.0022173 | 0.0005557 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2406-2_0_5_load_110 | 37 | 0.0031012 | 0.00077722 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2406-2_0_5_load_73 | 38 | 0.0026763 | 0.00067074 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2406-2_0_5_load_91 | 40 | 0.0030171 | 0.00075616 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2406-2_0_5_load_12 | 41 | 0.0041704 | 0.0010452 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2406-2_0_5_load_17 | 46 | 0.012936 | 0.0032421 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2406-2_0_5_load_80 | 47 | 0.0023735 | 0.00059487 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2406-2_0_5_load_78 | 48 | 0.0038193 | 0.00095722 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2406-2_0_5_load_83 | 49 | 0.003086 | 0.00077342 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2406-2_0_5_load_113 | 50 | 0.0021583 | 0.00054093 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2406-2_0_5_load_98 | 51 | 0.0023714 | 0.00059433 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2406-2_0_5_load_114 | 52 | 0.00098831 | 0.00024769 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2406-2_0_5_load_97 | 53 | 0.002876 | 0.00072078 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2406-2_0_5_load_21 | 54 | 0.0036354 | 0.00091113 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2406-2_0_5_load_22 | 55 | 0.0015815 | 0.00039637 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2406-2_0_5_load_67 | 56 | 0.0019066 | 0.00047785 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2406-2_0_5_load_82 | 58 | 0.0012944 | 0.00032441 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2406-2_0_5_load_50 | 59 | 0.002579 | 0.00064637 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2406-2_0_5_load_68 | 60 | 0.0020121 | 0.00050428 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2406-2_0_5_load_28 | 61 | 0.0013727 | 0.00034404 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2406-2_0_5_load_29 | 62 | 0.0013934 | 0.00034922 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2406-2_0_5_load_30 | 63 | 0.0016075 | 0.00040287 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2406-2_0_5_load_31 | 64 | 0.0014086 | 0.00035303 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2406-2_0_5_load_32 | 65 | 0.0017643 | 0.00044217 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2406-2_0_5_load_34 | 68 | 0.00093679 | 0.00023478 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2406-2_0_5_load_87 | 70 | 0.0014665 | 0.00036754 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2406-2_0_5_load_85 | 71 | 0.00094882 | 0.0002378 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2406-2_0_5_load_66 | 72 | 0.0013391 | 0.00033562 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2406-2_0_5_load_89 | 75 | 0.0025115 | 0.00062943 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2406-2_0_5_load_65 | 76 | 0.0012063 | 0.00030232 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2406-2_0_5_load_48 | 77 | 0.0018262 | 0.0004577 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2406-2_0_5_load_76 | 78 | 0.0017108 | 0.00042878 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2406-2_0_5_load_117 | 79 | 0.0026556 | 0.00066555 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2406-2_0_5_load_36 | 80 | 0.0018932 | 0.00047449 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2406-2_0_5_load_37 | 81 | 0.0020862 | 0.00052284 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2406-2_0_5_load_38 | 82 | 0.0018252 | 0.00045744 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2406-2_0_5_load_39 | 83 | 0.0015216 | 0.00038136 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2406-2_0_5_load_40 | 84 | 0.0020418 | 0.00051173 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2406-2_0_5_load_56 | 85 | 0.00095932 | 0.00024043 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2406-2_0_5_load_45 | 86 | 0.0013049 | 0.00032703 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2406-2_0_5_load_41 | 87 | 0.0019806 | 0.00049639 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2406-2_0_5_load_43 | 88 | 0.001063 | 0.00026641 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2406-2_0_5_load_111 | 89 | 0.0018528 | 0.00046435 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2406-2_0_5_load_71 | 90 | 0.0022749 | 0.00057016 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2406-2_0_5_load_101 | 91 | 0.0021313 | 0.00053416 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2406-2_0_5_load_69 | 92 | 0.0020021 | 0.00050178 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2406-2_0_5_load_100 | 93 | 0.0019351 | 0.00048499 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2406-2_0_5_load_99 | 94 | 0.0021236 | 0.00053222 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2406-2_0_5_load_47 | 96 | 0.00099497 | 0.00024936 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2406-2_0_5_load_84 | 97 | 0.001202 | 0.00030126 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2406-2_0_5_load_49 | 98 | 0.00451 | 0.0011303 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2406-2_0_5_load_51 | 99 | 0.0016095 | 0.00040337 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2406-2_0_5_load_58 | 100 | 0.0021081 | 0.00052833 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2406-2_0_5_load_60 | 101 | 0.0014118 | 0.00035384 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2406-2_0_5_load_88 | 103 | 0.0027025 | 0.00067732 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2406-2_0_5_load_75 | 104 | 0.0015854 | 0.00039734 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2406-2_0_5_load_104 | 105 | 0.0012065 | 0.00030237 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2406-2_0_5_load_74 | 106 | 0.0022697 | 0.00056884 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2406-2_0_5_load_79 | 107 | 0.0023157 | 0.00058037 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2406-2_0_5_load_81 | 108 | 0.0023485 | 0.00058858 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2406-2_0_5_load_107 | 109 | 0.0014932 | 0.00037424 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2406-2_0_5_load_106 | 110 | 0.0022757 | 0.00057035 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2406-2_0_5_load_108 | 111 | 0.0013516 | 0.00033875 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2406-2_0_5_load_115 | 112 | 0.0026416 | 0.00066206 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2406-2_0_5_load_116 | 113 | 0.0056303 | 0.0014111 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2406-2_0_5_load_95 | 114 | 0.0012038 | 0.0003017 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2406-2_0_5_load_96 | 115 | 0.0010542 | 0.0002642 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2406-2_0_5_load_105 | 116 | 0.0012865 | 0.00032242 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 27 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2406-2_0_5_line_0 | NAYY 4x150 SE | 0 | 1 | 0.006949 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2406-2_0_5_line_1 | NAYY 4x150 SE | 0 | 2 | 0.018537 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2406-2_0_5_line_2 | NAYY 4x150 SE | 1 | 3 | 0.024293 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2406-2_0_5_line_3 | NAYY 4x150 SE | 2 | 4 | 0.041512 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2406-2_0_5_line_4 | NAYY 4x150 SE | 3 | 10 | 0.020045 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2406-2_0_5_line_5 | NAYY 4x150 SE | 4 | 15 | 0.022123 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2406-2_0_5_line_6 | NAYY 4x150 SE | 5 | 6 | 0.010517 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2406-2_0_5_line_7 | NAYY 4x150 SE | 6 | 25 | 0.019431 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2406-2_0_5_line_8 | NAYY 4x150 SE | 6 | 10 | 0.017235 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2406-2_0_5_line_9 | NAYY 4x150 SE | 7 | 8 | 0.026309 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
10 | LV_2406-2_0_5_line_10 | NAYY 4x150 SE | 7 | 9 | 0.0069623 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
11 | LV_2406-2_0_5_line_11 | NAYY 4x150 SE | 8 | 54 | 0.0019722 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
12 | LV_2406-2_0_5_line_12 | NAYY 4x150 SE | 9 | 55 | 0.026867 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
13 | LV_2406-2_0_5_line_13 | NAYY 4x150 SE | 10 | 11 | 0.024049 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2406-2_0_5_line_14 | NAYY 4x150 SE | 11 | 18 | 0.019155 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2406-2_0_5_line_15 | NAYY 4x150 SE | 12 | 13 | 0.035365 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2406-2_0_5_line_16 | NAYY 4x150 SE | 12 | 14 | 0.029137 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2406-2_0_5_line_17 | NAYY 4x150 SE | 13 | 16 | 0.0097077 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2406-2_0_5_line_18 | NAYY 4x150 SE | 14 | 17 | 0.00015208 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2406-2_0_5_line_19 | NAYY 4x150 SE | 16 | 87 | 0.021667 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2406-2_0_5_line_20 | NAYY 4x150 SE | 17 | 19 | 0.044545 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2406-2_0_5_line_21 | NAYY 4x150 SE | 18 | 19 | 0.011851 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2406-2_0_5_line_22 | NAYY 4x150 SE | 19 | 60 | 0.013692 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2406-2_0_5_line_23 | NAYY 4x150 SE | 20 | 21 | 0.014985 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
24 | LV_2406-2_0_5_line_24 | NAYY 4x150 SE | 20 | 22 | 0.012062 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
25 | LV_2406-2_0_5_line_25 | NAYY 4x150 SE | 21 | 76 | 0.022263 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
26 | LV_2406-2_0_5_line_26 | NAYY 4x150 SE | 22 | 55 | 0.00049441 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
27 | LV_2406-2_0_5_line_27 | NAYY 4x150 SE | 23 | 24 | 0.018279 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2406-2_0_5_line_28 | NAYY 4x150 SE | 23 | 25 | 0.017972 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2406-2_0_5_line_29 | NAYY 4x150 SE | 24 | 57 | 0.0088776 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2406-2_0_5_line_30 | NAYY 4x150 SE | 26 | 27 | 0.019819 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
31 | LV_2406-2_0_5_line_31 | NAYY 4x150 SE | 26 | 28 | 0.010245 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
32 | LV_2406-2_0_5_line_32 | NAYY 4x150 SE | 27 | 56 | 0.025357 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2406-2_0_5_line_33 | NAYY 4x150 SE | 27 | 54 | 0.016357 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
34 | LV_2406-2_0_5_line_34 | NAYY 4x150 SE | 28 | 100 | 0.021782 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
35 | LV_2406-2_0_5_line_35 | NAYY 4x150 SE | 29 | 30 | 0.0062768 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2406-2_0_5_line_36 | NAYY 4x150 SE | 29 | 31 | 0.010121 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2406-2_0_5_line_37 | NAYY 4x150 SE | 30 | 32 | 0.018971 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2406-2_0_5_line_38 | NAYY 4x150 SE | 31 | 33 | 0.022063 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_2406-2_0_5_line_39 | NAYY 4x150 SE | 31 | 34 | 0.025248 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_2406-2_0_5_line_40 | NAYY 4x150 SE | 32 | 35 | 0.024302 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_2406-2_0_5_line_41 | NAYY 4x150 SE | 33 | 36 | 0.031535 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_2406-2_0_5_line_42 | NAYY 4x150 SE | 34 | 37 | 0.017096 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_2406-2_0_5_line_43 | NAYY 4x150 SE | 35 | 38 | 0.0013331 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_2406-2_0_5_line_44 | NAYY 4x150 SE | 36 | 39 | 0.026309 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
45 | LV_2406-2_0_5_line_45 | NAYY 4x150 SE | 37 | 40 | 0.02647 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_2406-2_0_5_line_46 | NAYY 4x150 SE | 39 | 102 | 0.039253 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
47 | LV_2406-2_0_5_line_47 | NAYY 4x150 SE | 39 | 85 | 0.028401 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_2406-2_0_5_line_48 | NAYY 4x150 SE | 40 | 108 | 0.019069 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_2406-2_0_5_line_49 | NAYY 4x150 SE | 41 | 42 | 0.020751 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_2406-2_0_5_line_50 | NAYY 4x150 SE | 41 | 43 | 0.011188 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_2406-2_0_5_line_51 | NAYY 4x150 SE | 42 | 44 | 0.0184 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_2406-2_0_5_line_52 | NAYY 4x150 SE | 42 | 45 | 0.012564 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_2406-2_0_5_line_53 | NAYY 4x150 SE | 43 | 46 | 0.043316 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_2406-2_0_5_line_54 | NAYY 4x150 SE | 44 | 49 | 0.04447 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_2406-2_0_5_line_55 | NAYY 4x150 SE | 45 | 50 | 0.027994 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_2406-2_0_5_line_56 | NAYY 4x150 SE | 46 | 51 | 0.00588 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_2406-2_0_5_line_57 | NAYY 4x150 SE | 47 | 48 | 0.014963 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_2406-2_0_5_line_58 | NAYY 4x150 SE | 48 | 107 | 0.012796 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_2406-2_0_5_line_59 | NAYY 4x150 SE | 50 | 52 | 0.025807 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_2406-2_0_5_line_60 | NAYY 4x150 SE | 51 | 53 | 0.05796 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_2406-2_0_5_line_61 | NAYY 4x150 SE | 52 | 112 | 0.026609 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_2406-2_0_5_line_62 | NAYY 4x150 SE | 53 | 109 | 0.018345 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_2406-2_0_5_line_63 | NAYY 4x150 SE | 53 | 58 | 0.0027739 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_2406-2_0_5_line_64 | NAYY 4x150 SE | 57 | 58 | 0.038401 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_2406-2_0_5_line_65 | NAYY 4x150 SE | 57 | 59 | 0.015797 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_2406-2_0_5_line_66 | NAYY 4x150 SE | 59 | 98 | 0.014463 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
67 | LV_2406-2_0_5_line_67 | NAYY 4x150 SE | 60 | 92 | 0.001491 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_2406-2_0_5_line_68 | NAYY 4x150 SE | 61 | 62 | 0.028677 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_2406-2_0_5_line_69 | NAYY 4x150 SE | 61 | 63 | 0.0038993 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_2406-2_0_5_line_70 | NAYY 4x150 SE | 62 | 64 | 0.014341 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_2406-2_0_5_line_71 | NAYY 4x150 SE | 63 | 65 | 0.034516 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_2406-2_0_5_line_72 | NAYY 4x150 SE | 64 | 66 | 0.015323 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_2406-2_0_5_line_73 | NAYY 4x150 SE | 65 | 67 | 0.013474 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_2406-2_0_5_line_74 | NAYY 4x150 SE | 66 | 68 | 0.028336 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
75 | LV_2406-2_0_5_line_75 | NAYY 4x150 SE | 66 | 69 | 0.036399 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
76 | LV_2406-2_0_5_line_76 | NAYY 4x150 SE | 67 | 70 | 0.016103 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_2406-2_0_5_line_77 | NAYY 4x150 SE | 67 | 71 | 0.016192 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_2406-2_0_5_line_78 | NAYY 4x150 SE | 68 | 72 | 0.023644 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
79 | LV_2406-2_0_5_line_79 | NAYY 4x150 SE | 69 | 73 | 0.022115 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
80 | LV_2406-2_0_5_line_80 | NAYY 4x150 SE | 69 | 74 | 0.065623 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_2406-2_0_5_line_81 | NAYY 4x150 SE | 69 | 75 | 0.026747 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_2406-2_0_5_line_82 | NAYY 4x150 SE | 70 | 114 | 0.012128 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_2406-2_0_5_line_83 | NAYY 4x150 SE | 72 | 76 | 0.037794 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
84 | LV_2406-2_0_5_line_84 | NAYY 4x150 SE | 73 | 77 | 0.067972 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_2406-2_0_5_line_85 | NAYY 4x150 SE | 73 | 78 | 0.063793 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
86 | LV_2406-2_0_5_line_86 | NAYY 4x150 SE | 74 | 79 | 0.049399 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_2406-2_0_5_line_87 | NAYY 4x150 SE | 77 | 95 | 0.018407 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_2406-2_0_5_line_88 | NAYY 4x150 SE | 78 | 106 | 0.030428 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
89 | LV_2406-2_0_5_line_89 | NAYY 4x150 SE | 80 | 81 | 0.016419 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_2406-2_0_5_line_90 | NAYY 4x150 SE | 80 | 82 | 0.011199 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_2406-2_0_5_line_91 | NAYY 4x150 SE | 81 | 83 | 0.0034482 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_2406-2_0_5_line_92 | NAYY 4x150 SE | 82 | 84 | 0.035582 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_2406-2_0_5_line_93 | NAYY 4x150 SE | 83 | 85 | 0.019961 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_2406-2_0_5_line_94 | NAYY 4x150 SE | 85 | 86 | 0.040509 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_2406-2_0_5_line_95 | NAYY 4x150 SE | 87 | 88 | 0.036634 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_2406-2_0_5_line_96 | NAYY 4x150 SE | 89 | 90 | 0.013119 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_2406-2_0_5_line_97 | NAYY 4x150 SE | 89 | 91 | 0.013363 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_2406-2_0_5_line_98 | NAYY 4x150 SE | 90 | 92 | 0.020576 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_2406-2_0_5_line_99 | NAYY 4x150 SE | 91 | 93 | 0.024681 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_2406-2_0_5_line_100 | NAYY 4x150 SE | 93 | 94 | 0.0067415 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_2406-2_0_5_line_101 | NAYY 4x150 SE | 95 | 96 | 0.032883 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_2406-2_0_5_line_102 | NAYY 4x150 SE | 96 | 97 | 0.022504 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_2406-2_0_5_line_103 | NAYY 4x150 SE | 98 | 99 | 0.022004 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
104 | LV_2406-2_0_5_line_104 | NAYY 4x150 SE | 99 | 100 | 0.039079 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
105 | LV_2406-2_0_5_line_105 | NAYY 4x150 SE | 100 | 101 | 0.00090162 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_2406-2_0_5_line_106 | NAYY 4x150 SE | 102 | 103 | 0.021804 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_2406-2_0_5_line_107 | NAYY 4x150 SE | 102 | 104 | 0.01119 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
108 | LV_2406-2_0_5_line_108 | NAYY 4x150 SE | 103 | 105 | 0.0074181 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_2406-2_0_5_line_109 | NAYY 4x150 SE | 104 | 106 | 0.01953 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
110 | LV_2406-2_0_5_line_110 | NAYY 4x150 SE | 105 | 116 | 0.0083339 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_2406-2_0_5_line_111 | NAYY 4x150 SE | 107 | 108 | 0.0048621 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_2406-2_0_5_line_112 | NAYY 4x150 SE | 109 | 110 | 0.021978 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_2406-2_0_5_line_113 | NAYY 4x150 SE | 110 | 111 | 0.0025363 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_2406-2_0_5_line_114 | NAYY 4x150 SE | 112 | 113 | 0.027057 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_2406-2_0_5_line_115 | NAYY 4x150 SE | 114 | 115 | 0.015956 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2406-2_0_5_trafo_61 | 0.25 MVA 20/0.4 kV | 117 | 27 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12
0 | 2624525.4565 | 1239604.8257 | 2624521.1576 | 1239610.2855
1 | 2624536.9238 | 1239590.2617 | 2624525.4565 | 1239604.8257
2 | 2624506.1291 | 1239629.3725 | 2624521.1576 | 1239610.2855
3 | 2624536.9238 | 1239590.2617 | 2624505.5087 | 1239563.1263
4 | 2624493.5953 | 1239645.0158 | 2624506.1291 | 1239629.3725
5 | 2624505.5087 | 1239563.1263 | 2624489.6595 | 1239547.6913
6 | 2624481.1479 | 1239633.0949 | 2624478.152 | 1239623.0137
7 | 2624467.6381 | 1239619.1553 | 2624472.9018 | 1239625.1977 | 2624481.1479 | 1239633.0949
8 | 2624493.5953 | 1239645.0158 | 2624481.1479 | 1239633.0949
9 | 2624448.2466 | 1239703.0432 | 2624428.3413 | 1239685.8402
10 | 2624453.5142 | 1239707.5958 | 2624448.2466 | 1239703.0432
11 | 2624426.8492 | 1239684.5507 | 2624428.3413 | 1239685.8402
12 | 2624473.8414 | 1239725.1635 | 2624453.5142 | 1239707.5958
13 | 2624493.5953 | 1239645.0158 | 2624510.9637 | 1239661.6495
14 | 2624524.6745 | 1239675.025 | 2624515.3999 | 1239665.8981 | 2624510.9637 | 1239661.6495
15 | 2624574.4361 | 1239622.3143 | 2624593.3017 | 1239641.104 | 2624599.2143 | 1239647.5392
16 | 2624574.4361 | 1239622.3143 | 2624559.9819 | 1239647.6135
17 | 2624605.7824 | 1239654.6876 | 2624599.2143 | 1239647.5392
18 | 2624559.9065 | 1239647.7455 | 2624559.9819 | 1239647.6135
19 | 2624619.0122 | 1239671.8069 | 2624618.7515 | 1239671.4061 | 2624609.9241 | 1239659.1952 | 2624605.7824 | 1239654.6876
20 | 2624533.1216 | 1239683.3376 | 2624559.9065 | 1239647.7455
21 | 2624533.1216 | 1239683.3376 | 2624524.6745 | 1239675.025
22 | 2624533.1216 | 1239683.3376 | 2624542.8771 | 1239692.945
23 | 2624494.679 | 1239743.1722 | 2624483.3414 | 1239733.3738
24 | 2624474.2155 | 1239725.4868 | 2624483.3414 | 1239733.3738
25 | 2624494.679 | 1239743.1722 | 2624511.5228 | 1239757.7294
26 | 2624474.2155 | 1239725.4868 | 2624473.8414 | 1239725.1635
27 | 2624460.0205 | 1239602.8772 | 2624447.6602 | 1239589.4113
28 | 2624467.6381 | 1239619.1553 | 2624460.0205 | 1239602.8772
29 | 2624439.2501 | 1239586.5685 | 2624447.6602 | 1239589.4113
30 | 2624414.4732 | 1239673.8548 | 2624414.3016 | 1239669.6181 | 2624410.6961 | 1239665.5229 | 2624401.5871 | 1239661.1067
31 | 2624392.3683 | 1239656.6373 | 2624401.5871 | 1239661.1067
32 | 2624414.4732 | 1239673.8548 | 2624398.4816 | 1239693.5682
33 | 2624414.4732 | 1239673.8548 | 2624426.8492 | 1239684.5507
34 | 2624392.3683 | 1239656.6373 | 2624372.768 | 1239647.1346
35 | 2624315.318 | 1239681.4813 | 2624309.669 | 1239678.745
36 | 2624323.7726 | 1239686.9248 | 2624319.6121 | 1239683.5613 | 2624315.318 | 1239681.4813
37 | 2624292.4822 | 1239670.7194 | 2624299.9593 | 1239674.0417 | 2624309.669 | 1239678.745
38 | 2624323.7726 | 1239686.9248 | 2624325.5464 | 1239691.4238 | 2624326.7345 | 1239698.6109 | 2624328.8588 | 1239704.3232 | 2624330.8077 | 1239707.6406
39 | 2624323.7726 | 1239686.9248 | 2624327.9412 | 1239682.7837 | 2624335.8199 | 1239665.0857
40 | 2624292.4822 | 1239670.7194 | 2624279.3521 | 1239664.8852 | 2624269.9066 | 1239661.8092
41 | 2624349.9661 | 1239732.6145 | 2624338.7034 | 1239719.4062 | 2624332.486 | 1239710.4975 | 2624330.8077 | 1239707.6406
42 | 2624335.8199 | 1239665.0857 | 2624342.7727 | 1239649.4673
43 | 2624269.9066 | 1239661.8092 | 2624268.639 | 1239661.3964
44 | 2624366.864 | 1239752.7424 | 2624363.3025 | 1239749.0032 | 2624360.0995 | 1239744.4984 | 2624349.9661 | 1239732.6145
45 | 2624334.0678 | 1239629.9452 | 2624343.9421 | 1239634.8858 | 2624345.61 | 1239639.3732 | 2624345.297 | 1239643.797 | 2624342.7727 | 1239649.4673
46 | 2624366.864 | 1239752.7424 | 2624375.4039 | 1239757.7027 | 2624390.903 | 1239765.8046 | 2624401.4057 | 1239771.5624
47 | 2624366.864 | 1239752.7424 | 2624358.0992 | 1239751.0054 | 2624352.0991 | 1239750.0024 | 2624345.802 | 1239749.4986 | 2624340.6021 | 1239748.7991 | 2624338.7976 | 1239748.5755
48 | 2624334.0678 | 1239629.9452 | 2624317.0143 | 1239621.4123
49 | 2624321.0615 | 1239451.2106 | 2624337.1633 | 1239464.3007
50 | 2624345.8442 | 1239471.3579 | 2624337.1633 | 1239464.3007
51 | 2624307.6019 | 1239463.7968 | 2624321.0615 | 1239451.2106
52 | 2624321.0615 | 1239451.2106 | 2624326.1009 | 1239446.8173 | 2624330.5707 | 1239442.9999
53 | 2624345.8442 | 1239471.3579 | 2624363.5998 | 1239493.7001 | 2624372.8618 | 1239505.2152
54 | 2624307.6019 | 1239463.7968 | 2624293.2848 | 1239477.1245 | 2624282.9986 | 1239486.6996 | 2624274.3025 | 1239493.1999
55 | 2624330.5707 | 1239442.9999 | 2624347.7155 | 1239465.1299
56 | 2624372.8618 | 1239505.2152 | 2624376.5471 | 1239509.7971
57 | 2624323.8847 | 1239592.9776 | 2624317.4025 | 1239606.4634
58 | 2624317.4025 | 1239606.4634 | 2624313.3135 | 1239614.9703 | 2624313.2998 | 1239618.328 | 2624313.2998 | 1239618.328
59 | 2624347.7155 | 1239465.1299 | 2624361.2631 | 1239482.6169 | 2624363.5516 | 1239485.5069
60 | 2624376.5471 | 1239509.7971 | 2624412.8737 | 1239554.9609
61 | 2624363.5516 | 1239485.5069 | 2624380.0709 | 1239506.3678
62 | 2624412.8737 | 1239554.9609 | 2624427.2163 | 1239543.5223
63 | 2624414.6122 | 1239557.1224 | 2624412.8737 | 1239554.9609
64 | 2624439.2501 | 1239586.5685 | 2624426.8986 | 1239572.3978 | 2624414.6122 | 1239557.1224
65 | 2624439.2501 | 1239586.5685 | 2624427.3338 | 1239596.9385
66 | 2624415.7303 | 1239605.32 | 2624419.5405 | 1239603.7205 | 2624427.3338 | 1239596.9385
67 | 2624542.8771 | 1239692.945 | 2624543.9394 | 1239693.9912
68 | 2624498.4821 | 1239792.6218 | 2624520.2501 | 1239811.2913
69 | 2624495.5223 | 1239790.0833 | 2624498.4821 | 1239792.6218
70 | 2624520.2501 | 1239811.2913 | 2624529.7019 | 1239819.3977 | 2624531.1069 | 1239820.66
71 | 2624495.5223 | 1239790.0833 | 2624469.3224 | 1239767.6127
72 | 2624542.4034 | 1239831.0018 | 2624541.5001 | 1239829.9974 | 2624531.1069 | 1239820.66
73 | 2624458.7992 | 1239759.2014 | 2624467.2037 | 1239765.7957 | 2624469.3224 | 1239767.6127
74 | 2624542.4034 | 1239831.0018 | 2624548.2439 | 1239823.0209 | 2624550.4538 | 1239815.2585 | 2624549.2244 | 1239805.3138 | 2624549.0868 | 1239804.987
75 | 2624528.6003 | 1239840.8066 | 2624529.0007 | 1239840.8972 | 2624536.4992 | 1239841.6063 | 2624546.5994 | 1239842.2039 | 2624550.401 | 1239842.6977 | 2624549.5004 | 1239839.2029 | 2624548.1034 | 1239836.8957 | 2624542.4034 | 1239831.0018
76 | 2624458.7992 | 1239759.2014 | 2624445.6758 | 1239749.869
77 | 2624458.7992 | 1239759.2014 | 2624458.0982 | 1239760.4993 | 2624450.0554 | 1239772.8246
78 | 2624549.0868 | 1239804.987 | 2624543.1213 | 1239790.824 | 2624538.4616 | 1239783.9843
79 | 2624528.6003 | 1239840.8066 | 2624521.6996 | 1239839.9999 | 2624506.5991 | 1239838.0031
80 | 2624528.6003 | 1239840.8066 | 2624529.0007 | 1239840.8972 | 2624529.0002 | 1239846.5007 | 2624529.3008 | 1239854.2957 | 2624529.1022 | 1239862.0998 | 2624527.9995 | 1239867.2985 | 2624525.9004 | 1239870.2028 | 2624523.0985 | 1239873.0041 | 2624518.8985 | 1239875.5995 | 2624509.4998 | 1239879.0963 | 2624501.9029 | 1239882.1003 | 2624498.4007 | 1239884.1983 | 2624495.9984 | 1239887.3014
81 | 2624528.6003 | 1239840.8066 | 2624506.5458 | 1239841.7496 | 2624501.9364 | 1239842.5123
82 | 2624445.6758 | 1239749.869 | 2624435.7918 | 1239742.8402
83 | 2624511.5228 | 1239757.7294 | 2624523.2975 | 1239767.9057 | 2624534.4698 | 1239778.1248 | 2624538.4616 | 1239783.9843
84 | 2624506.5991 | 1239838.0031 | 2624493.6021 | 1239835.7037 | 2624483.1001 | 1239833.5035 | 2624470.9034 | 1239831.4965 | 2624465.4016 | 1239830.7067 | 2624460.0993 | 1239829.2062 | 2624454.4042 | 1239827.604 | 2624446.8008 | 1239824.8043 | 2624440.7333 | 1239822.219
85 | 2624506.5991 | 1239838.0031 | 2624504.8041 | 1239835.0049 | 2624502.6039 | 1239833.1058 | 2624491.9033 | 1239827.7028 | 2624476.6019 | 1239819.4012 | 2624462.5032 | 1239811.0047 | 2624452.879 | 1239804.5528
86 | 2624495.9984 | 1239887.3014 | 2624490.19 | 1239885.6654 | 2624483.4979 | 1239885.6378 | 2624474.0629 | 1239886.9554 | 2624465.6319 | 1239890.5118 | 2624457.9394 | 1239898.3629 | 2624454.9713 | 1239904.8214
87 | 2624423.7999 | 1239815.0037 | 2624440.7333 | 1239822.219
88 | 2624427.4673 | 1239787.8205 | 2624434.9025 | 1239792.5019 | 2624452.879 | 1239804.5528
89 | 2624316.2679 | 1239742.59 | 2624301.0741 | 1239736.3677
90 | 2624290.6858 | 1239732.186 | 2624297.0042 | 1239734.701 | 2624301.0741 | 1239736.3677
91 | 2624316.2679 | 1239742.59 | 2624319.4589 | 1239743.8968
92 | 2624257.6265 | 1239719.0272 | 2624290.6858 | 1239732.186
93 | 2624338.7976 | 1239748.5755 | 2624334.2004 | 1239748.0057 | 2624330.0975 | 1239747.1996 | 2624325.603 | 1239746.0027 | 2624320.2035 | 1239744.2017 | 2624319.4589 | 1239743.8968
94 | 2624338.7976 | 1239748.5755 | 2624330.0466 | 1239788.128
95 | 2624638.9909 | 1239702.5135 | 2624619.0122 | 1239671.8069
96 | 2624566.6538 | 1239718.8694 | 2624557.8865 | 1239709.1103
97 | 2624566.6538 | 1239718.8694 | 2624567.4017 | 1239719.7019 | 2624575.1729 | 1239729.1632
98 | 2624543.9394 | 1239693.9912 | 2624547.1001 | 1239697.1039 | 2624557.8865 | 1239709.1103
99 | 2624590.8383 | 1239748.2354 | 2624575.1729 | 1239729.1632
100 | 2624595.1172 | 1239753.4449 | 2624590.8383 | 1239748.2354
101 | 2624423.7999 | 1239815.0037 | 2624420.712 | 1239810.0991 | 2624396.4009 | 1239798.1543
102 | 2624376.203 | 1239788.2304 | 2624396.4009 | 1239798.1543
103 | 2624415.7303 | 1239605.32 | 2624403.8294 | 1239610.3158 | 2624398.1809 | 1239617.4471
104 | 2624372.768 | 1239647.1346 | 2624398.1809 | 1239617.4471
105 | 2624371.9567 | 1239646.7413 | 2624372.768 | 1239647.1346
106 | 2624401.4057 | 1239771.5624 | 2624402.4237 | 1239751.9988 | 2624400.5798 | 1239750.7732
107 | 2624401.4057 | 1239771.5624 | 2624403.2995 | 1239772.6042 | 2624410.9399 | 1239777.4147
108 | 2624394.402 | 1239746.6667 | 2624400.5798 | 1239750.7732
109 | 2624427.4673 | 1239787.8205 | 2624410.9399 | 1239777.4147
110 | 2624387.4614 | 1239742.0534 | 2624394.402 | 1239746.6667
111 | 2624313.2998 | 1239618.328 | 2624316.0946 | 1239620.9521 | 2624317.0143 | 1239621.4123
112 | 2624442.874 | 1239528.0994 | 2624427.2163 | 1239543.5223
113 | 2624442.874 | 1239528.0994 | 2624444.6809 | 1239526.3196
114 | 2624380.0709 | 1239506.3678 | 2624396.8679 | 1239527.5794
115 | 2624422.7882 | 1239733.593 | 2624435.7918 | 1239742.8402

## bus_geodata
| x | y | coords
0 | 2624525.4565 | 1239604.8257
1 | 2624521.1576 | 1239610.2855
2 | 2624536.9238 | 1239590.2617
3 | 2624506.1291 | 1239629.3725
4 | 2624505.5087 | 1239563.1263
5 | 2624478.152 | 1239623.0137
6 | 2624481.1479 | 1239633.0949
7 | 2624448.2466 | 1239703.0432
8 | 2624428.3413 | 1239685.8402
9 | 2624453.5142 | 1239707.5958
10 | 2624493.5953 | 1239645.0158
11 | 2624510.9637 | 1239661.6495
12 | 2624574.4361 | 1239622.3143
13 | 2624599.2143 | 1239647.5392
14 | 2624559.9819 | 1239647.6135
15 | 2624489.6595 | 1239547.6913
16 | 2624605.7824 | 1239654.6876
17 | 2624559.9065 | 1239647.7455
18 | 2624524.6745 | 1239675.025
19 | 2624533.1216 | 1239683.3376
20 | 2624483.3414 | 1239733.3738
21 | 2624494.679 | 1239743.1722
22 | 2624474.2155 | 1239725.4868
23 | 2624460.0205 | 1239602.8772
24 | 2624447.6602 | 1239589.4113
25 | 2624467.6381 | 1239619.1553
26 | 2624401.5871 | 1239661.1067
27 | 2624414.4732 | 1239673.8548
28 | 2624392.3683 | 1239656.6373
29 | 2624315.318 | 1239681.4813
30 | 2624309.669 | 1239678.745
31 | 2624323.7726 | 1239686.9248
32 | 2624292.4822 | 1239670.7194
33 | 2624330.8077 | 1239707.6406
34 | 2624335.8199 | 1239665.0857
35 | 2624269.9066 | 1239661.8092
36 | 2624349.9661 | 1239732.6145
37 | 2624342.7727 | 1239649.4673
38 | 2624268.639 | 1239661.3964
39 | 2624366.864 | 1239752.7424
40 | 2624334.0678 | 1239629.9452
41 | 2624337.1633 | 1239464.3007
42 | 2624321.0615 | 1239451.2106
43 | 2624345.8442 | 1239471.3579
44 | 2624307.6019 | 1239463.7968
45 | 2624330.5707 | 1239442.9999
46 | 2624372.8618 | 1239505.2152
47 | 2624323.8847 | 1239592.9776
48 | 2624317.4025 | 1239606.4634
49 | 2624274.3025 | 1239493.1999
50 | 2624347.7155 | 1239465.1299
51 | 2624376.5471 | 1239509.7971
52 | 2624363.5516 | 1239485.5069
53 | 2624412.8737 | 1239554.9609
54 | 2624426.8492 | 1239684.5507
55 | 2624473.8414 | 1239725.1635
56 | 2624398.4816 | 1239693.5682
57 | 2624439.2501 | 1239586.5685
58 | 2624414.6122 | 1239557.1224
59 | 2624427.3338 | 1239596.9385
60 | 2624542.8771 | 1239692.945
61 | 2624498.4821 | 1239792.6218
62 | 2624520.2501 | 1239811.2913
63 | 2624495.5223 | 1239790.0833
64 | 2624531.1069 | 1239820.66
65 | 2624469.3224 | 1239767.6127
66 | 2624542.4034 | 1239831.0018
67 | 2624458.7992 | 1239759.2014
68 | 2624549.0868 | 1239804.987
69 | 2624528.6003 | 1239840.8066
70 | 2624445.6758 | 1239749.869
71 | 2624450.0554 | 1239772.8246
72 | 2624538.4616 | 1239783.9843
73 | 2624506.5991 | 1239838.0031
74 | 2624495.9984 | 1239887.3014
75 | 2624501.9364 | 1239842.5123
76 | 2624511.5228 | 1239757.7294
77 | 2624440.7333 | 1239822.219
78 | 2624452.879 | 1239804.5528
79 | 2624454.9713 | 1239904.8214
80 | 2624301.0741 | 1239736.3677
81 | 2624316.2679 | 1239742.59
82 | 2624290.6858 | 1239732.186
83 | 2624319.4589 | 1239743.8968
84 | 2624257.6265 | 1239719.0272
85 | 2624338.7976 | 1239748.5755
86 | 2624330.0466 | 1239788.128
87 | 2624619.0122 | 1239671.8069
88 | 2624638.9909 | 1239702.5135
89 | 2624566.6538 | 1239718.8694
90 | 2624557.8865 | 1239709.1103
91 | 2624575.1729 | 1239729.1632
92 | 2624543.9394 | 1239693.9912
93 | 2624590.8383 | 1239748.2354
94 | 2624595.1172 | 1239753.4449
95 | 2624423.7999 | 1239815.0037
96 | 2624396.4009 | 1239798.1543
97 | 2624376.203 | 1239788.2304
98 | 2624415.7303 | 1239605.32
99 | 2624398.1809 | 1239617.4471
100 | 2624372.768 | 1239647.1346
101 | 2624371.9567 | 1239646.7413
102 | 2624401.4057 | 1239771.5624
103 | 2624400.5798 | 1239750.7732
104 | 2624410.9399 | 1239777.4147
105 | 2624394.402 | 1239746.6667
106 | 2624427.4673 | 1239787.8205
107 | 2624313.2998 | 1239618.328
108 | 2624317.0143 | 1239621.4123
109 | 2624427.2163 | 1239543.5223
110 | 2624442.874 | 1239528.0994
111 | 2624444.6809 | 1239526.3196
112 | 2624380.0709 | 1239506.3678
113 | 2624396.8679 | 1239527.5794
114 | 2624435.7918 | 1239742.8402
115 | 2624422.7882 | 1239733.593
116 | 2624387.4614 | 1239742.0534
117 | 2624398.4816 | 1239693.5682

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98057 | -0.13616 | 0.0016951 | 0.00042484
1 | 0.98063 | -0.13578 | 0.0011448 | 0.00028691
2 | 0.98048 | -0.13685 | 0 | 0
3 | 0.98085 | -0.13416 | 0.0017065 | 0.00042768
4 | 0.98026 | -0.1384 | 0.0015266 | 0.0003826
5 | 0.98206 | -0.12559 | 0.0060365 | 0.0015129
6 | 0.98215 | -0.12494 | 0.0022604 | 0.00056651
7 | 0.99681 | -0.021958 | 0.0013522 | 0.00033888
8 | 0.99865 | -0.009277 | 0.0018898 | 0.00047363
9 | 0.99633 | -0.025274 | 0.0038111 | 0.00095515
10 | 0.98109 | -0.13247 | 0.0025328 | 0.00063477
11 | 0.97999 | -0.14033 | 0.0026781 | 0.0006712
12 | 0.97766 | -0.15697 | 0 | 0
13 | 0.97727 | -0.15979 | 0.0024235 | 0.00060739
14 | 0.97799 | -0.15465 | 0.0024093 | 0.00060383
15 | 0.98019 | -0.13888 | 0.0020606 | 0.00051643
16 | 0.97719 | -0.16032 | 0.0021529 | 0.00053956
17 | 0.97799 | -0.15463 | 0.0012891 | 0.00032308
18 | 0.97918 | -0.14607 | 0.0020544 | 0.00051488
19 | 0.97872 | -0.14937 | 0.0010828 | 0.00027138
20 | 0.99375 | -0.04315 | 0.00079964 | 0.00020041
21 | 0.9928 | -0.04974 | 0.0012231 | 0.00030655
22 | 0.99452 | -0.037806 | 0.0016458 | 0.00041249
23 | 0.98501 | -0.10465 | 0.0021968 | 0.00055057
24 | 0.98652 | -0.09394 | 0.0012175 | 0.00030514
25 | 0.98357 | -0.1148 | 0.0043694 | 0.0010951
26 | 0.99823 | -0.012214 | 0.0063751 | 0.0015978
27 | 1 | 0 | -0.23147 | -0.058321
28 | 0.99736 | -0.018217 | 0.0030868 | 0.00077362
29 | 0.97251 | -0.19333 | 0.0030949 | 0.00077566
30 | 0.9724 | -0.19407 | 0.0017749 | 0.00044483
31 | 0.97272 | -0.19181 | 0 | 0
32 | 0.97214 | -0.19596 | 0.0030011 | 0.00075215
33 | 0.9738 | -0.18404 | 0.0026889 | 0.0006739
34 | 0.97201 | -0.1969 | 0.0021147 | 0.00052999
35 | 0.97191 | -0.19761 | 0.0037407 | 0.00093751
36 | 0.97547 | -0.17209 | 0.0022173 | 0.0005557
37 | 0.97158 | -0.19996 | 0.0031012 | 0.00077722
38 | 0.97191 | -0.19765 | 0.0026763 | 0.00067074
39 | 0.97621 | -0.1668 | 0 | 0
40 | 0.97104 | -0.20385 | 0.0030171 | 0.00075616
41 | 0.98007 | -0.13976 | 0.0041704 | 0.0010452
42 | 0.97964 | -0.14289 | 0 | 0
43 | 0.98038 | -0.13759 | 0 | 0
44 | 0.97955 | -0.14348 | 0 | 0
45 | 0.97943 | -0.14438 | 0 | 0
46 | 0.98156 | -0.12919 | 0.012936 | 0.0032421
47 | 0.97051 | -0.2077 | 0.0023735 | 0.00059487
48 | 0.97056 | -0.20732 | 0.0038193 | 0.00095722
49 | 0.97935 | -0.14491 | 0.003086 | 0.00077342
50 | 0.97896 | -0.14771 | 0.0021583 | 0.00054093
51 | 0.98183 | -0.12726 | 0.0023714 | 0.00059433
52 | 0.97861 | -0.1502 | 0.00098831 | 0.00024769
53 | 0.98469 | -0.10691 | 0.002876 | 0.00072078
54 | 0.99879 | -0.0083097 | 0.0036354 | 0.00091113
55 | 0.99455 | -0.037583 | 0.0015815 | 0.00039637
56 | 0.99993 | -0.00048286 | 0.0019066 | 0.00047785
57 | 0.98727 | -0.088639 | 0 | 0
58 | 0.98486 | -0.10571 | 0.0012944 | 0.00032441
59 | 0.98961 | -0.072248 | 0.002579 | 0.00064637
60 | 0.97844 | -0.15142 | 0.0020121 | 0.00050428
61 | 0.98507 | -0.10395 | 0.0013727 | 0.00034404
62 | 0.98546 | -0.10117 | 0.0013934 | 0.00034922
63 | 0.98502 | -0.10428 | 0.0016075 | 0.00040287
64 | 0.98568 | -0.099577 | 0.0014086 | 0.00035303
65 | 0.9847 | -0.10656 | 0.0017643 | 0.00044217
66 | 0.98596 | -0.097651 | 0 | 0
67 | 0.98461 | -0.10721 | 0 | 0
68 | 0.98765 | -0.085713 | 0.00093679 | 0.00023478
69 | 0.9841 | -0.11075 | 0 | 0
70 | 0.98452 | -0.10783 | 0.0014665 | 0.00036754
71 | 0.98459 | -0.10737 | 0.00094882 | 0.0002378
72 | 0.98909 | -0.075668 | 0.0013391 | 0.00033562
73 | 0.98305 | -0.11814 | 0 | 0
74 | 0.98384 | -0.11255 | 0 | 0
75 | 0.984 | -0.11144 | 0.0025115 | 0.00062943
76 | 0.99141 | -0.059415 | 0.0012063 | 0.00030232
77 | 0.98265 | -0.12098 | 0.0018262 | 0.0004577
78 | 0.98022 | -0.13821 | 0.0017108 | 0.00042878
79 | 0.98365 | -0.11391 | 0.0026556 | 0.00066555
80 | 0.97527 | -0.17351 | 0.0018932 | 0.00047449
81 | 0.97541 | -0.17252 | 0.0020862 | 0.00052284
82 | 0.97521 | -0.17396 | 0.0018252 | 0.00045744
83 | 0.97545 | -0.17223 | 0.0015216 | 0.00038136
84 | 0.9751 | -0.17473 | 0.0020418 | 0.00051173
85 | 0.97572 | -0.17027 | 0.00095932 | 0.00024043
86 | 0.97565 | -0.17082 | 0.0013049 | 0.00032703
87 | 0.9771 | -0.16101 | 0.0019806 | 0.00049639
88 | 0.97704 | -0.16142 | 0.001063 | 0.00026641
89 | 0.97795 | -0.15493 | 0.0018528 | 0.00046435
90 | 0.9781 | -0.15382 | 0.0022749 | 0.00057016
91 | 0.97783 | -0.15579 | 0.0021313 | 0.00053416
92 | 0.97841 | -0.15161 | 0.0020021 | 0.00050178
93 | 0.97768 | -0.15684 | 0.0019351 | 0.00048499
94 | 0.97766 | -0.15699 | 0.0021236 | 0.00053222
95 | 0.98259 | -0.12139 | 0 | 0
96 | 0.98249 | -0.12214 | 0.00099497 | 0.00024936
97 | 0.98245 | -0.12242 | 0.001202 | 0.00030126
98 | 0.9907 | -0.064581 | 0.00451 | 0.0011303
99 | 0.99244 | -0.052444 | 0.0016095 | 0.00040337
100 | 0.99556 | -0.030677 | 0.0021081 | 0.00052833
101 | 0.99556 | -0.030689 | 0.0014118 | 0.00035384
102 | 0.97764 | -0.15655 | 0 | 0
103 | 0.97748 | -0.15773 | 0.0027025 | 0.00067732
104 | 0.97809 | -0.15333 | 0.0015854 | 0.00039734
105 | 0.97745 | -0.15793 | 0.0012065 | 0.00030237
106 | 0.9789 | -0.14755 | 0.0022697 | 0.00056884
107 | 0.97068 | -0.20648 | 0.0023157 | 0.00058037
108 | 0.97074 | -0.20604 | 0.0023485 | 0.00058858
109 | 0.98456 | -0.10788 | 0.0014932 | 0.00037424
110 | 0.98444 | -0.1087 | 0.0022757 | 0.00057035
111 | 0.98443 | -0.10873 | 0.0013516 | 0.00033875
112 | 0.97829 | -0.1525 | 0.0026416 | 0.00066206
113 | 0.97807 | -0.15409 | 0.0056303 | 0.0014111
114 | 0.98448 | -0.10811 | 0.0012038 | 0.0003017
115 | 0.98446 | -0.10829 | 0.0010542 | 0.0002642
116 | 0.97743 | -0.15804 | 0.0012865 | 0.00032242
117 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0052835 | -0.0013233 | 0.0052838 | 0.0013233 | 2.7872e-07 | 1.9538e-08 | 0.0080174 | 0.0080174 | 0.0080174 | 0.98057 | -0.13616 | 0.98063 | -0.13578 | 2.9694
1 | 0.0035884 | 0.00089847 | -0.003588 | -0.00089857 | 3.4295e-07 | -1.0191e-07 | 0.005445 | 0.0054451 | 0.0054451 | 0.98057 | -0.13616 | 0.98048 | -0.13685 | 2.0167
2 | -0.0064286 | -0.0016102 | 0.00643 | 0.0016105 | 1.4424e-06 | 2.482e-07 | 0.0097545 | 0.0097544 | 0.0097545 | 0.98063 | -0.13578 | 0.98085 | -0.13416 | 3.6128
3 | 0.003588 | 0.00089857 | -0.0035873 | -0.0008988 | 7.6805e-07 | -2.2803e-07 | 0.0054451 | 0.0054453 | 0.0054453 | 0.98048 | -0.13685 | 0.98026 | -0.1384 | 2.0168
4 | -0.0081365 | -0.0020382 | 0.0081384 | 0.0020386 | 1.9057e-06 | 4.7988e-07 | 0.012343 | 0.012343 | 0.012343 | 0.98085 | -0.13416 | 0.98109 | -0.13247 | 4.5716
5 | 0.0020607 | 0.0005162 | -0.0020606 | -0.00051643 | 1.3508e-07 | -2.2692e-07 | 0.003128 | 0.0031281 | 0.0031281 | 0.98026 | -0.1384 | 0.98019 | -0.13888 | 1.1586
6 | -0.0060365 | -0.0015129 | 0.006037 | 0.001513 | 5.4901e-07 | 7.8078e-08 | 0.0091465 | 0.0091464 | 0.0091465 | 0.98206 | -0.12559 | 0.98215 | -0.12494 | 3.3876
7 | -0.050573 | -0.012688 | 0.050644 | 0.012715 | 7.1192e-05 | 2.7135e-05 | 0.076625 | 0.076625 | 0.076625 | 0.98215 | -0.12494 | 0.98357 | -0.1148 | 28.3798
8 | 0.042275 | 0.010608 | -0.042231 | -0.010592 | 4.4126e-05 | 1.6754e-05 | 0.064054 | 0.064054 | 0.064054 | 0.98215 | -0.12494 | 0.98109 | -0.13247 | 23.7238
9 | -0.097688 | -0.024689 | 0.097862 | 0.024756 | 0.00017473 | 6.6516e-05 | 0.1459 | 0.1459 | 0.1459 | 0.99681 | -0.021958 | 0.99865 | -0.009277 | 27.0183
10 | 0.096336 | 0.02435 | -0.096291 | -0.024333 | 4.4969e-05 | 1.7114e-05 | 0.14388 | 0.14388 | 0.14388 | 0.99681 | -0.021958 | 0.99633 | -0.025274 | 26.6445
11 | -0.099752 | -0.025229 | 0.099766 | 0.025235 | 1.3608e-05 | 5.1823e-06 | 0.14871 | 0.14871 | 0.14871 | 0.99865 | -0.009277 | 0.99879 | -0.0083097 | 27.5397
12 | 0.092479 | 0.023378 | -0.092319 | -0.023317 | 0.00016007 | 6.0867e-05 | 0.13819 | 0.13819 | 0.13819 | 0.99633 | -0.025274 | 0.99455 | -0.037583 | 25.5905
13 | 0.03156 | 0.0079182 | -0.031526 | -0.0079053 | 3.4388e-05 | 1.2923e-05 | 0.04787 | 0.04787 | 0.04787 | 0.98109 | -0.13247 | 0.97999 | -0.14033 | 17.7296
14 | 0.028847 | 0.0072341 | -0.028824 | -0.0072255 | 2.2934e-05 | 8.5796e-06 | 0.043803 | 0.043804 | 0.043804 | 0.97999 | -0.14033 | 0.97918 | -0.14607 | 16.2235
15 | 0.0076237 | 0.0019099 | -0.0076207 | -0.0019092 | 2.9711e-06 | 6.9944e-07 | 0.011603 | 0.011603 | 0.011603 | 0.97766 | -0.15697 | 0.97727 | -0.15979 | 4.2975
16 | -0.0076237 | -0.0019099 | 0.0076261 | 0.0019105 | 2.4478e-06 | 5.7597e-07 | 0.011603 | 0.011603 | 0.011603 | 0.97766 | -0.15697 | 0.97799 | -0.15465 | 4.2974
17 | 0.0051972 | 0.0013018 | -0.0051968 | -0.0013018 | 3.7931e-07 | 2.4266e-08 | 0.0079131 | 0.0079132 | 0.0079132 | 0.97727 | -0.15979 | 0.97719 | -0.16032 | 2.9308
18 | -0.010035 | -0.0025143 | 0.010035 | 0.0025143 | 2.2124e-08 | 6.6011e-09 | 0.015269 | 0.015269 | 0.015269 | 0.97799 | -0.15465 | 0.97799 | -0.15463 | 5.6551
19 | 0.0030439 | 0.0007622 | -0.0030436 | -0.00076236 | 2.9045e-07 | -1.597e-07 | 0.0046349 | 0.004635 | 0.004635 | 0.97719 | -0.16032 | 0.9771 | -0.16101 | 1.7167
20 | -0.011325 | -0.0028374 | 0.011333 | 0.00284 | 8.2519e-06 | 2.6144e-06 | 0.01723 | 0.01723 | 0.01723 | 0.97799 | -0.15463 | 0.97872 | -0.14937 | 6.3815
21 | 0.02677 | 0.0067106 | -0.026758 | -0.006706 | 1.2239e-05 | 4.5583e-06 | 0.040682 | 0.040682 | 0.040682 | 0.97918 | -0.14607 | 0.97872 | -0.14937 | 15.0673
22 | 0.014342 | 0.0035947 | -0.014338 | -0.0035933 | 4.0624e-06 | 1.3904e-06 | 0.021805 | 0.021805 | 0.021805 | 0.97872 | -0.14937 | 0.97844 | -0.15142 | 8.0761
23 | 0.088223 | 0.022282 | -0.088141 | -0.022251 | 8.1663e-05 | 3.1021e-05 | 0.13216 | 0.13216 | 0.13216 | 0.99375 | -0.04315 | 0.9928 | -0.04974 | 24.4746
24 | -0.089022 | -0.022482 | 0.089089 | 0.022507 | 6.6929e-05 | 2.5429e-05 | 0.13336 | 0.13336 | 0.13336 | 0.99375 | -0.04315 | 0.99452 | -0.037806 | 24.6963
25 | 0.086918 | 0.021944 | -0.0868 | -0.021899 | 0.00011798 | 4.4803e-05 | 0.13033 | 0.13033 | 0.13033 | 0.9928 | -0.04974 | 0.99141 | -0.059415 | 24.1351
26 | -0.090735 | -0.02292 | 0.090738 | 0.022921 | 2.8457e-06 | 1.0817e-06 | 0.13582 | 0.13582 | 0.13582 | 0.99452 | -0.037806 | 0.99455 | -0.037583 | 25.1523
27 | -0.057288 | -0.01439 | 0.057373 | 0.014423 | 8.5448e-05 | 3.2632e-05 | 0.086554 | 0.086554 | 0.086554 | 0.98501 | -0.10465 | 0.98652 | -0.09394 | 32.0571
28 | 0.055091 | 0.01384 | -0.055013 | -0.01381 | 7.7697e-05 | 2.9655e-05 | 0.083236 | 0.083236 | 0.083236 | 0.98501 | -0.10465 | 0.98357 | -0.1148 | 30.828
29 | -0.058591 | -0.014728 | 0.058634 | 0.014745 | 4.328e-05 | 1.6533e-05 | 0.088391 | 0.08839 | 0.088391 | 0.98652 | -0.09394 | 0.98727 | -0.088639 | 32.7372
30 | -0.12503 | -0.031569 | 0.12524 | 0.031651 | 0.00021498 | 8.2165e-05 | 0.18646 | 0.18646 | 0.18646 | 0.99823 | -0.012214 | 1 | 0 | 34.5289
31 | 0.11865 | 0.029972 | -0.11855 | -0.029933 | 0.00010009 | 3.8228e-05 | 0.17695 | 0.17695 | 0.17695 | 0.99823 | -0.012214 | 0.99736 | -0.018217 | 32.7691
32 | 0.0019068 | 0.00047757 | -0.0019066 | -0.00047785 | 1.2737e-07 | -2.8365e-07 | 0.0028372 | 0.0028373 | 0.0028373 | 1 | 0 | 0.99993 | -0.00048286 | 1.0509
33 | 0.10352 | 0.026192 | -0.1034 | -0.026146 | 0.00012124 | 4.6202e-05 | 0.15413 | 0.15413 | 0.15413 | 1 | 0 | 0.99879 | -0.0083097 | 28.5427
34 | 0.11547 | 0.02916 | -0.11526 | -0.029083 | 0.00020187 | 7.7075e-05 | 0.17235 | 0.17235 | 0.17235 | 0.99736 | -0.018217 | 0.99556 | -0.030677 | 31.9163
35 | 0.011198 | 0.0028066 | -0.011197 | -0.0028062 | 1.1499e-06 | 3.6438e-07 | 0.017134 | 0.017134 | 0.017134 | 0.97251 | -0.19333 | 0.9724 | -0.19407 | 6.346
36 | -0.014293 | -0.0035822 | 0.014296 | 0.0035833 | 3.0207e-06 | 1.0362e-06 | 0.02187 | 0.02187 | 0.02187 | 0.97251 | -0.19333 | 0.97272 | -0.19181 | 8.0999
37 | 0.0094221 | 0.0023614 | -0.0094196 | -0.0023607 | 2.4609e-06 | 7.1122e-07 | 0.014418 | 0.014418 | 0.014418 | 0.9724 | -0.19407 | 0.97214 | -0.19596 | 5.3401
38 | -0.033419 | -0.0083788 | 0.033455 | 0.0083924 | 3.5982e-05 | 1.3565e-05 | 0.051124 | 0.051124 | 0.051124 | 0.97272 | -0.19181 | 0.9738 | -0.18404 | 18.9347
39 | 0.019123 | 0.0047955 | -0.019109 | -0.0047907 | 1.3483e-05 | 4.8727e-06 | 0.029254 | 0.029254 | 0.029254 | 0.97272 | -0.19181 | 0.97201 | -0.1969 | 10.835
40 | 0.0064185 | 0.0016085 | -0.006417 | -0.0016082 | 1.4637e-06 | 2.6172e-07 | 0.0098245 | 0.0098246 | 0.0098246 | 0.97214 | -0.19596 | 0.97191 | -0.19761 | 3.6387
41 | -0.036144 | -0.0090663 | 0.036204 | 0.009089 | 6.003e-05 | 2.2696e-05 | 0.055232 | 0.055232 | 0.055232 | 0.9738 | -0.18404 | 0.97547 | -0.17209 | 20.4565
42 | 0.016995 | 0.0042607 | -0.016987 | -0.0042581 | 7.2211e-06 | 2.5655e-06 | 0.026017 | 0.026017 | 0.026017 | 0.97201 | -0.1969 | 0.97158 | -0.19996 | 9.636
43 | 0.0026763 | 0.00067073 | -0.0026763 | -0.00067074 | 1.3966e-08 | -1.1149e-08 | 0.0040975 | 0.0040975 | 0.0040975 | 0.97191 | -0.19761 | 0.97191 | -0.19765 | 1.5176
44 | -0.038421 | -0.0096447 | 0.038449 | 0.0096549 | 2.8201e-05 | 1.0189e-05 | 0.058615 | 0.058614 | 0.058615 | 0.97547 | -0.17209 | 0.97621 | -0.1668 | 10.8546
45 | 0.013886 | 0.0034809 | -0.013879 | -0.0034783 | 7.4711e-06 | 2.5459e-06 | 0.021268 | 0.021268 | 0.021268 | 0.97158 | -0.19996 | 0.97104 | -0.20385 | 7.8769
46 | -0.050091 | -0.012572 | 0.050163 | 0.012598 | 7.141e-05 | 2.6482e-05 | 0.07636 | 0.07636 | 0.07636 | 0.97621 | -0.1668 | 0.97764 | -0.15655 | 14.1407
47 | 0.011642 | 0.0029171 | -0.011636 | -0.0029153 | 5.5808e-06 | 1.7916e-06 | 0.017746 | 0.017746 | 0.017746 | 0.97621 | -0.1668 | 0.97572 | -0.17027 | 6.5725
48 | 0.010862 | 0.0027222 | -0.010858 | -0.0027212 | 3.2965e-06 | 1.0321e-06 | 0.016644 | 0.016644 | 0.016644 | 0.97104 | -0.20385 | 0.97074 | -0.20604 | 6.1646
49 | 0.014526 | 0.003641 | -0.01452 | -0.0036389 | 6.2987e-06 | 2.1612e-06 | 0.022055 | 0.022055 | 0.022055 | 0.98007 | -0.13976 | 0.97964 | -0.14289 | 8.1686
50 | -0.018697 | -0.0046862 | 0.018702 | 0.0046883 | 5.6255e-06 | 2.0226e-06 | 0.028387 | 0.028387 | 0.028387 | 0.98007 | -0.13976 | 0.98038 | -0.13759 | 10.5137
51 | 0.0030868 | 0.00077296 | -0.0030866 | -0.0007731 | 2.5239e-07 | -1.3457e-07 | 0.0046885 | 0.0046886 | 0.0046886 | 0.97964 | -0.14289 | 0.97955 | -0.14348 | 1.7365
52 | 0.011433 | 0.0028659 | -0.011431 | -0.0028652 | 2.3645e-06 | 7.5128e-07 | 0.017367 | 0.017367 | 0.017367 | 0.97964 | -0.14289 | 0.97943 | -0.14438 | 6.4322
53 | -0.018702 | -0.0046883 | 0.018724 | 0.0046961 | 2.178e-05 | 7.8302e-06 | 0.028387 | 0.028387 | 0.028387 | 0.98038 | -0.13759 | 0.98156 | -0.12919 | 10.5137
54 | 0.0030866 | 0.0007731 | -0.003086 | -0.00077342 | 6.1004e-07 | -3.2506e-07 | 0.0046886 | 0.0046888 | 0.0046888 | 0.97955 | -0.14348 | 0.97935 | -0.14491 | 1.7366
55 | 0.011431 | 0.0028652 | -0.011426 | -0.0028635 | 5.2686e-06 | 1.6743e-06 | 0.017367 | 0.017367 | 0.017367 | 0.97943 | -0.14438 | 0.97896 | -0.14771 | 6.4322
56 | -0.03166 | -0.0079382 | 0.031669 | 0.0079413 | 8.4528e-06 | 3.1767e-06 | 0.047997 | 0.047997 | 0.047997 | 0.98156 | -0.12919 | 0.98183 | -0.12726 | 17.7768
57 | -0.0023735 | -0.00059487 | 0.0023737 | 0.00059473 | 1.2365e-07 | -1.3735e-07 | 0.0036392 | 0.0036391 | 0.0036392 | 0.97051 | -0.2077 | 0.97056 | -0.20732 | 1.3478
58 | -0.006193 | -0.0015519 | 0.0061937 | 0.0015521 | 7.1983e-07 | 1.187e-07 | 0.0094947 | 0.0094947 | 0.0094947 | 0.97056 | -0.20732 | 0.97068 | -0.20648 | 3.5166
59 | 0.0092673 | 0.0023226 | -0.0092641 | -0.0023217 | 3.1954e-06 | 9.0463e-07 | 0.014086 | 0.014086 | 0.014086 | 0.97896 | -0.14771 | 0.97861 | -0.1502 | 5.2172
60 | -0.03404 | -0.0085357 | 0.034136 | 0.008572 | 9.6265e-05 | 3.629e-05 | 0.051591 | 0.051591 | 0.051591 | 0.98183 | -0.12726 | 0.98469 | -0.10691 | 19.1079
61 | 0.0082758 | 0.002074 | -0.0082732 | -0.0020733 | 2.6293e-06 | 6.7704e-07 | 0.012584 | 0.012584 | 0.012584 | 0.97861 | -0.1502 | 0.97829 | -0.1525 | 4.6606
62 | 0.0051217 | 0.0012832 | -0.005121 | -0.0012832 | 6.8571e-07 | 3.0401e-08 | 0.0077395 | 0.0077396 | 0.0077396 | 0.98469 | -0.10691 | 0.98456 | -0.10788 | 2.8665
63 | -0.042134 | -0.010576 | 0.042141 | 0.010579 | 7.0183e-06 | 2.6641e-06 | 0.063677 | 0.063677 | 0.063677 | 0.98469 | -0.10691 | 0.98486 | -0.10571 | 23.5839
64 | 0.043539 | 0.010942 | -0.043435 | -0.010903 | 0.00010322 | 3.921e-05 | 0.065632 | 0.065632 | 0.065632 | 0.98727 | -0.088639 | 0.98486 | -0.10571 | 24.3082
65 | -0.10217 | -0.025687 | 0.10241 | 0.025777 | 0.00023384 | 8.9736e-05 | 0.15402 | 0.15402 | 0.15402 | 0.98727 | -0.088639 | 0.98961 | -0.072248 | 57.0454
66 | -0.10499 | -0.026423 | 0.1051 | 0.026466 | 0.00011251 | 4.2901e-05 | 0.1579 | 0.1579 | 0.1579 | 0.98961 | -0.072248 | 0.9907 | -0.064581 | 29.2408
67 | 0.012326 | 0.003089 | -0.012326 | -0.0030889 | 3.2693e-07 | 1.0702e-07 | 0.018745 | 0.018745 | 0.018745 | 0.97844 | -0.15142 | 0.97841 | -0.15161 | 6.9427
68 | -0.009421 | -0.0023601 | 0.0094247 | 0.0023612 | 3.6239e-06 | 1.0286e-06 | 0.014231 | 0.014231 | 0.014231 | 0.98507 | -0.10395 | 0.98546 | -0.10117 | 5.2707
69 | 0.0080483 | 0.0020161 | -0.008048 | -0.002016 | 3.5962e-07 | 8.8677e-08 | 0.012157 | 0.012157 | 0.012157 | 0.98507 | -0.10395 | 0.98502 | -0.10428 | 4.5027
70 | -0.010818 | -0.0027104 | 0.01082 | 0.0027111 | 2.3876e-06 | 7.3558e-07 | 0.016335 | 0.016335 | 0.016335 | 0.98546 | -0.10117 | 0.98568 | -0.099577 | 6.0499
71 | 0.0064405 | 0.0016131 | -0.0064384 | -0.0016128 | 2.0386e-06 | 3.4487e-07 | 0.0097289 | 0.0097291 | 0.0097291 | 0.98502 | -0.10428 | 0.9847 | -0.10656 | 3.6034
72 | -0.012229 | -0.0030642 | 0.012232 | 0.0030652 | 3.2586e-06 | 1.0579e-06 | 0.018461 | 0.018461 | 0.018461 | 0.98568 | -0.099577 | 0.98596 | -0.097651 | 6.8374
73 | 0.0046742 | 0.0011706 | -0.0046737 | -0.0011706 | 4.1943e-07 | -1.0066e-08 | 0.007063 | 0.007063 | 0.007063 | 0.9847 | -0.10656 | 0.98461 | -0.10721 | 2.6159
74 | -0.082866 | -0.020855 | 0.083005 | 0.020908 | 0.00013834 | 5.2485e-05 | 0.12509 | 0.12509 | 0.12509 | 0.98596 | -0.097651 | 0.98765 | -0.085713 | 23.1656
75 | 0.070634 | 0.01779 | -0.070505 | -0.017741 | 0.00012913 | 4.8739e-05 | 0.10663 | 0.10663 | 0.10663 | 0.98596 | -0.097651 | 0.9841 | -0.11075 | 19.7469
76 | 0.0037249 | 0.00093305 | -0.0037246 | -0.00093313 | 3.1842e-07 | -8.2327e-08 | 0.0056292 | 0.0056292 | 0.0056292 | 0.98461 | -0.10721 | 0.98452 | -0.10783 | 2.0849
77 | 0.00094884 | 0.0002376 | -0.00094882 | -0.0002378 | 2.0775e-08 | -1.9795e-07 | 0.0014339 | 0.001434 | 0.001434 | 0.98461 | -0.10721 | 0.98459 | -0.10737 | 0.53109
78 | -0.083942 | -0.021142 | 0.08406 | 0.021187 | 0.00011806 | 4.4801e-05 | 0.12651 | 0.1265 | 0.12651 | 0.98765 | -0.085713 | 0.98909 | -0.075668 | 23.4269
79 | 0.065337 | 0.016448 | -0.065269 | -0.016422 | 6.7379e-05 | 2.5354e-05 | 0.098819 | 0.098819 | 0.098819 | 0.9841 | -0.11075 | 0.98305 | -0.11814 | 18.2998
80 | 0.0026567 | 0.00066454 | -0.0026561 | -0.00066512 | 6.6071e-07 | -5.7943e-07 | 0.0040167 | 0.004017 | 0.004017 | 0.9841 | -0.11075 | 0.98384 | -0.11255 | 1.4878
81 | 0.0025117 | 0.00062919 | -0.0025115 | -0.00062943 | 2.4072e-07 | -2.4721e-07 | 0.0037977 | 0.0037979 | 0.0037979 | 0.9841 | -0.11075 | 0.984 | -0.11144 | 1.4066
82 | 0.0022581 | 0.00056558 | -0.002258 | -0.0005657 | 8.8146e-08 | -1.2032e-07 | 0.0034127 | 0.0034128 | 0.0034128 | 0.98452 | -0.10783 | 0.98448 | -0.10811 | 1.264
83 | -0.085399 | -0.021523 | 0.085594 | 0.021597 | 0.00019477 | 7.3938e-05 | 0.12852 | 0.12852 | 0.12852 | 0.98909 | -0.075668 | 0.99141 | -0.059415 | 23.7999
84 | 0.0040252 | 0.0010073 | -0.0040236 | -0.0010075 | 1.5744e-06 | -2.559e-07 | 0.0060923 | 0.0060926 | 0.0060926 | 0.98305 | -0.11814 | 0.98265 | -0.12098 | 2.2565
85 | 0.061244 | 0.015415 | -0.061073 | -0.015351 | 0.00017114 | 6.4208e-05 | 0.092727 | 0.092727 | 0.092727 | 0.98305 | -0.11814 | 0.98022 | -0.13821 | 17.1717
86 | 0.0026561 | 0.00066512 | -0.0026556 | -0.00066555 | 4.9743e-07 | -4.3587e-07 | 0.004017 | 0.0040172 | 0.0040172 | 0.98384 | -0.11255 | 0.98365 | -0.11391 | 1.4879
87 | 0.0021974 | 0.00054984 | -0.0021973 | -0.00055003 | 1.2715e-07 | -1.8426e-07 | 0.0033272 | 0.0033273 | 0.0033273 | 0.98265 | -0.12098 | 0.98259 | -0.12139 | 1.2323
88 | 0.059362 | 0.014922 | -0.059285 | -0.014893 | 7.7121e-05 | 2.8896e-05 | 0.09013 | 0.09013 | 0.09013 | 0.98022 | -0.13821 | 0.9789 | -0.14755 | 16.6908
89 | -0.0057607 | -0.0014432 | 0.0057615 | 0.0014433 | 7.9143e-07 | 9.9489e-08 | 0.0087892 | 0.0087891 | 0.0087892 | 0.97527 | -0.17351 | 0.97541 | -0.17252 | 3.2553
90 | 0.0038675 | 0.00096876 | -0.0038672 | -0.0009688 | 2.433e-07 | -4.6155e-08 | 0.0059006 | 0.0059006 | 0.0059006 | 0.97527 | -0.17351 | 0.97521 | -0.17396 | 2.1854
91 | -0.0078477 | -0.0019662 | 0.007848 | 0.0019663 | 3.0838e-07 | 7.5565e-08 | 0.011972 | 0.011972 | 0.011972 | 0.97541 | -0.17252 | 0.97545 | -0.17223 | 4.4339
92 | 0.002042 | 0.00051137 | -0.0020418 | -0.00051173 | 2.1555e-07 | -3.61e-07 | 0.0031157 | 0.0031159 | 0.0031159 | 0.97521 | -0.17396 | 0.9751 | -0.17473 | 1.154
93 | -0.0093696 | -0.0023476 | 0.0093722 | 0.0023484 | 2.5445e-06 | 7.2942e-07 | 0.014293 | 0.014293 | 0.014293 | 0.97545 | -0.17223 | 0.97572 | -0.17027 | 5.2936
94 | 0.001305 | 0.00032656 | -0.0013049 | -0.00032703 | 1.0011e-07 | -4.6742e-07 | 0.00199 | 0.0019901 | 0.0019901 | 0.97572 | -0.17027 | 0.97565 | -0.17082 | 0.73709
95 | 0.001063 | 0.00026597 | -0.001063 | -0.00026641 | 5.9904e-08 | -4.3578e-07 | 0.0016187 | 0.0016189 | 0.0016189 | 0.9771 | -0.16101 | 0.97704 | -0.16142 | 0.59959
96 | -0.0080442 | -0.0020157 | 0.0080454 | 0.002016 | 1.2264e-06 | 3.0705e-07 | 0.01224 | 0.01224 | 0.01224 | 0.97795 | -0.15493 | 0.9781 | -0.15382 | 4.5332
97 | 0.0061914 | 0.0015513 | -0.0061907 | -0.0015512 | 7.4001e-07 | 1.1697e-07 | 0.0094205 | 0.0094206 | 0.0094206 | 0.97795 | -0.15493 | 0.97783 | -0.15579 | 3.4891
98 | -0.01032 | -0.0025861 | 0.010324 | 0.0025871 | 3.165e-06 | 9.5898e-07 | 0.015701 | 0.0157 | 0.015701 | 0.9781 | -0.15382 | 0.97841 | -0.15161 | 5.815
99 | 0.0040593 | 0.0010171 | -0.0040588 | -0.0010171 | 5.8769e-07 | -8.3518e-08 | 0.0061772 | 0.0061774 | 0.0061774 | 0.97783 | -0.15579 | 0.97768 | -0.15684 | 2.2879
100 | 0.0021236 | 0.00053215 | -0.0021236 | -0.00053222 | 4.3946e-08 | -6.7636e-08 | 0.0032321 | 0.0032321 | 0.0032321 | 0.97768 | -0.15684 | 0.97766 | -0.15699 | 1.1971
101 | 0.0021973 | 0.00055003 | -0.0021971 | -0.00055036 | 2.2717e-07 | -3.2909e-07 | 0.0033273 | 0.0033274 | 0.0033274 | 0.98259 | -0.12139 | 0.98249 | -0.12214 | 1.2324
102 | 0.0012021 | 0.00030099 | -0.001202 | -0.00030126 | 4.6544e-08 | -2.6708e-07 | 0.0018205 | 0.0018206 | 0.0018206 | 0.98249 | -0.12214 | 0.98245 | -0.12242 | 0.6743
103 | -0.10961 | -0.027596 | 0.10979 | 0.027667 | 0.00018617 | 7.1037e-05 | 0.16467 | 0.16467 | 0.16467 | 0.9907 | -0.064581 | 0.99244 | -0.052444 | 30.4952
104 | -0.1114 | -0.028071 | 0.11174 | 0.0282 | 0.00034039 | 0.00012991 | 0.16709 | 0.16709 | 0.16709 | 0.99244 | -0.052444 | 0.99556 | -0.030677 | 30.9421
105 | 0.0014118 | 0.00035383 | -0.0014118 | -0.00035384 | 2.5052e-09 | -1.076e-08 | 0.0021102 | 0.0021102 | 0.0021102 | 0.99556 | -0.030677 | 0.99556 | -0.030689 | 0.78156
106 | 0.0051964 | 0.001302 | -0.0051956 | -0.0013019 | 8.511e-07 | 5.3985e-08 | 0.0079091 | 0.0079092 | 0.0079092 | 0.97764 | -0.15655 | 0.97748 | -0.15773 | 2.9293
107 | -0.055359 | -0.0139 | 0.055384 | 0.01391 | 2.4792e-05 | 9.2548e-06 | 0.084269 | 0.084269 | 0.084269 | 0.97764 | -0.15655 | 0.97809 | -0.15333 | 15.6053
108 | 0.002493 | 0.00062462 | -0.002493 | -0.00062469 | 6.6669e-08 | -6.7341e-08 | 0.0037951 | 0.0037951 | 0.0037951 | 0.97748 | -0.15773 | 0.97745 | -0.15793 | 1.4056
109 | -0.056969 | -0.014307 | 0.057015 | 0.014324 | 4.5783e-05 | 1.7118e-05 | 0.086681 | 0.08668 | 0.086681 | 0.97809 | -0.15333 | 0.9789 | -0.14755 | 16.0519
110 | 0.0012865 | 0.00032232 | -0.0012865 | -0.00032242 | 1.9946e-08 | -9.6786e-08 | 0.0019584 | 0.0019585 | 0.0019585 | 0.97745 | -0.15793 | 0.97743 | -0.15804 | 0.72536
111 | -0.0085094 | -0.0021324 | 0.00851 | 0.0021326 | 5.1626e-07 | 1.3846e-07 | 0.013045 | 0.013045 | 0.013045 | 0.97068 | -0.20648 | 0.97074 | -0.20604 | 4.8313
112 | 0.0036278 | 0.00090894 | -0.0036273 | -0.00090907 | 4.1226e-07 | -1.209e-07 | 0.0054827 | 0.0054828 | 0.0054828 | 0.98456 | -0.10788 | 0.98444 | -0.1087 | 2.0307
113 | 0.0013516 | 0.00033872 | -0.0013516 | -0.00033875 | 6.6059e-09 | -2.9706e-08 | 0.002043 | 0.002043 | 0.002043 | 0.98444 | -0.1087 | 0.98443 | -0.10873 | 0.75668
114 | 0.0056315 | 0.0014112 | -0.0056303 | -0.0014111 | 1.2388e-06 | 1.3681e-07 | 0.0085657 | 0.0085658 | 0.0085658 | 0.97829 | -0.1525 | 0.97807 | -0.15409 | 3.1725
115 | 0.0010542 | 0.000264 | -0.0010542 | -0.0002642 | 2.5277e-08 | -1.9316e-07 | 0.0015933 | 0.0015934 | 0.0015934 | 0.98448 | -0.10811 | 0.98446 | -0.10829 | 0.59013

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.23147 | 0.058321

## res_load
| p_mw | q_mvar
0 | 0.0016951 | 0.00042484
1 | 0.0011448 | 0.00028691
2 | 0.0017065 | 0.00042768
3 | 0.0015266 | 0.0003826
4 | 0.0060365 | 0.0015129
5 | 0.0022604 | 0.00056651
6 | 0.0013522 | 0.00033888
7 | 0.0018898 | 0.00047363
8 | 0.0038111 | 0.00095515
9 | 0.0025328 | 0.00063477
10 | 0.0026781 | 0.0006712
11 | 0.0024235 | 0.00060739
12 | 0.0024093 | 0.00060383
13 | 0.0020606 | 0.00051643
14 | 0.0021529 | 0.00053956
15 | 0.0012891 | 0.00032308
16 | 0.0020544 | 0.00051488
17 | 0.0010828 | 0.00027138
18 | 0.00079964 | 0.00020041
19 | 0.0012231 | 0.00030655
20 | 0.0016458 | 0.00041249
21 | 0.0021968 | 0.00055057
22 | 0.0012175 | 0.00030514
23 | 0.0043694 | 0.0010951
24 | 0.0063751 | 0.0015978
25 | 0.0030868 | 0.00077362
26 | 0.0030949 | 0.00077566
27 | 0.0017749 | 0.00044483
28 | 0.0030011 | 0.00075215
29 | 0.0026889 | 0.0006739
30 | 0.0021147 | 0.00052999
31 | 0.0037407 | 0.00093751
32 | 0.0022173 | 0.0005557
33 | 0.0031012 | 0.00077722
34 | 0.0026763 | 0.00067074
35 | 0.0030171 | 0.00075616
36 | 0.0041704 | 0.0010452
37 | 0.012936 | 0.0032421
38 | 0.0023735 | 0.00059487
39 | 0.0038193 | 0.00095722
40 | 0.003086 | 0.00077342
41 | 0.0021583 | 0.00054093
42 | 0.0023714 | 0.00059433
43 | 0.00098831 | 0.00024769
44 | 0.002876 | 0.00072078
45 | 0.0036354 | 0.00091113
46 | 0.0015815 | 0.00039637
47 | 0.0019066 | 0.00047785
48 | 0.0012944 | 0.00032441
49 | 0.002579 | 0.00064637
50 | 0.0020121 | 0.00050428
51 | 0.0013727 | 0.00034404
52 | 0.0013934 | 0.00034922
53 | 0.0016075 | 0.00040287
54 | 0.0014086 | 0.00035303
55 | 0.0017643 | 0.00044217
56 | 0.00093679 | 0.00023478
57 | 0.0014665 | 0.00036754
58 | 0.00094882 | 0.0002378
59 | 0.0013391 | 0.00033562
60 | 0.0025115 | 0.00062943
61 | 0.0012063 | 0.00030232
62 | 0.0018262 | 0.0004577
63 | 0.0017108 | 0.00042878
64 | 0.0026556 | 0.00066555
65 | 0.0018932 | 0.00047449
66 | 0.0020862 | 0.00052284
67 | 0.0018252 | 0.00045744
68 | 0.0015216 | 0.00038136
69 | 0.0020418 | 0.00051173
70 | 0.00095932 | 0.00024043
71 | 0.0013049 | 0.00032703
72 | 0.0019806 | 0.00049639
73 | 0.001063 | 0.00026641
74 | 0.0018528 | 0.00046435
75 | 0.0022749 | 0.00057016
76 | 0.0021313 | 0.00053416
77 | 0.0020021 | 0.00050178
78 | 0.0019351 | 0.00048499
79 | 0.0021236 | 0.00053222
80 | 0.00099497 | 0.00024936
81 | 0.001202 | 0.00030126
82 | 0.00451 | 0.0011303
83 | 0.0016095 | 0.00040337
84 | 0.0021081 | 0.00052833
85 | 0.0014118 | 0.00035384
86 | 0.0027025 | 0.00067732
87 | 0.0015854 | 0.00039734
88 | 0.0012065 | 0.00030237
89 | 0.0022697 | 0.00056884
90 | 0.0023157 | 0.00058037
91 | 0.0023485 | 0.00058858
92 | 0.0014932 | 0.00037424
93 | 0.0022757 | 0.00057035
94 | 0.0013516 | 0.00033875
95 | 0.0026416 | 0.00066206
96 | 0.0056303 | 0.0014111
97 | 0.0012038 | 0.0003017
98 | 0.0010542 | 0.0002642
99 | 0.0012865 | 0.00032242

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1