## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2408-9_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2408-9_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2408-9_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2408-9_0_3_node_28 | 0.4 | n |  | TRUE
4 | bus_LV_2408-9_0_3_node_26 | 0.4 | n |  | TRUE
5 | bus_LV_2408-9_0_3_node_27 | 0.4 | n |  | TRUE
6 | bus_LV_2408-9_0_3_node_3 | 0.4 | n |  | TRUE
7 | bus_LV_2408-9_0_3_node_4 | 0.4 | n |  | TRUE
8 | bus_LV_2408-9_0_3_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_2408-9_0_3_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_2408-9_0_3_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_2408-9_0_3_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_2408-9_0_3_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_2408-9_0_3_node_15 | 0.4 | n |  | TRUE
14 | bus_LV_2408-9_0_3_node_19 | 0.4 | n |  | TRUE
15 | bus_LV_2408-9_0_3_node_16 | 0.4 | n |  | TRUE
16 | bus_LV_2408-9_0_3_node_18 | 0.4 | n |  | TRUE
17 | bus_LV_2408-9_0_3_node_20 | 0.4 | n |  | TRUE
18 | bus_LV_2408-9_0_3_node_21 | 0.4 | n |  | TRUE
19 | bus_LV_2408-9_0_3_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_2408-9_0_3_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_2408-9_0_3_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_2408-9_0_3_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_2408-9_0_3_node_22 | 0.4 | n |  | TRUE
24 | bus_LV_2408-9_0_3_node_23 | 0.4 | n |  | TRUE
25 | bus_LV_2408-9_0_3_node_24 | 0.4 | n |  | TRUE
26 | bus_LV_2408-9_0_3_node_17 | 0.4 | n |  | TRUE
27 | bus_LV_2408-9_0_3_node_29 | 0.4 | n |  | TRUE
28 | bus_LV_2408-9_0_3_node_39 | 0.4 | n |  | TRUE
29 | bus_LV_2408-9_0_3_node_38 | 0.4 | n |  | TRUE
30 | bus_LV_2408-9_0_3_node_40 | 0.4 | n |  | TRUE
31 | bus_LV_2408-9_0_3_node_30 | 0.4 | n |  | TRUE
32 | bus_LV_2408-9_0_3_node_25 | 0.4 | n |  | TRUE
33 | bus_LV_2408-9_0_3_node_32 | 0.4 | n |  | TRUE
34 | bus_LV_2408-9_0_3_node_31 | 0.4 | n |  | TRUE
35 | bus_LV_2408-9_0_3_node_33 | 0.4 | n |  | TRUE
36 | bus_LV_2408-9_0_3_node_34 | 0.4 | n |  | TRUE
37 | bus_LV_2408-9_0_3_node_35 | 0.4 | n |  | TRUE
38 | bus_LV_2408-9_0_3_node_36 | 0.4 | n |  | TRUE
39 | bus_LV_2408-9_0_3_node_37 | 0.4 | n |  | TRUE
40 | bus_LV_2408-9_0_3_node_41 | 0.4 | n |  | TRUE
41 | bus_MV_334_0_node_260 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2408-9_0_3_load_0 | 0 | 0.0072656 | 0.0018209 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2408-9_0_3_load_1 | 1 | 0.0023792 | 0.00059628 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2408-9_0_3_load_28 | 3 | 0.025663 | 0.0064317 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2408-9_0_3_load_26 | 4 | 0.0070672 | 0.0017712 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2408-9_0_3_load_3 | 6 | 0.0013247 | 0.00033201 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2408-9_0_3_load_9 | 12 | 0.00065896 | 0.00016515 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2408-9_0_3_load_15 | 13 | 0.0034088 | 0.00085432 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2408-9_0_3_load_19 | 14 | 0.00070176 | 0.00017588 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2408-9_0_3_load_16 | 15 | 0.00084469 | 0.0002117 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2408-9_0_3_load_18 | 16 | 0.0012713 | 0.00031862 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2408-9_0_3_load_10 | 19 | 0.0024962 | 0.00062559 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2408-9_0_3_load_11 | 20 | 0.010623 | 0.0026623 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2408-9_0_3_load_12 | 21 | 0.0027614 | 0.00069207 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2408-9_0_3_load_13 | 22 | 0.0024055 | 0.00060288 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2408-9_0_3_load_22 | 23 | 0.0052001 | 0.0013033 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2408-9_0_3_load_23 | 24 | 0.0010508 | 0.00026336 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2408-9_0_3_load_24 | 25 | 0.0032564 | 0.00081612 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2408-9_0_3_load_29 | 27 | 0.0005609 | 0.00014058 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2408-9_0_3_load_39 | 28 | 0.0088889 | 0.0022278 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2408-9_0_3_load_38 | 29 | 0.0012093 | 0.00030308 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2408-9_0_3_load_30 | 31 | 0.00068871 | 0.00017261 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2408-9_0_3_load_32 | 33 | 0.0094321 | 0.0023639 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2408-9_0_3_load_31 | 34 | 0.0038015 | 0.00095274 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2408-9_0_3_load_34 | 36 | 0.00086107 | 0.0002158 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2408-9_0_3_load_35 | 37 | 0.0021969 | 0.0005506 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2408-9_0_3_load_41 | 40 | 0.0012768 | 0.00032 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 18 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2408-9_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0061452 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2408-9_0_3_line_1 | NAYY 4x150 SE | 1 | 2 | 0.056099 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2408-9_0_3_line_2 | NAYY 4x150 SE | 2 | 3 | 0.02011 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2408-9_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.015913 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2408-9_0_3_line_4 | NAYY 4x150 SE | 4 | 5 | 0.03127 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2408-9_0_3_line_5 | NAYY 4x150 SE | 5 | 10 | 0.097659 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2408-9_0_3_line_6 | NAYY 4x150 SE | 6 | 7 | 0.047716 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2408-9_0_3_line_7 | NAYY 4x150 SE | 6 | 8 | 0.013803 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2408-9_0_3_line_8 | NAYY 4x150 SE | 7 | 9 | 0.009191 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2408-9_0_3_line_9 | NAYY 4x150 SE | 7 | 10 | 0.019097 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2408-9_0_3_line_10 | NAYY 4x150 SE | 8 | 11 | 0.004491 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2408-9_0_3_line_11 | NAYY 4x150 SE | 8 | 12 | 0.023934 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2408-9_0_3_line_12 | NAYY 4x150 SE | 9 | 13 | 0.015098 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2408-9_0_3_line_13 | NAYY 4x150 SE | 11 | 14 | 0.0015529 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2408-9_0_3_line_14 | NAYY 4x150 SE | 13 | 15 | 0.031171 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2408-9_0_3_line_15 | NAYY 4x150 SE | 14 | 16 | 0.030203 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2408-9_0_3_line_16 | NAYY 4x150 SE | 15 | 26 | 0.050811 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2408-9_0_3_line_17 | NAYY 4x150 SE | 16 | 17 | 0.0012503 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2408-9_0_3_line_18 | NAYY 4x150 SE | 17 | 18 | 0.025773 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2408-9_0_3_line_19 | NAYY 4x150 SE | 18 | 28 | 0.048972 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2408-9_0_3_line_20 | NAYY 4x150 SE | 18 | 29 | 0.04819 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2408-9_0_3_line_21 | NAYY 4x150 SE | 19 | 20 | 0.012732 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2408-9_0_3_line_22 | NAYY 4x150 SE | 19 | 21 | 0.018909 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2408-9_0_3_line_23 | NAYY 4x150 SE | 20 | 22 | 0.0065282 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2408-9_0_3_line_24 | NAYY 4x150 SE | 22 | 23 | 0.013067 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2408-9_0_3_line_25 | NAYY 4x150 SE | 23 | 24 | 0.04868 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2408-9_0_3_line_26 | NAYY 4x150 SE | 23 | 25 | 0.03945 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2408-9_0_3_line_27 | NAYY 4x150 SE | 24 | 32 | 0.015451 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2408-9_0_3_line_28 | NAYY 4x150 SE | 26 | 27 | 0.049748 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2408-9_0_3_line_29 | NAYY 4x150 SE | 28 | 30 | 0.050263 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2408-9_0_3_line_30 | NAYY 4x150 SE | 29 | 31 | 0.0054708 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2408-9_0_3_line_31 | NAYY 4x150 SE | 30 | 40 | 0.012837 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2408-9_0_3_line_32 | NAYY 4x150 SE | 31 | 33 | 0.030353 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2408-9_0_3_line_33 | NAYY 4x150 SE | 31 | 32 | 0.046478 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2408-9_0_3_line_34 | NAYY 4x150 SE | 33 | 34 | 0.033177 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2408-9_0_3_line_35 | NAYY 4x150 SE | 34 | 35 | 0.17331 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2408-9_0_3_line_36 | NAYY 4x150 SE | 35 | 36 | 0.014534 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2408-9_0_3_line_37 | NAYY 4x150 SE | 37 | 38 | 0.080073 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2408-9_0_3_line_38 | NAYY 4x150 SE | 38 | 39 | 0.064905 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_2408-9_0_3_line_39 | NAYY 4x150 SE | 39 | 40 | 0.090227 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2408-9_0_3_trafo_21 | 0.25 MVA 20/0.4 kV | 41 | 18 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2627251.5386 | 1235595.9879 | 2627252.8525 | 1235589.9848
1 | 2627256.1429 | 1235534.5258 | 2627258.1477 | 1235551.1675 | 2627256.4112 | 1235565.1682 | 2627256.6339 | 1235572.7073 | 2627252.8525 | 1235589.9848
2 | 2627239.1273 | 1235545.3213 | 2627256.1429 | 1235534.5258
3 | 2627256.1429 | 1235534.5258 | 2627263.6565 | 1235529.7573 | 2627268.3623 | 1235524.5563
4 | 2627289.342 | 1235501.3686 | 2627268.3623 | 1235524.5563
5 | 2627289.342 | 1235501.3686 | 2627275.6971 | 1235496.5809 | 2627250.8561 | 1235489.307 | 2627195.9115 | 1235472.1007
6 | 2627177.0999 | 1235468.5236 | 2627176.8376 | 1235476.2494 | 2627165.8834 | 1235514.7058
7 | 2627162.102 | 1235527.9808 | 2627165.8834 | 1235514.7058
8 | 2627177.0999 | 1235468.5236 | 2627167.8833 | 1235468.3815
9 | 2627177.0999 | 1235468.5236 | 2627189.0015 | 1235470.6349 | 2627195.9115 | 1235472.1007
10 | 2627162.102 | 1235527.9808 | 2627160.8715 | 1235532.3001
11 | 2627162.102 | 1235527.9808 | 2627172.7518 | 1235530.7645 | 2627176.1168 | 1235529.6681 | 2627180.4815 | 1235525.074 | 2627181.2864 | 1235522.1316
12 | 2627167.8833 | 1235468.3815 | 2627152.7925 | 1235468.8317
13 | 2627160.8715 | 1235532.3001 | 2627160.4464 | 1235533.7937
14 | 2627121.6459 | 1235468.3595 | 2627140.4095 | 1235469.2011 | 2627152.7925 | 1235468.8317
15 | 2627152.1772 | 1235562.8426 | 2627160.4464 | 1235533.7937
16 | 2627071.6264 | 1235459.6487 | 2627096.5976 | 1235464.9989 | 2627121.6459 | 1235468.3595 | 2627121.6459 | 1235468.3595
17 | 2627151.8349 | 1235564.0452 | 2627152.1772 | 1235562.8426
18 | 2627139.4994 | 1235585.7579 | 2627145.789 | 1235580.5389 | 2627149.3355 | 1235572.8059 | 2627151.8349 | 1235564.0452
19 | 2627139.4994 | 1235585.7579 | 2627154.5373 | 1235595.3546 | 2627153.802 | 1235600.6101 | 2627178.4758 | 1235608.2399
20 | 2627139.4994 | 1235585.7579 | 2627131.4394 | 1235589.2233 | 2627121.4538 | 1235588.4996 | 2627093.1618 | 1235580.4872
21 | 2626992.9738 | 1235627.2005 | 2627005.2383 | 1235630.6174
22 | 2626974.7586 | 1235622.1257 | 2626992.9738 | 1235627.2005
23 | 2627011.527 | 1235632.3695 | 2627005.2383 | 1235630.6174
24 | 2627023.4837 | 1235627.0993 | 2627011.527 | 1235632.3695
25 | 2627038.395 | 1235580.7595 | 2627023.4837 | 1235627.0993
26 | 2627045.8933 | 1235647.8935 | 2627019.8933 | 1235638.2573 | 2627023.4837 | 1235627.0993
27 | 2627043.1277 | 1235566.0515 | 2627038.395 | 1235580.7595
28 | 2627071.6264 | 1235459.6487 | 2627059.1003 | 1235507.7941
29 | 2627226.4685 | 1235621.0547 | 2627207.2182 | 1235614.218 | 2627200.6231 | 1235615.0884 | 2627178.4758 | 1235608.2399
30 | 2627087.898 | 1235578.9964 | 2627093.1618 | 1235580.4872
31 | 2627226.4685 | 1235621.0547 | 2627238.6682 | 1235625.0489
32 | 2627087.898 | 1235578.9964 | 2627078.406 | 1235607.8275
33 | 2627087.898 | 1235578.9964 | 2627043.1277 | 1235566.0515
34 | 2627068.0308 | 1235639.341 | 2627078.406 | 1235607.8275
35 | 2627068.0308 | 1235639.341 | 2627160.5309 | 1235785.8998
36 | 2627160.5309 | 1235785.8998 | 2627150.8 | 1235796.6957
37 | 2627348.5451 | 1235592.9414 | 2627271.1985 | 1235572.2262
38 | 2627324.4164 | 1235653.1233 | 2627340.7327 | 1235614.9746 | 2627346.3054 | 1235601.1361 | 2627348.5451 | 1235592.9414
39 | 2627324.4164 | 1235653.1233 | 2627238.6682 | 1235625.0489

## bus_geodata
| x | y | coords
0 | 2627251.5386 | 1235595.9879
1 | 2627252.8525 | 1235589.9848
2 | 2627256.1429 | 1235534.5258
3 | 2627239.1273 | 1235545.3213
4 | 2627268.3623 | 1235524.5563
5 | 2627289.342 | 1235501.3686
6 | 2627165.8834 | 1235514.7058
7 | 2627177.0999 | 1235468.5236
8 | 2627162.102 | 1235527.9808
9 | 2627167.8833 | 1235468.3815
10 | 2627195.9115 | 1235472.1007
11 | 2627160.8715 | 1235532.3001
12 | 2627181.2864 | 1235522.1316
13 | 2627152.7925 | 1235468.8317
14 | 2627160.4464 | 1235533.7937
15 | 2627121.6459 | 1235468.3595
16 | 2627152.1772 | 1235562.8426
17 | 2627151.8349 | 1235564.0452
18 | 2627139.4994 | 1235585.7579
19 | 2626992.9738 | 1235627.2005
20 | 2627005.2383 | 1235630.6174
21 | 2626974.7586 | 1235622.1257
22 | 2627011.527 | 1235632.3695
23 | 2627023.4837 | 1235627.0993
24 | 2627038.395 | 1235580.7595
25 | 2627045.8933 | 1235647.8935
26 | 2627071.6264 | 1235459.6487
27 | 2627059.1003 | 1235507.7941
28 | 2627178.4758 | 1235608.2399
29 | 2627093.1618 | 1235580.4872
30 | 2627226.4685 | 1235621.0547
31 | 2627087.898 | 1235578.9964
32 | 2627043.1277 | 1235566.0515
33 | 2627078.406 | 1235607.8275
34 | 2627068.0308 | 1235639.341
35 | 2627160.5309 | 1235785.8998
36 | 2627150.8 | 1235796.6957
37 | 2627271.1985 | 1235572.2262
38 | 2627348.5451 | 1235592.9414
39 | 2627324.4164 | 1235653.1233
40 | 2627238.6682 | 1235625.0489
41 | 2627151.8349 | 1235564.0452

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98035 | -0.1378 | 0.0072656 | 0.0018209
1 | 0.98042 | -0.13733 | 0.0023792 | 0.00059628
2 | 0.9812 | -0.13172 | 0 | 0
3 | 0.98045 | -0.13707 | 0.025663 | 0.0064317
4 | 0.98202 | -0.1259 | 0.0070672 | 0.0017712
5 | 0.98395 | -0.11221 | 0 | 0
6 | 0.99441 | -0.038732 | 0.0013247 | 0.00033201
7 | 0.99114 | -0.061552 | 0 | 0
8 | 0.99538 | -0.031973 | 0 | 0
9 | 0.99107 | -0.062003 | 0 | 0
10 | 0.98996 | -0.069788 | 0 | 0
11 | 0.9957 | -0.029747 | 0 | 0
12 | 0.99536 | -0.032133 | 0.00065896 | 0.00016515
13 | 0.99097 | -0.062744 | 0.0034088 | 0.00085432
14 | 0.99581 | -0.028978 | 0.00070176 | 0.00017588
15 | 0.99091 | -0.063193 | 0.00084469 | 0.0002117
16 | 0.998 | -0.013836 | 0.0012713 | 0.00031862
17 | 0.99809 | -0.013194 | 0 | 0
18 | 1 | 0 | -0.10925 | -0.027318
19 | 0.99171 | -0.058165 | 0.0024962 | 0.00062559
20 | 0.9918 | -0.057486 | 0.010623 | 0.0026623
21 | 0.99163 | -0.058695 | 0.0027614 | 0.00069207
22 | 0.99195 | -0.056434 | 0.0024055 | 0.00060288
23 | 0.99229 | -0.05401 | 0.0052001 | 0.0013033
24 | 0.99417 | -0.040835 | 0.0010508 | 0.00026336
25 | 0.99211 | -0.055313 | 0.0032564 | 0.00081612
26 | 0.99086 | -0.063486 | 0 | 0
27 | 0.99082 | -0.063771 | 0.0005609 | 0.00014058
28 | 0.99914 | -0.006063 | 0.0088889 | 0.0022278
29 | 0.99697 | -0.021145 | 0.0012093 | 0.00030308
30 | 0.99889 | -0.0078224 | 0 | 0
31 | 0.99664 | -0.023487 | 0.00068871 | 0.00017261
32 | 0.99478 | -0.036499 | 0 | 0
33 | 0.99603 | -0.027796 | 0.0094321 | 0.0023639
34 | 0.9958 | -0.029359 | 0.0038015 | 0.00095274
35 | 0.99559 | -0.030878 | 0 | 0
36 | 0.99557 | -0.031004 | 0.00086107 | 0.0002158
37 | 0.99809 | -0.013472 | 0.0021969 | 0.0005506
38 | 0.99834 | -0.011706 | 0 | 0
39 | 0.99854 | -0.010272 | 0 | 0
40 | 0.99882 | -0.0082715 | 0.0012768 | 0.00032
41 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0072656 | -0.0018209 | 0.0072661 | 0.001821 | 4.6635e-07 | 1.0188e-07 | 0.011028 | 0.011028 | 0.011028 | 0.98035 | -0.1378 | 0.98042 | -0.13733 | 4.0844
1 | -0.0096452 | -0.0024173 | 0.0096527 | 0.0024195 | 7.5015e-06 | 2.1772e-06 | 0.014639 | 0.014639 | 0.014639 | 0.98042 | -0.13733 | 0.9812 | -0.13172 | 5.4218
2 | 0.025682 | 0.0064388 | -0.025663 | -0.0064317 | 1.9036e-05 | 7.0676e-06 | 0.038948 | 0.038948 | 0.038948 | 0.9812 | -0.13172 | 0.98045 | -0.13707 | 14.4253
3 | -0.035335 | -0.0088583 | 0.035363 | 0.0088691 | 2.8514e-05 | 1.0766e-05 | 0.053587 | 0.053587 | 0.053587 | 0.9812 | -0.13172 | 0.98202 | -0.1259 | 19.847
4 | -0.04243 | -0.01064 | 0.042511 | 0.010671 | 8.0663e-05 | 3.0628e-05 | 0.064295 | 0.064295 | 0.064295 | 0.98202 | -0.1259 | 0.98395 | -0.11221 | 23.8131
5 | -0.042511 | -0.010671 | 0.042763 | 0.010767 | 0.00025191 | 9.5642e-05 | 0.064295 | 0.064295 | 0.064295 | 0.98395 | -0.11221 | 0.98996 | -0.069788 | 23.8131
6 | 0.04778 | 0.012048 | -0.047628 | -0.01199 | 0.00015232 | 5.7966e-05 | 0.071523 | 0.071523 | 0.071523 | 0.99441 | -0.038732 | 0.99114 | -0.061552 | 26.4901
7 | -0.049105 | -0.01238 | 0.049151 | 0.012398 | 4.6537e-05 | 1.772e-05 | 0.073505 | 0.073505 | 0.073505 | 0.99441 | -0.038732 | 0.99538 | -0.031973 | 27.2242
8 | 0.0048153 | 0.0012049 | -0.004815 | -0.0012049 | 2.9968e-07 | -3.1808e-09 | 0.0072286 | 0.0072287 | 0.0072287 | 0.99114 | -0.061552 | 0.99107 | -0.062003 | 2.6773
9 | 0.042812 | 0.010785 | -0.042763 | -0.010767 | 4.9261e-05 | 1.8701e-05 | 0.064295 | 0.064295 | 0.064295 | 0.99114 | -0.061552 | 0.98996 | -0.069788 | 23.8129
10 | -0.04981 | -0.012563 | 0.049826 | 0.012569 | 1.555e-05 | 5.9223e-06 | 0.07449 | 0.07449 | 0.07449 | 0.99538 | -0.031973 | 0.9957 | -0.029747 | 27.589
11 | 0.00065897 | 0.00016484 | -0.00065896 | -0.00016515 | 1.4492e-08 | -3.0552e-07 | 0.00098501 | 0.00098512 | 0.00098512 | 0.99538 | -0.031973 | 0.99536 | -0.032133 | 0.36486
12 | 0.004815 | 0.0012049 | -0.0048145 | -0.0012049 | 4.9228e-07 | -5.189e-09 | 0.0072287 | 0.0072288 | 0.0072288 | 0.99107 | -0.062003 | 0.99097 | -0.062744 | 2.6773
13 | -0.049826 | -0.012569 | 0.049831 | 0.012571 | 5.3769e-06 | 2.0478e-06 | 0.07449 | 0.07449 | 0.07449 | 0.9957 | -0.029747 | 0.99581 | -0.028978 | 27.589
14 | 0.0014057 | 0.00035063 | -0.0014056 | -0.000351 | 8.662e-08 | -3.6825e-07 | 0.0021102 | 0.0021104 | 0.0021104 | 0.99097 | -0.062744 | 0.99091 | -0.063193 | 0.78161
15 | -0.050533 | -0.012747 | 0.05064 | 0.012788 | 0.00010754 | 4.0968e-05 | 0.075539 | 0.075539 | 0.075539 | 0.99581 | -0.028978 | 0.998 | -0.013836 | 27.9774
16 | 0.00056095 | 0.0001393 | -0.00056093 | -0.00013994 | 2.2479e-08 | -6.4586e-07 | 0.00084191 | 0.00084214 | 0.00084214 | 0.99091 | -0.063193 | 0.99086 | -0.063486 | 0.3119
17 | -0.051912 | -0.013106 | 0.051916 | 0.013108 | 4.6781e-06 | 1.7829e-06 | 0.077434 | 0.077434 | 0.077434 | 0.998 | -0.013836 | 0.99809 | -0.013194 | 28.6794
18 | -0.051916 | -0.013108 | 0.052013 | 0.013145 | 9.6431e-05 | 3.6751e-05 | 0.077434 | 0.077434 | 0.077434 | 0.99809 | -0.013194 | 1 | 0 | 28.6794
19 | 0.012376 | 0.0030988 | -0.012365 | -0.0030955 | 1.0362e-05 | 3.3434e-06 | 0.018414 | 0.018414 | 0.018414 | 1 | 0 | 0.99914 | -0.006063 | 6.8201
20 | 0.044064 | 0.011074 | -0.043935 | -0.011025 | 0.00012932 | 4.9109e-05 | 0.065579 | 0.06558 | 0.06558 | 1 | 0 | 0.99697 | -0.021145 | 24.2888
21 | -0.0052577 | -0.0013175 | 0.0052582 | 0.0013175 | 4.9442e-07 | 2.5878e-08 | 0.0078889 | 0.0078889 | 0.0078889 | 0.99171 | -0.058165 | 0.9918 | -0.057486 | 2.9218
22 | 0.0027616 | 0.0006919 | -0.0027614 | -0.00069207 | 2.0259e-07 | -1.6604e-07 | 0.0041436 | 0.0041437 | 0.0041437 | 0.99171 | -0.058165 | 0.99163 | -0.058695 | 1.5347
23 | -0.015881 | -0.0039799 | 0.015883 | 0.0039807 | 2.3126e-06 | 8.0519e-07 | 0.023826 | 0.023826 | 0.023826 | 0.9918 | -0.057486 | 0.99195 | -0.056434 | 8.8246
24 | -0.018289 | -0.0045835 | 0.018295 | 0.0045857 | 6.137e-06 | 2.1917e-06 | 0.027435 | 0.027435 | 0.027435 | 0.99195 | -0.056434 | 0.99229 | -0.05401 | 10.1611
25 | -0.026752 | -0.0067048 | 0.026801 | 0.006723 | 4.8886e-05 | 1.8172e-05 | 0.040117 | 0.040116 | 0.040117 | 0.99229 | -0.05401 | 0.99417 | -0.040835 | 14.858
26 | 0.003257 | 0.00081584 | -0.0032564 | -0.00081612 | 5.8719e-07 | -2.8367e-07 | 0.0048839 | 0.0048841 | 0.0048841 | 0.99229 | -0.05401 | 0.99211 | -0.055313 | 1.8089
27 | -0.027852 | -0.0069864 | 0.027869 | 0.0069926 | 1.6756e-05 | 6.2443e-06 | 0.041689 | 0.041689 | 0.041689 | 0.99417 | -0.040835 | 0.99478 | -0.036499 | 15.4405
28 | 0.00056093 | 0.00013994 | -0.0005609 | -0.00014058 | 2.2021e-08 | -6.323e-07 | 0.00084214 | 0.00084236 | 0.00084236 | 0.99086 | -0.063486 | 0.99082 | -0.063771 | 0.31199
29 | 0.0034764 | 0.00086771 | -0.0034755 | -0.00086804 | 8.4034e-07 | -3.349e-07 | 0.0051761 | 0.0051763 | 0.0051763 | 0.99914 | -0.006063 | 0.99889 | -0.0078224 | 1.9172
30 | 0.042726 | 0.010722 | -0.042712 | -0.010717 | 1.3885e-05 | 5.2689e-06 | 0.063775 | 0.063775 | 0.063775 | 0.99697 | -0.021145 | 0.99664 | -0.023487 | 23.6203
31 | 0.0034755 | 0.00086804 | -0.0034753 | -0.00086813 | 2.1463e-07 | -8.5475e-08 | 0.0051763 | 0.0051764 | 0.0051764 | 0.99889 | -0.0078224 | 0.99882 | -0.0082715 | 1.9172
32 | 0.014104 | 0.0035329 | -0.014096 | -0.00353 | 8.3986e-06 | 2.8349e-06 | 0.021057 | 0.021058 | 0.021058 | 0.99664 | -0.023487 | 0.99603 | -0.027796 | 7.7991
33 | 0.027919 | 0.0070114 | -0.027869 | -0.0069926 | 5.0405e-05 | 1.8782e-05 | 0.041689 | 0.041689 | 0.041689 | 0.99664 | -0.023487 | 0.99478 | -0.036499 | 15.4405
34 | 0.0046637 | 0.0011661 | -0.0046627 | -0.0011662 | 1.0048e-06 | -4.5272e-08 | 0.0069665 | 0.0069666 | 0.0069666 | 0.99603 | -0.027796 | 0.9958 | -0.029359 | 2.5802
35 | 0.00086126 | 0.00021344 | -0.00086108 | -0.00021562 | 1.7899e-07 | -2.1853e-06 | 0.0012861 | 0.0012869 | 0.0012869 | 0.9958 | -0.029359 | 0.99559 | -0.030878 | 0.47663
36 | 0.00086108 | 0.00021562 | -0.00086107 | -0.0002158 | 1.5021e-08 | -1.8322e-07 | 0.0012869 | 0.001287 | 0.001287 | 0.99559 | -0.030878 | 0.99557 | -0.031004 | 0.47666
37 | -0.0021969 | -0.0005506 | 0.0021975 | 0.00054976 | 5.3596e-07 | -8.406e-07 | 0.0032753 | 0.003275 | 0.0032753 | 0.99809 | -0.013472 | 0.99834 | -0.011706 | 1.2131
38 | -0.0021975 | -0.00054976 | 0.0021979 | 0.00054908 | 4.3435e-07 | -6.818e-07 | 0.003275 | 0.0032747 | 0.003275 | 0.99834 | -0.011706 | 0.99854 | -0.010272 | 1.2129
39 | -0.0021979 | -0.00054908 | 0.0021985 | 0.00054813 | 6.0367e-07 | -9.4842e-07 | 0.0032747 | 0.0032742 | 0.0032747 | 0.99854 | -0.010272 | 0.99882 | -0.0082715 | 1.2128

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.10925 | 0.027318

## res_load
| p_mw | q_mvar
0 | 0.0072656 | 0.0018209
1 | 0.0023792 | 0.00059628
2 | 0.025663 | 0.0064317
3 | 0.0070672 | 0.0017712
4 | 0.0013247 | 0.00033201
5 | 0.00065896 | 0.00016515
6 | 0.0034088 | 0.00085432
7 | 0.00070176 | 0.00017588
8 | 0.00084469 | 0.0002117
9 | 0.0012713 | 0.00031862
10 | 0.0024962 | 0.00062559
11 | 0.010623 | 0.0026623
12 | 0.0027614 | 0.00069207
13 | 0.0024055 | 0.00060288
14 | 0.0052001 | 0.0013033
15 | 0.0010508 | 0.00026336
16 | 0.0032564 | 0.00081612
17 | 0.0005609 | 0.00014058
18 | 0.0088889 | 0.0022278
19 | 0.0012093 | 0.00030308
20 | 0.00068871 | 0.00017261
21 | 0.0094321 | 0.0023639
22 | 0.0038015 | 0.00095274
23 | 0.00086107 | 0.0002158
24 | 0.0021969 | 0.0005506
25 | 0.0012768 | 0.00032

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1