## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2575-10_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2575-10_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2575-10_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2575-10_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2575-10_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2575-10_0_3_node_38 | 0.4 | n |  | TRUE
6 | bus_LV_2575-10_0_3_node_60 | 0.4 | n |  | TRUE
7 | bus_LV_2575-10_0_3_node_39 | 0.4 | n |  | TRUE
8 | bus_LV_2575-10_0_3_node_59 | 0.4 | n |  | TRUE
9 | bus_LV_2575-10_0_3_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_2575-10_0_3_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_2575-10_0_3_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_2575-10_0_3_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_2575-10_0_3_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_2575-10_0_3_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_2575-10_0_3_node_81 | 0.4 | n |  | TRUE
16 | bus_LV_2575-10_0_3_node_49 | 0.4 | n |  | TRUE
17 | bus_LV_2575-10_0_3_node_53 | 0.4 | n |  | TRUE
18 | bus_LV_2575-10_0_3_node_47 | 0.4 | n |  | TRUE
19 | bus_LV_2575-10_0_3_node_73 | 0.4 | n |  | TRUE
20 | bus_LV_2575-10_0_3_node_52 | 0.4 | n |  | TRUE
21 | bus_LV_2575-10_0_3_node_11 | 0.4 | n |  | TRUE
22 | bus_LV_2575-10_0_3_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_2575-10_0_3_node_13 | 0.4 | n |  | TRUE
24 | bus_LV_2575-10_0_3_node_14 | 0.4 | n |  | TRUE
25 | bus_LV_2575-10_0_3_node_15 | 0.4 | n |  | TRUE
26 | bus_LV_2575-10_0_3_node_65 | 0.4 | n |  | TRUE
27 | bus_LV_2575-10_0_3_node_69 | 0.4 | n |  | TRUE
28 | bus_LV_2575-10_0_3_node_50 | 0.4 | n |  | TRUE
29 | bus_LV_2575-10_0_3_node_63 | 0.4 | n |  | TRUE
30 | bus_LV_2575-10_0_3_node_70 | 0.4 | n |  | TRUE
31 | bus_LV_2575-10_0_3_node_16 | 0.4 | n |  | TRUE
32 | bus_LV_2575-10_0_3_node_17 | 0.4 | n |  | TRUE
33 | bus_LV_2575-10_0_3_node_18 | 0.4 | n |  | TRUE
34 | bus_LV_2575-10_0_3_node_87 | 0.4 | n |  | TRUE
35 | bus_LV_2575-10_0_3_node_85 | 0.4 | n |  | TRUE
36 | bus_LV_2575-10_0_3_node_83 | 0.4 | n |  | TRUE
37 | bus_LV_2575-10_0_3_node_19 | 0.4 | n |  | TRUE
38 | bus_LV_2575-10_0_3_node_20 | 0.4 | n |  | TRUE
39 | bus_LV_2575-10_0_3_node_21 | 0.4 | n |  | TRUE
40 | bus_LV_2575-10_0_3_node_22 | 0.4 | n |  | TRUE
41 | bus_LV_2575-10_0_3_node_23 | 0.4 | n |  | TRUE
42 | bus_LV_2575-10_0_3_node_24 | 0.4 | n |  | TRUE
43 | bus_LV_2575-10_0_3_node_72 | 0.4 | n |  | TRUE
44 | bus_LV_2575-10_0_3_node_88 | 0.4 | n |  | TRUE
45 | bus_LV_2575-10_0_3_node_67 | 0.4 | n |  | TRUE
46 | bus_LV_2575-10_0_3_node_57 | 0.4 | n |  | TRUE
47 | bus_LV_2575-10_0_3_node_68 | 0.4 | n |  | TRUE
48 | bus_LV_2575-10_0_3_node_25 | 0.4 | n |  | TRUE
49 | bus_LV_2575-10_0_3_node_26 | 0.4 | n |  | TRUE
50 | bus_LV_2575-10_0_3_node_27 | 0.4 | n |  | TRUE
51 | bus_LV_2575-10_0_3_node_28 | 0.4 | n |  | TRUE
52 | bus_LV_2575-10_0_3_node_29 | 0.4 | n |  | TRUE
53 | bus_LV_2575-10_0_3_node_36 | 0.4 | n |  | TRUE
54 | bus_LV_2575-10_0_3_node_45 | 0.4 | n |  | TRUE
55 | bus_LV_2575-10_0_3_node_37 | 0.4 | n |  | TRUE
56 | bus_LV_2575-10_0_3_node_71 | 0.4 | n |  | TRUE
57 | bus_LV_2575-10_0_3_node_30 | 0.4 | n |  | TRUE
58 | bus_LV_2575-10_0_3_node_31 | 0.4 | n |  | TRUE
59 | bus_LV_2575-10_0_3_node_32 | 0.4 | n |  | TRUE
60 | bus_LV_2575-10_0_3_node_33 | 0.4 | n |  | TRUE
61 | bus_LV_2575-10_0_3_node_34 | 0.4 | n |  | TRUE
62 | bus_LV_2575-10_0_3_node_35 | 0.4 | n |  | TRUE
63 | bus_LV_2575-10_0_3_node_58 | 0.4 | n |  | TRUE
64 | bus_LV_2575-10_0_3_node_78 | 0.4 | n |  | TRUE
65 | bus_LV_2575-10_0_3_node_56 | 0.4 | n |  | TRUE
66 | bus_LV_2575-10_0_3_node_76 | 0.4 | n |  | TRUE
67 | bus_LV_2575-10_0_3_node_40 | 0.4 | n |  | TRUE
68 | bus_LV_2575-10_0_3_node_41 | 0.4 | n |  | TRUE
69 | bus_LV_2575-10_0_3_node_42 | 0.4 | n |  | TRUE
70 | bus_LV_2575-10_0_3_node_43 | 0.4 | n |  | TRUE
71 | bus_LV_2575-10_0_3_node_44 | 0.4 | n |  | TRUE
72 | bus_LV_2575-10_0_3_node_77 | 0.4 | n |  | TRUE
73 | bus_LV_2575-10_0_3_node_79 | 0.4 | n |  | TRUE
74 | bus_LV_2575-10_0_3_node_46 | 0.4 | n |  | TRUE
75 | bus_LV_2575-10_0_3_node_48 | 0.4 | n |  | TRUE
76 | bus_LV_2575-10_0_3_node_51 | 0.4 | n |  | TRUE
77 | bus_LV_2575-10_0_3_node_74 | 0.4 | n |  | TRUE
78 | bus_LV_2575-10_0_3_node_54 | 0.4 | n |  | TRUE
79 | bus_LV_2575-10_0_3_node_55 | 0.4 | n |  | TRUE
80 | bus_LV_2575-10_0_3_node_61 | 0.4 | n |  | TRUE
81 | bus_LV_2575-10_0_3_node_64 | 0.4 | n |  | TRUE
82 | bus_LV_2575-10_0_3_node_66 | 0.4 | n |  | TRUE
83 | bus_LV_2575-10_0_3_node_80 | 0.4 | n |  | TRUE
84 | bus_LV_2575-10_0_3_node_75 | 0.4 | n |  | TRUE
85 | bus_LV_2575-10_0_3_node_86 | 0.4 | n |  | TRUE
86 | bus_LV_2575-10_0_3_node_84 | 0.4 | n |  | TRUE
87 | bus_LV_2575-10_0_3_node_82 | 0.4 | n |  | TRUE
88 | bus_MV_397_0_node_16 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2575-10_0_3_load_0 | 0 | 0.0040821 | 0.0010231 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2575-10_0_3_load_1 | 1 | 0.0054995 | 0.0013783 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2575-10_0_3_load_2 | 2 | 0.0029685 | 0.00074397 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2575-10_0_3_load_3 | 3 | 0.0059023 | 0.0014792 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2575-10_0_3_load_4 | 4 | 0.0012316 | 0.00030867 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2575-10_0_3_load_38 | 5 | 0.0047783 | 0.0011975 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2575-10_0_3_load_60 | 6 | 0.0034628 | 0.00086785 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2575-10_0_3_load_59 | 8 | 0.0027338 | 0.00068516 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2575-10_0_3_load_5 | 9 | 0.0088235 | 0.0022114 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2575-10_0_3_load_6 | 10 | 0.0070195 | 0.0017593 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2575-10_0_3_load_8 | 12 | 0.0011552 | 0.00028952 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2575-10_0_3_load_9 | 13 | 0.00098324 | 0.00024642 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2575-10_0_3_load_81 | 15 | 0.003164 | 0.00079296 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2575-10_0_3_load_49 | 16 | 0.014196 | 0.0035579 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2575-10_0_3_load_47 | 18 | 0.0062648 | 0.0015701 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2575-10_0_3_load_73 | 19 | 0.0028694 | 0.00071914 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2575-10_0_3_load_52 | 20 | 0.0054262 | 0.0013599 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2575-10_0_3_load_11 | 21 | 0.0019008 | 0.00047638 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2575-10_0_3_load_12 | 22 | 0.0047582 | 0.0011925 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2575-10_0_3_load_13 | 23 | 0.0056665 | 0.0014202 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2575-10_0_3_load_14 | 24 | 0.0035048 | 0.00087839 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2575-10_0_3_load_15 | 25 | 0.0061023 | 0.0015294 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2575-10_0_3_load_69 | 27 | 0.0071373 | 0.0017888 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2575-10_0_3_load_50 | 28 | 0.0014456 | 0.00036229 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2575-10_0_3_load_63 | 29 | 0.0022316 | 0.0005593 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2575-10_0_3_load_70 | 30 | 0.0032234 | 0.00080787 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2575-10_0_3_load_18 | 33 | 0.0035046 | 0.00087833 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2575-10_0_3_load_87 | 34 | 0.0017162 | 0.00043012 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2575-10_0_3_load_19 | 37 | 0.0057359 | 0.0014376 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2575-10_0_3_load_20 | 38 | 0.0013061 | 0.00032733 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2575-10_0_3_load_23 | 41 | 0.00092193 | 0.00023106 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2575-10_0_3_load_24 | 42 | 0.0012844 | 0.0003219 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2575-10_0_3_load_88 | 44 | 0.0013864 | 0.00034747 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2575-10_0_3_load_67 | 45 | 0.0012539 | 0.00031425 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2575-10_0_3_load_57 | 46 | 0.0030595 | 0.00076678 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2575-10_0_3_load_68 | 47 | 0.001288 | 0.0003228 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2575-10_0_3_load_25 | 48 | 0.0012002 | 0.00030081 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2575-10_0_3_load_26 | 49 | 0.0017327 | 0.00043425 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2575-10_0_3_load_27 | 50 | 0.0012722 | 0.00031885 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2575-10_0_3_load_28 | 51 | 0.0017561 | 0.00044011 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2575-10_0_3_load_29 | 52 | 0.0024874 | 0.00062339 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2575-10_0_3_load_36 | 53 | 0.0047545 | 0.0011916 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2575-10_0_3_load_45 | 54 | 0.00096974 | 0.00024304 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2575-10_0_3_load_37 | 55 | 0.003908 | 0.00097943 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2575-10_0_3_load_71 | 56 | 0.0017351 | 0.00043486 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2575-10_0_3_load_30 | 57 | 0.0019745 | 0.00049486 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2575-10_0_3_load_31 | 58 | 0.0011881 | 0.00029776 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2575-10_0_3_load_33 | 60 | 0.0016909 | 0.00042378 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2575-10_0_3_load_34 | 61 | 0.0037569 | 0.00094157 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2575-10_0_3_load_35 | 62 | 0.0018181 | 0.00045566 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2575-10_0_3_load_58 | 63 | 0.0025187 | 0.00063124 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2575-10_0_3_load_78 | 64 | 0.0017479 | 0.00043807 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2575-10_0_3_load_56 | 65 | 0.0015989 | 0.00040073 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2575-10_0_3_load_76 | 66 | 0.012377 | 0.0031018 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2575-10_0_3_load_40 | 67 | 0.011028 | 0.0027639 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2575-10_0_3_load_41 | 68 | 0.00035034 | 8.7802e-05 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2575-10_0_3_load_42 | 69 | 0.0026484 | 0.00066374 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2575-10_0_3_load_44 | 71 | 0.0020291 | 0.00050854 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2575-10_0_3_load_77 | 72 | 0.00225 | 0.0005639 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2575-10_0_3_load_79 | 73 | 0.00057523 | 0.00014417 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2575-10_0_3_load_46 | 74 | 0.0033881 | 0.00084913 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2575-10_0_3_load_48 | 75 | 0.0040887 | 0.0010247 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2575-10_0_3_load_51 | 76 | 0.0011634 | 0.00029158 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2575-10_0_3_load_74 | 77 | 0.00069327 | 0.00017375 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2575-10_0_3_load_54 | 78 | 0.0016608 | 0.00041624 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2575-10_0_3_load_55 | 79 | 0.0028841 | 0.00072283 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2575-10_0_3_load_61 | 80 | 0.0020084 | 0.00050335 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2575-10_0_3_load_64 | 81 | 0.0050403 | 0.0012632 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2575-10_0_3_load_66 | 82 | 0.007083 | 0.0017752 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2575-10_0_3_load_80 | 83 | 0.00070864 | 0.0001776 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2575-10_0_3_load_86 | 85 | 0.001304 | 0.00032681 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2575-10_0_3_load_84 | 86 | 0.0029656 | 0.00074324 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2575-10_0_3_load_82 | 87 | 0.00066846 | 0.00016753 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 24 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2575-10_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.021916 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2575-10_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.0028638 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2575-10_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.0039734 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2575-10_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.010146 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2575-10_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.017357 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2575-10_0_3_line_5 | NAYY 4x150 SE | 4 | 6 | 0.017282 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2575-10_0_3_line_6 | NAYY 4x150 SE | 5 | 7 | 0.014733 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2575-10_0_3_line_7 | NAYY 4x150 SE | 6 | 8 | 0.00010612 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2575-10_0_3_line_8 | NAYY 4x150 SE | 7 | 15 | 0.032402 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2575-10_0_3_line_9 | NAYY 4x150 SE | 7 | 55 | 0.038719 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2575-10_0_3_line_10 | NAYY 4x150 SE | 8 | 80 | 0.017005 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2575-10_0_3_line_11 | NAYY 4x150 SE | 9 | 10 | 0.0091399 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2575-10_0_3_line_12 | NAYY 4x150 SE | 9 | 11 | 0.020845 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2575-10_0_3_line_13 | NAYY 4x150 SE | 10 | 12 | 0.034989 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2575-10_0_3_line_14 | NAYY 4x150 SE | 11 | 13 | 0.046474 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2575-10_0_3_line_15 | NAYY 4x150 SE | 11 | 14 | 0.025928 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2575-10_0_3_line_16 | NAYY 4x150 SE | 13 | 15 | 0.0040628 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2575-10_0_3_line_17 | NAYY 4x150 SE | 14 | 16 | 0.02234 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2575-10_0_3_line_18 | NAYY 4x150 SE | 14 | 17 | 0.0122 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2575-10_0_3_line_19 | NAYY 4x150 SE | 16 | 18 | 0.0041248 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
20 | LV_2575-10_0_3_line_20 | NAYY 4x150 SE | 17 | 19 | 0.026873 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2575-10_0_3_line_21 | NAYY 4x150 SE | 17 | 20 | 0.044286 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2575-10_0_3_line_22 | NAYY 4x150 SE | 18 | 74 | 0.026034 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
23 | LV_2575-10_0_3_line_23 | NAYY 4x150 SE | 19 | 77 | 0.025462 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2575-10_0_3_line_24 | NAYY 4x150 SE | 20 | 76 | 0.0012439 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2575-10_0_3_line_25 | NAYY 4x150 SE | 21 | 22 | 0.027142 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2575-10_0_3_line_26 | NAYY 4x150 SE | 21 | 23 | 0.00080991 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2575-10_0_3_line_27 | NAYY 4x150 SE | 22 | 24 | 0.011976 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2575-10_0_3_line_28 | NAYY 4x150 SE | 23 | 25 | 0.023461 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2575-10_0_3_line_29 | NAYY 4x150 SE | 24 | 26 | 0.0078609 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
30 | LV_2575-10_0_3_line_30 | NAYY 4x150 SE | 25 | 27 | 0.0016395 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2575-10_0_3_line_31 | NAYY 4x150 SE | 26 | 28 | 0.012305 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
32 | LV_2575-10_0_3_line_32 | NAYY 4x150 SE | 26 | 29 | 0.035181 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2575-10_0_3_line_33 | NAYY 4x150 SE | 27 | 30 | 0.012882 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2575-10_0_3_line_34 | NAYY 4x150 SE | 28 | 75 | 0.012271 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
35 | LV_2575-10_0_3_line_35 | NAYY 4x150 SE | 29 | 81 | 0.0079483 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2575-10_0_3_line_36 | NAYY 4x150 SE | 30 | 83 | 0.02777 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2575-10_0_3_line_37 | NAYY 4x150 SE | 31 | 32 | 0.025864 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2575-10_0_3_line_38 | NAYY 4x150 SE | 31 | 33 | 0.01564 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_2575-10_0_3_line_39 | NAYY 4x150 SE | 32 | 34 | 0.008053 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_2575-10_0_3_line_40 | NAYY 4x150 SE | 34 | 35 | 0.018548 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_2575-10_0_3_line_41 | NAYY 4x150 SE | 35 | 36 | 0.007017 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_2575-10_0_3_line_42 | NAYY 4x150 SE | 36 | 86 | 0.02708 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_2575-10_0_3_line_43 | NAYY 4x150 SE | 36 | 87 | 0.02485 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_2575-10_0_3_line_44 | NAYY 4x150 SE | 37 | 38 | 0.028332 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_2575-10_0_3_line_45 | NAYY 4x150 SE | 37 | 39 | 0.0090541 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_2575-10_0_3_line_46 | NAYY 4x150 SE | 38 | 40 | 0.016414 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_2575-10_0_3_line_47 | NAYY 4x150 SE | 39 | 41 | 0.020055 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_2575-10_0_3_line_48 | NAYY 4x150 SE | 39 | 42 | 0.012512 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_2575-10_0_3_line_49 | NAYY 4x150 SE | 40 | 43 | 0.006767 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_2575-10_0_3_line_50 | NAYY 4x150 SE | 40 | 44 | 0.044268 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_2575-10_0_3_line_51 | NAYY 4x150 SE | 41 | 45 | 0.0073997 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_2575-10_0_3_line_52 | NAYY 4x150 SE | 43 | 46 | 0.017104 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_2575-10_0_3_line_53 | NAYY 4x150 SE | 45 | 47 | 0.016407 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_2575-10_0_3_line_54 | NAYY 4x150 SE | 46 | 79 | 0.014225 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_2575-10_0_3_line_55 | NAYY 4x150 SE | 48 | 49 | 0.0019207 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_2575-10_0_3_line_56 | NAYY 4x150 SE | 48 | 50 | 0.02115 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_2575-10_0_3_line_57 | NAYY 4x150 SE | 49 | 51 | 0.027735 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_2575-10_0_3_line_58 | NAYY 4x150 SE | 50 | 52 | 0.0062708 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_2575-10_0_3_line_59 | NAYY 4x150 SE | 51 | 53 | 0.027043 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_2575-10_0_3_line_60 | NAYY 4x150 SE | 52 | 54 | 0.021259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_2575-10_0_3_line_61 | NAYY 4x150 SE | 53 | 55 | 0.023038 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_2575-10_0_3_line_62 | NAYY 4x150 SE | 54 | 56 | 0.00096213 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_2575-10_0_3_line_63 | NAYY 4x150 SE | 57 | 58 | 0.014661 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_2575-10_0_3_line_64 | NAYY 4x150 SE | 57 | 59 | 0.032402 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_2575-10_0_3_line_65 | NAYY 4x150 SE | 58 | 60 | 0.0032102 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_2575-10_0_3_line_66 | NAYY 4x150 SE | 59 | 61 | 0.011682 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_2575-10_0_3_line_67 | NAYY 4x150 SE | 59 | 62 | 0.038403 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_2575-10_0_3_line_68 | NAYY 4x150 SE | 61 | 63 | 0.0079417 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_2575-10_0_3_line_69 | NAYY 4x150 SE | 62 | 64 | 0.022614 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_2575-10_0_3_line_70 | NAYY 4x150 SE | 63 | 65 | 0.017828 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_2575-10_0_3_line_71 | NAYY 4x150 SE | 64 | 66 | 0.0016963 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_2575-10_0_3_line_72 | NAYY 4x150 SE | 65 | 78 | 0.015226 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_2575-10_0_3_line_73 | NAYY 4x150 SE | 66 | 70 | 0.034137 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_2575-10_0_3_line_74 | NAYY 4x150 SE | 67 | 68 | 0.011017 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_2575-10_0_3_line_75 | NAYY 4x150 SE | 67 | 69 | 0.0067483 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_2575-10_0_3_line_76 | NAYY 4x150 SE | 68 | 70 | 0.01749 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_2575-10_0_3_line_77 | NAYY 4x150 SE | 69 | 71 | 0.029059 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_2575-10_0_3_line_78 | NAYY 4x150 SE | 70 | 72 | 0.0016718 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_2575-10_0_3_line_79 | NAYY 4x150 SE | 72 | 73 | 0.0087501 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_2575-10_0_3_line_80 | NAYY 4x150 SE | 73 | 83 | 0.0088974 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_2575-10_0_3_line_81 | NAYY 4x150 SE | 74 | 75 | 0.005916 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
82 | LV_2575-10_0_3_line_82 | NAYY 4x150 SE | 77 | 84 | 0.0052812 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_2575-10_0_3_line_83 | NAYY 4x150 SE | 78 | 79 | 0.031327 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_2575-10_0_3_line_84 | NAYY 4x150 SE | 81 | 82 | 0.0012453 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_2575-10_0_3_line_85 | NAYY 4x150 SE | 84 | 85 | 0.020957 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_2575-10_0_3_line_86 | NAYY 4x150 SE | 85 | 86 | 0.002117 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2575-10_0_3_trafo_14 | 0.25 MVA 20/0.4 kV | 88 | 24 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2629824.1019 | 1236182.068 | 2629839.9113 | 1236197.2458
1 | 2629824.1019 | 1236182.068 | 2629822.0361 | 1236180.0847
2 | 2629839.9113 | 1236197.2458 | 2629842.7776 | 1236199.9976
3 | 2629814.7171 | 1236173.0582 | 2629822.0361 | 1236180.0847
4 | 2629855.2982 | 1236212.018 | 2629842.7776 | 1236199.9976
5 | 2629814.7171 | 1236173.0582 | 2629802.2505 | 1236161.0896
6 | 2629865.9261 | 1236222.2212 | 2629855.2982 | 1236212.018
7 | 2629802.174 | 1236161.0161 | 2629802.2505 | 1236161.0896
8 | 2629865.9261 | 1236222.2212 | 2629889.8237 | 1236200.3404
9 | 2629865.9261 | 1236222.2212 | 2629837.9525 | 1236248.9919
10 | 2629789.907 | 1236149.2392 | 2629802.174 | 1236161.0161
11 | 2629941.9095 | 1236186.396 | 2629944.7563 | 1236190.3754 | 2629948.6649 | 1236192.0368
12 | 2629929.7813 | 1236169.4426 | 2629941.9095 | 1236186.396
13 | 2629971.1051 | 1236218.644 | 2629967.1414 | 1236215.3036 | 2629953.1409 | 1236197.7222 | 2629949.3092 | 1236192.3106 | 2629948.6649 | 1236192.0368
14 | 2629929.7813 | 1236169.4426 | 2629904.7252 | 1236188.0726 | 2629894.1127 | 1236196.4134 | 2629892.8202 | 1236197.5968
15 | 2629949.3657 | 1236152.5417 | 2629942.2525 | 1236160.1662 | 2629929.7813 | 1236169.4426
16 | 2629889.8237 | 1236200.3404 | 2629892.8202 | 1236197.5968
17 | 2629949.3657 | 1236152.5417 | 2629941.0285 | 1236146.2737 | 2629931.4734 | 1236139.1657
18 | 2629949.3657 | 1236152.5417 | 2629959.5543 | 1236159.2972
19 | 2629928.1639 | 1236136.7039 | 2629931.4734 | 1236139.1657
20 | 2629959.5543 | 1236159.2972 | 2629967.9939 | 1236164.7542 | 2629982.7219 | 1236172.883
21 | 2629959.5543 | 1236159.2972 | 2629970.83 | 1236142.5102 | 2629966.325 | 1236128.0563 | 2629971.3495 | 1236120.6811
22 | 2629907.2245 | 1236121.2354 | 2629910.0152 | 1236123.2033 | 2629928.1639 | 1236136.7039
23 | 2629982.7219 | 1236172.883 | 2629982.7532 | 1236172.9003 | 2629984.7377 | 1236173.9888 | 2630005.6435 | 1236183.9628
24 | 2629972.0499 | 1236119.653 | 2629971.3495 | 1236120.6811
25 | 2629843.122 | 1236077.7471 | 2629865.8028 | 1236092.6564
26 | 2629842.4452 | 1236077.3022 | 2629843.122 | 1236077.7471
27 | 2629865.8028 | 1236092.6564 | 2629870.2773 | 1236095.5977 | 2629875.7767 | 1236099.2852
28 | 2629822.8404 | 1236064.415 | 2629842.4452 | 1236077.3022
29 | 2629882.3057 | 1236103.6631 | 2629875.7767 | 1236099.2852
30 | 2629822.8404 | 1236064.415 | 2629821.4704 | 1236063.5145
31 | 2629882.3057 | 1236103.6631 | 2629892.3617 | 1236110.7544
32 | 2629882.3057 | 1236103.6631 | 2629884.403 | 1236100.4049 | 2629898.351 | 1236072.3777
33 | 2629810.706 | 1236056.4385 | 2629821.4704 | 1236063.5145
34 | 2629892.3617 | 1236110.7544 | 2629902.3897 | 1236117.826
35 | 2629898.351 | 1236072.3777 | 2629901.8922 | 1236065.2619
36 | 2629810.706 | 1236056.4385 | 2629787.5011 | 1236041.1847
37 | 2630019.2903 | 1236260.2833 | 2630035.9159 | 1236240.4327
38 | 2630009.0234 | 1236272.1056 | 2630019.2903 | 1236260.2833
39 | 2630035.9159 | 1236240.4327 | 2630041.0858 | 1236234.2583
40 | 2630053.6837 | 1236220.6656 | 2630047.7977 | 1236226.5062 | 2630044.8986 | 1236229.7047 | 2630041.0858 | 1236234.2583
41 | 2630053.6837 | 1236220.6656 | 2630051.1062 | 1236214.1374
42 | 2630051.1062 | 1236214.1374 | 2630046.5858 | 1236207.277 | 2630032.3949 | 1236197.477 | 2630030.9543 | 1236196.7405
43 | 2630051.1062 | 1236214.1374 | 2630062.0278 | 1236204.5755 | 2630068.3567 | 1236196.4062
44 | 2629944.7551 | 1236039.7863 | 2629922.7451 | 1236021.9468
45 | 2629951.789 | 1236045.4874 | 2629944.7551 | 1236039.7863
46 | 2629909.9938 | 1236011.6116 | 2629922.7451 | 1236021.9468
47 | 2629951.789 | 1236045.4874 | 2629966.9524 | 1236058.6122
48 | 2629951.789 | 1236045.4874 | 2629960.5705 | 1236036.5749
49 | 2629907.3066 | 1236017.8242 | 2629909.9938 | 1236011.6116
50 | 2629909.9938 | 1236011.6116 | 2629915.0015 | 1236004.399 | 2629931.9042 | 1235986.7063 | 2629939.8095 | 1235979.0309
51 | 2629966.9524 | 1236058.6122 | 2629972.5473 | 1236063.4549
52 | 2629907.3066 | 1236017.8242 | 2629898.8289 | 1236007.8532 | 2629895.8855 | 1236005.1209
53 | 2629984.9527 | 1236074.1926 | 2629972.5473 | 1236063.4549
54 | 2629885.4599 | 1235995.4431 | 2629895.8855 | 1236005.1209
55 | 2629778.5588 | 1236256.3803 | 2629779.856 | 1236257.7968
56 | 2629764.2749 | 1236240.7822 | 2629778.5588 | 1236256.3803
57 | 2629779.856 | 1236257.7968 | 2629796.3476 | 1236275.8058 | 2629799.1338 | 1236277.6042
58 | 2629764.2749 | 1236240.7822 | 2629760.0399 | 1236236.1575
59 | 2629821.308 | 1236264.9207 | 2629811.7238 | 1236274.0928 | 2629807.4192 | 1236276.9619 | 2629803.5315 | 1236278.1877 | 2629799.8019 | 1236278.0356 | 2629799.1338 | 1236277.6042
60 | 2629760.0399 | 1236236.1575 | 2629745.6828 | 1236220.4794
61 | 2629837.9525 | 1236248.9919 | 2629821.308 | 1236264.9207
62 | 2629745.6828 | 1236220.4794 | 2629745.033 | 1236219.7699
63 | 2629781.0949 | 1235918.0176 | 2629790.6952 | 1235929.0979
64 | 2629814.4098 | 1235951.1388 | 2629804.6972 | 1235942.9295 | 2629791.3992 | 1235929.9104 | 2629790.6952 | 1235929.0979
65 | 2629778.9927 | 1235915.5914 | 2629781.0949 | 1235918.0176
66 | 2629814.4098 | 1235951.1388 | 2629823.9261 | 1235957.9152
67 | 2629814.4098 | 1235951.1388 | 2629809.9263 | 1235957.9539 | 2629795.2803 | 1235973.8571 | 2629790.0185 | 1235980.6919
68 | 2629830.3953 | 1235962.5217 | 2629823.9261 | 1235957.9152
69 | 2629790.0185 | 1235980.6919 | 2629789.7126 | 1235981.0893 | 2629787.7948 | 1235986.3052 | 2629786.8986 | 1235993.0048 | 2629787.5845 | 1235998.067 | 2629791.3616 | 1236000.8432
70 | 2629830.3953 | 1235962.5217 | 2629831.1561 | 1235963.0635 | 2629845.7562 | 1235971.5639
71 | 2629790.4146 | 1236002.2505 | 2629791.3616 | 1236000.8432 | 2629791.3616 | 1236000.8432
72 | 2629859.1945 | 1235978.7161 | 2629848.781 | 1235973.3249 | 2629845.7562 | 1235971.5639
73 | 2629771.3573 | 1236030.5726 | 2629790.4146 | 1236002.2505
74 | 2629756.7049 | 1236021.0224 | 2629747.4756 | 1236015.007
75 | 2629741.8222 | 1236011.3222 | 2629747.4756 | 1236015.007
76 | 2629771.3573 | 1236030.5726 | 2629756.7049 | 1236021.0224
77 | 2629717.3744 | 1235995.6263 | 2629719.8738 | 1235997.0167 | 2629741.8222 | 1236011.3222
78 | 2629771.3573 | 1236030.5726 | 2629772.7544 | 1236031.491
79 | 2629780.0662 | 1236036.2974 | 2629772.7544 | 1236031.491
80 | 2629780.0662 | 1236036.2974 | 2629787.5011 | 1236041.1847
81 | 2629907.2245 | 1236121.2354 | 2629902.3897 | 1236117.826
82 | 2630010.4101 | 1236186.2369 | 2630005.6435 | 1236183.9628
83 | 2629859.1945 | 1235978.7161 | 2629866.585 | 1235982.5422 | 2629879.4046 | 1235989.8222 | 2629885.4599 | 1235995.4431
84 | 2629902.447 | 1236064.147 | 2629901.8922 | 1236065.2619
85 | 2630010.4101 | 1236186.2369 | 2630029.0694 | 1236195.7768
86 | 2630030.9543 | 1236196.7405 | 2630029.0694 | 1236195.7768

## bus_geodata
| x | y | coords
0 | 2629824.1019 | 1236182.068
1 | 2629839.9113 | 1236197.2458
2 | 2629822.0361 | 1236180.0847
3 | 2629842.7776 | 1236199.9976
4 | 2629814.7171 | 1236173.0582
5 | 2629855.2982 | 1236212.018
6 | 2629802.2505 | 1236161.0896
7 | 2629865.9261 | 1236222.2212
8 | 2629802.174 | 1236161.0161
9 | 2629941.9095 | 1236186.396
10 | 2629948.6649 | 1236192.0368
11 | 2629929.7813 | 1236169.4426
12 | 2629971.1051 | 1236218.644
13 | 2629892.8202 | 1236197.5968
14 | 2629949.3657 | 1236152.5417
15 | 2629889.8237 | 1236200.3404
16 | 2629931.4734 | 1236139.1657
17 | 2629959.5543 | 1236159.2972
18 | 2629928.1639 | 1236136.7039
19 | 2629982.7219 | 1236172.883
20 | 2629971.3495 | 1236120.6811
21 | 2629843.122 | 1236077.7471
22 | 2629865.8028 | 1236092.6564
23 | 2629842.4452 | 1236077.3022
24 | 2629875.7767 | 1236099.2852
25 | 2629822.8404 | 1236064.415
26 | 2629882.3057 | 1236103.6631
27 | 2629821.4704 | 1236063.5145
28 | 2629892.3617 | 1236110.7544
29 | 2629898.351 | 1236072.3777
30 | 2629810.706 | 1236056.4385
31 | 2630019.2903 | 1236260.2833
32 | 2630035.9159 | 1236240.4327
33 | 2630009.0234 | 1236272.1056
34 | 2630041.0858 | 1236234.2583
35 | 2630053.6837 | 1236220.6656
36 | 2630051.1062 | 1236214.1374
37 | 2629944.7551 | 1236039.7863
38 | 2629922.7451 | 1236021.9468
39 | 2629951.789 | 1236045.4874
40 | 2629909.9938 | 1236011.6116
41 | 2629966.9524 | 1236058.6122
42 | 2629960.5705 | 1236036.5749
43 | 2629907.3066 | 1236017.8242
44 | 2629939.8095 | 1235979.0309
45 | 2629972.5473 | 1236063.4549
46 | 2629895.8855 | 1236005.1209
47 | 2629984.9527 | 1236074.1926
48 | 2629778.5588 | 1236256.3803
49 | 2629779.856 | 1236257.7968
50 | 2629764.2749 | 1236240.7822
51 | 2629799.1338 | 1236277.6042
52 | 2629760.0399 | 1236236.1575
53 | 2629821.308 | 1236264.9207
54 | 2629745.6828 | 1236220.4794
55 | 2629837.9525 | 1236248.9919
56 | 2629745.033 | 1236219.7699
57 | 2629790.6952 | 1235929.0979
58 | 2629781.0949 | 1235918.0176
59 | 2629814.4098 | 1235951.1388
60 | 2629778.9927 | 1235915.5914
61 | 2629823.9261 | 1235957.9152
62 | 2629790.0185 | 1235980.6919
63 | 2629830.3953 | 1235962.5217
64 | 2629791.3616 | 1236000.8432
65 | 2629845.7562 | 1235971.5639
66 | 2629790.4146 | 1236002.2505
67 | 2629747.4756 | 1236015.007
68 | 2629756.7049 | 1236021.0224
69 | 2629741.8222 | 1236011.3222
70 | 2629771.3573 | 1236030.5726
71 | 2629717.3744 | 1235995.6263
72 | 2629772.7544 | 1236031.491
73 | 2629780.0662 | 1236036.2974
74 | 2629907.2245 | 1236121.2354
75 | 2629902.3897 | 1236117.826
76 | 2629972.0499 | 1236119.653
77 | 2630005.6435 | 1236183.9628
78 | 2629859.1945 | 1235978.7161
79 | 2629885.4599 | 1235995.4431
80 | 2629789.907 | 1236149.2392
81 | 2629901.8922 | 1236065.2619
82 | 2629902.447 | 1236064.147
83 | 2629787.5011 | 1236041.1847
84 | 2630010.4101 | 1236186.2369
85 | 2630029.0693 | 1236195.7768
86 | 2630030.9543 | 1236196.7405
87 | 2630068.3567 | 1236196.4062
88 | 2629882.3057 | 1236103.6631

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97956 | -0.14362 | 0.0040821 | 0.0010231
1 | 0.98008 | -0.13986 | 0.0054995 | 0.0013783
2 | 0.97951 | -0.14399 | 0.0029685 | 0.00074397
3 | 0.98021 | -0.13895 | 0.0059023 | 0.0014792
4 | 0.97937 | -0.14498 | 0.0012316 | 0.00030867
5 | 0.98092 | -0.13393 | 0.0047783 | 0.0011975
6 | 0.97916 | -0.14646 | 0.0034628 | 0.00086785
7 | 0.98162 | -0.12894 | 0 | 0
8 | 0.97916 | -0.14647 | 0.0027338 | 0.00068516
9 | 0.98774 | -0.085638 | 0.0088235 | 0.0022114
10 | 0.98763 | -0.086402 | 0.0070195 | 0.0017593
11 | 0.98825 | -0.082014 | 0 | 0
12 | 0.98757 | -0.086817 | 0.0011552 | 0.00028952
13 | 0.98442 | -0.10903 | 0.00098324 | 0.00024642
14 | 0.99102 | -0.062549 | 0 | 0
15 | 0.98409 | -0.11136 | 0.003164 | 0.00079296
16 | 0.99406 | -0.041273 | 0.014196 | 0.0035579
17 | 0.99066 | -0.065071 | 0 | 0
18 | 0.99438 | -0.03902 | 0.0062648 | 0.0015701
19 | 0.99013 | -0.068828 | 0.0028694 | 0.00071914
20 | 0.99024 | -0.068041 | 0.0054262 | 0.0013599
21 | 0.99464 | -0.037126 | 0.0019008 | 0.00047638
22 | 0.9983 | -0.01172 | 0.0047582 | 0.0011925
23 | 0.99454 | -0.037871 | 0.0056665 | 0.0014202
24 | 1 | 0 | -0.2395 | -0.060234
25 | 0.99163 | -0.058185 | 0.0061023 | 0.0015294
26 | 0.99922 | -0.0054083 | 0 | 0
27 | 0.99144 | -0.059507 | 0.0071373 | 0.0017888
28 | 0.99812 | -0.013006 | 0.0014456 | 0.00036229
29 | 0.9985 | -0.010461 | 0.0022316 | 0.0005593
30 | 0.99008 | -0.068978 | 0.0032234 | 0.00080787
31 | 0.98873 | -0.078765 | 0 | 0
32 | 0.98886 | -0.077839 | 0 | 0
33 | 0.98865 | -0.079325 | 0.0035046 | 0.00087833
34 | 0.9889 | -0.077551 | 0.0017162 | 0.00043012
35 | 0.98904 | -0.076562 | 0 | 0
36 | 0.98909 | -0.076187 | 0 | 0
37 | 0.97559 | -0.17184 | 0.0057359 | 0.0014376
38 | 0.97603 | -0.16873 | 0.0013061 | 0.00032733
39 | 0.97553 | -0.1723 | 0 | 0
40 | 0.97631 | -0.1667 | 0 | 0
41 | 0.97543 | -0.17303 | 0.00092193 | 0.00023106
42 | 0.97551 | -0.17246 | 0.0012844 | 0.0003219
43 | 0.97644 | -0.16577 | 0 | 0
44 | 0.97622 | -0.16734 | 0.0013864 | 0.00034747
45 | 0.9754 | -0.17322 | 0.0012539 | 0.00031425
46 | 0.97677 | -0.1634 | 0.0030595 | 0.00076678
47 | 0.97537 | -0.17344 | 0.001288 | 0.0003228
48 | 0.97913 | -0.14671 | 0.0012002 | 0.00030081
49 | 0.97915 | -0.14656 | 0.0017327 | 0.00043425
50 | 0.97893 | -0.14814 | 0.0012722 | 0.00031885
51 | 0.97953 | -0.14385 | 0.0017561 | 0.00044011
52 | 0.97888 | -0.14848 | 0.0024874 | 0.00062339
53 | 0.97997 | -0.14071 | 0.0047545 | 0.0011916
54 | 0.9788 | -0.14908 | 0.00096974 | 0.00024304
55 | 0.9805 | -0.1369 | 0.003908 | 0.00097943
56 | 0.97879 | -0.14909 | 0.0017351 | 0.00043486
57 | 0.97957 | -0.14335 | 0.0019745 | 0.00049486
58 | 0.97951 | -0.14379 | 0.0011881 | 0.00029776
59 | 0.9798 | -0.14171 | 0 | 0
60 | 0.9795 | -0.14385 | 0.0016909 | 0.00042378
61 | 0.97931 | -0.1452 | 0.0037569 | 0.00094157
62 | 0.98168 | -0.12835 | 0.0018181 | 0.00045566
63 | 0.97903 | -0.14726 | 0.0025187 | 0.00063124
64 | 0.98284 | -0.12008 | 0.0017479 | 0.00043807
65 | 0.97844 | -0.15142 | 0.0015989 | 0.00040073
66 | 0.98294 | -0.11943 | 0.012377 | 0.0031018
67 | 0.98474 | -0.10669 | 0.011028 | 0.0027639
68 | 0.98499 | -0.10491 | 0.00035034 | 8.7802e-05
69 | 0.98469 | -0.10701 | 0.0026484 | 0.00066374
70 | 0.98539 | -0.10202 | 0 | 0
71 | 0.98461 | -0.10762 | 0.0020291 | 0.00050854
72 | 0.98555 | -0.10089 | 0.00225 | 0.0005639
73 | 0.98641 | -0.094802 | 0.00057523 | 0.00014417
74 | 0.99654 | -0.024012 | 0.0033881 | 0.00084913
75 | 0.99704 | -0.02051 | 0.0040887 | 0.0010247
76 | 0.99024 | -0.068056 | 0.0011634 | 0.00029158
77 | 0.98973 | -0.071646 | 0.00069327 | 0.00017375
78 | 0.97798 | -0.15472 | 0.0016608 | 0.00041624
79 | 0.97711 | -0.16099 | 0.0028841 | 0.00072283
80 | 0.97911 | -0.14682 | 0.0020084 | 0.00050335
81 | 0.99836 | -0.011426 | 0.0050403 | 0.0012632
82 | 0.99835 | -0.011514 | 0.007083 | 0.0017752
83 | 0.9873 | -0.088567 | 0.00070864 | 0.0001776
84 | 0.98965 | -0.072194 | 0 | 0
85 | 0.98935 | -0.074366 | 0.001304 | 0.00032681
86 | 0.98932 | -0.074558 | 0.0029656 | 0.00074324
87 | 0.98907 | -0.076357 | 0.00066846 | 0.00016753
88 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.016491 | -0.0041329 | 0.0165 | 0.0041359 | 8.5819e-06 | 3.0247e-06 | 0.025051 | 0.025051 | 0.025051 | 0.97956 | -0.14362 | 0.98008 | -0.13986 | 9.2781
1 | 0.012409 | 0.0031098 | -0.012408 | -0.0031096 | 6.3495e-07 | 2.0816e-07 | 0.01885 | 0.01885 | 0.01885 | 0.97956 | -0.14362 | 0.97951 | -0.14399 | 6.9814
2 | -0.021999 | -0.0055143 | 0.022002 | 0.0055153 | 2.766e-06 | 1.0138e-06 | 0.0334 | 0.0334 | 0.0334 | 0.98008 | -0.13986 | 0.98021 | -0.13895 | 12.3705
3 | 0.0094397 | 0.0023657 | -0.0094384 | -0.0023653 | 1.3019e-06 | 3.7305e-07 | 0.01434 | 0.01434 | 0.01434 | 0.97951 | -0.14399 | 0.97937 | -0.14498 | 5.3112
4 | -0.027904 | -0.0069945 | 0.027923 | 0.0070018 | 1.9434e-05 | 7.2558e-06 | 0.04236 | 0.04236 | 0.04236 | 0.98021 | -0.13895 | 0.98092 | -0.13393 | 15.689
5 | 0.0082068 | 0.0020566 | -0.0082051 | -0.0020562 | 1.6767e-06 | 4.2745e-07 | 0.012469 | 0.012469 | 0.012469 | 0.97937 | -0.14498 | 0.97916 | -0.14646 | 4.6182
6 | -0.032702 | -0.0081993 | 0.032724 | 0.0082078 | 2.2625e-05 | 8.5158e-06 | 0.049609 | 0.049609 | 0.049609 | 0.98092 | -0.13393 | 0.98162 | -0.12894 | 18.3736
7 | 0.0047423 | 0.0011883 | -0.0047423 | -0.0011883 | 3.4395e-09 | -1.2555e-11 | 0.0072068 | 0.0072068 | 0.0072068 | 0.97916 | -0.14646 | 0.97916 | -0.14647 | 2.6692
8 | -0.052581 | -0.013188 | 0.052709 | 0.013237 | 0.00012846 | 4.8998e-05 | 0.07971 | 0.07971 | 0.07971 | 0.98162 | -0.12894 | 0.98409 | -0.11136 | 29.5222
9 | 0.019856 | 0.0049798 | -0.019835 | -0.0049719 | 2.1892e-05 | 7.9311e-06 | 0.030101 | 0.030101 | 0.030101 | 0.98162 | -0.12894 | 0.9805 | -0.1369 | 11.1487
10 | 0.0020085 | 0.00050318 | -0.0020084 | -0.00050335 | 9.8857e-08 | -1.7586e-07 | 0.0030522 | 0.0030523 | 0.0030523 | 0.97916 | -0.14647 | 0.97911 | -0.14682 | 1.1305
11 | 0.0081756 | 0.0020486 | -0.0081748 | -0.0020484 | 8.6516e-07 | 2.1578e-07 | 0.012316 | 0.012316 | 0.012316 | 0.98774 | -0.085638 | 0.98763 | -0.086402 | 4.5616
12 | -0.016999 | -0.00426 | 0.017008 | 0.004263 | 8.5304e-06 | 3.014e-06 | 0.025609 | 0.025609 | 0.025609 | 0.98774 | -0.085638 | 0.98825 | -0.082014 | 9.4848
13 | 0.0011553 | 0.00028909 | -0.0011552 | -0.00028952 | 6.614e-08 | -4.2228e-07 | 0.0017404 | 0.0017406 | 0.0017406 | 0.98763 | -0.086402 | 0.98757 | -0.086817 | 0.64466
14 | 0.057089 | 0.014365 | -0.056875 | -0.014283 | 0.00021438 | 8.1861e-05 | 0.08598 | 0.08598 | 0.08598 | 0.98825 | -0.082014 | 0.98442 | -0.10903 | 31.8445
15 | -0.074097 | -0.018628 | 0.074298 | 0.018705 | 0.00020146 | 7.7152e-05 | 0.11159 | 0.11159 | 0.11159 | 0.98825 | -0.082014 | 0.99102 | -0.062549 | 41.3292
16 | 0.055891 | 0.014037 | -0.055873 | -0.01403 | 1.8099e-05 | 6.9096e-06 | 0.084494 | 0.084494 | 0.084494 | 0.98442 | -0.10903 | 0.98409 | -0.11136 | 31.294
17 | -0.094638 | -0.023803 | 0.094919 | 0.023911 | 0.00028159 | 0.00010802 | 0.14213 | 0.14213 | 0.14213 | 0.99102 | -0.062549 | 0.99406 | -0.041273 | 52.6402
18 | 0.02034 | 0.005098 | -0.020332 | -0.0050954 | 7.1004e-06 | 2.5738e-06 | 0.03054 | 0.03054 | 0.03054 | 0.99102 | -0.062549 | 0.99066 | -0.065071 | 11.3111
19 | -0.10912 | -0.027469 | 0.10915 | 0.027482 | 3.4351e-05 | 1.3105e-05 | 0.16338 | 0.16338 | 0.16338 | 0.99406 | -0.041273 | 0.99438 | -0.03902 | 30.2553
20 | 0.01374 | 0.0034434 | -0.013733 | -0.003441 | 7.1423e-06 | 2.4012e-06 | 0.020638 | 0.020638 | 0.020638 | 0.99066 | -0.065071 | 0.99013 | -0.068828 | 7.6438
21 | 0.0065923 | 0.001652 | -0.0065896 | -0.0016515 | 2.7095e-06 | 4.7217e-07 | 0.0099019 | 0.0099021 | 0.0099021 | 0.99066 | -0.065071 | 0.99024 | -0.068041 | 3.6674
22 | -0.11541 | -0.029052 | 0.11566 | 0.029145 | 0.00024241 | 9.2558e-05 | 0.17275 | 0.17275 | 0.17275 | 0.99438 | -0.03902 | 0.99654 | -0.024012 | 31.9914
23 | 0.010864 | 0.0027219 | -0.010859 | -0.0027206 | 4.2349e-06 | 1.3015e-06 | 0.016326 | 0.016326 | 0.016326 | 0.99013 | -0.068828 | 0.98973 | -0.071646 | 6.0467
24 | 0.0011634 | 0.00029156 | -0.0011634 | -0.00029158 | 2.3724e-09 | -1.509e-08 | 0.0017482 | 0.0017482 | 0.0017482 | 0.99024 | -0.068041 | 0.99024 | -0.068056 | 0.6475
25 | -0.094075 | -0.023705 | 0.09441 | 0.023833 | 0.00033569 | 0.00012876 | 0.14078 | 0.14078 | 0.14078 | 0.99464 | -0.037126 | 0.9983 | -0.01172 | 52.1421
26 | 0.092174 | 0.023228 | -0.092164 | -0.023224 | 9.6161e-06 | 3.688e-06 | 0.13794 | 0.13794 | 0.13794 | 0.99464 | -0.037126 | 0.99454 | -0.037871 | 51.0889
27 | -0.099169 | -0.025026 | 0.099332 | 0.025089 | 0.00016341 | 6.2695e-05 | 0.14788 | 0.14788 | 0.14788 | 0.9983 | -0.01172 | 1 | 0 | 54.7688
28 | 0.086498 | 0.021804 | -0.086252 | -0.02171 | 0.00024537 | 9.4069e-05 | 0.12946 | 0.12946 | 0.12946 | 0.99454 | -0.037871 | 0.99163 | -0.058185 | 47.9489
29 | 0.13937 | 0.035145 | -0.13927 | -0.035105 | 0.00010556 | 4.0395e-05 | 0.20746 | 0.20746 | 0.20746 | 1 | 0 | 0.99922 | -0.0054083 | 38.4193
30 | 0.08015 | 0.020181 | -0.080135 | -0.020175 | 1.4806e-05 | 5.6736e-06 | 0.12031 | 0.12031 | 0.12031 | 0.99163 | -0.058185 | 0.99144 | -0.059507 | 44.5574
31 | 0.1249 | 0.031503 | -0.12477 | -0.031452 | 0.00013292 | 5.08e-05 | 0.18607 | 0.18607 | 0.18607 | 0.99922 | -0.0054083 | 0.99812 | -0.013006 | 34.4573
32 | 0.014367 | 0.0036016 | -0.014357 | -0.0035982 | 1.0049e-05 | 3.4045e-06 | 0.021395 | 0.021395 | 0.021395 | 0.99922 | -0.0054083 | 0.9985 | -0.010461 | 7.9241
33 | 0.072998 | 0.018386 | -0.072902 | -0.018349 | 9.6544e-05 | 3.6967e-05 | 0.10959 | 0.10959 | 0.10959 | 0.99144 | -0.059507 | 0.99008 | -0.068978 | 40.59
34 | 0.12332 | 0.03109 | -0.12319 | -0.031041 | 0.00012949 | 4.9485e-05 | 0.18391 | 0.18391 | 0.18391 | 0.99812 | -0.013006 | 0.99704 | -0.02051 | 34.0582
35 | 0.012125 | 0.0030389 | -0.012123 | -0.0030384 | 1.6194e-06 | 5.1889e-07 | 0.018069 | 0.01807 | 0.01807 | 0.9985 | -0.010461 | 0.99836 | -0.011426 | 6.6924
36 | 0.069678 | 0.017542 | -0.069488 | -0.017469 | 0.00019013 | 7.2771e-05 | 0.10475 | 0.10475 | 0.10475 | 0.99008 | -0.068978 | 0.9873 | -0.088567 | 38.7958
37 | -0.0035048 | -0.00087823 | 0.0035053 | 0.00087807 | 4.4901e-07 | -1.5906e-07 | 0.0052747 | 0.0052745 | 0.0052747 | 0.98873 | -0.078765 | 0.98886 | -0.077839 | 1.9536
38 | 0.0035048 | 0.00087823 | -0.0035046 | -0.00087833 | 2.7153e-07 | -9.6135e-08 | 0.0052747 | 0.0052747 | 0.0052747 | 0.98873 | -0.078765 | 0.98865 | -0.079325 | 1.9536
39 | -0.0035053 | -0.00087807 | 0.0035054 | 0.00087802 | 1.398e-07 | -4.9543e-08 | 0.0052745 | 0.0052745 | 0.0052745 | 0.98886 | -0.077839 | 0.9889 | -0.077551 | 1.9535
40 | -0.0052216 | -0.0013081 | 0.0052223 | 0.0013082 | 7.1446e-07 | 3.6795e-08 | 0.0078569 | 0.0078568 | 0.0078569 | 0.9889 | -0.077551 | 0.98904 | -0.076562 | 2.91
41 | -0.0052223 | -0.0013082 | 0.0052226 | 0.0013082 | 2.7029e-07 | 1.3901e-08 | 0.0078568 | 0.0078568 | 0.0078568 | 0.98904 | -0.076562 | 0.98909 | -0.076187 | 2.9099
42 | -0.0058911 | -0.0014754 | 0.0058924 | 0.0014756 | 1.3271e-06 | 1.628e-07 | 0.0088623 | 0.0088622 | 0.0088623 | 0.98909 | -0.076187 | 0.98932 | -0.074558 | 3.2823
43 | 0.00066848 | 0.00016722 | -0.00066846 | -0.00016753 | 1.5681e-08 | -3.129e-07 | 0.0010056 | 0.0010057 | 0.0010057 | 0.98909 | -0.076187 | 0.98907 | -0.076357 | 0.37247
44 | -0.010485 | -0.002627 | 0.010489 | 0.0026284 | 4.5211e-06 | 1.385e-06 | 0.015992 | 0.015992 | 0.015992 | 0.97559 | -0.17184 | 0.97603 | -0.16873 | 5.9229
45 | 0.0047489 | 0.0011895 | -0.0047486 | -0.0011895 | 2.964e-07 | 9.5038e-10 | 0.007243 | 0.0072431 | 0.0072431 | 0.97559 | -0.17184 | 0.97553 | -0.1723 | 2.6826
46 | -0.011795 | -0.0029558 | 0.011799 | 0.0029568 | 3.3121e-06 | 1.0687e-06 | 0.017983 | 0.017983 | 0.017983 | 0.97603 | -0.16873 | 0.97631 | -0.1667 | 6.6603
47 | 0.0034642 | 0.00086773 | -0.0034639 | -0.00086785 | 3.494e-07 | -1.1597e-07 | 0.005284 | 0.0052841 | 0.0052841 | 0.97553 | -0.1723 | 0.97543 | -0.17303 | 1.9571
48 | 0.0012844 | 0.00032175 | -0.0012844 | -0.0003219 | 2.9966e-08 | -1.4468e-07 | 0.0019591 | 0.0019592 | 0.0019592 | 0.97553 | -0.1723 | 0.97551 | -0.17246 | 0.72562
49 | -0.013185 | -0.0033038 | 0.013187 | 0.0033044 | 1.7053e-06 | 5.7123e-07 | 0.020096 | 0.020096 | 0.020096 | 0.97631 | -0.1667 | 0.97644 | -0.16577 | 7.4429
50 | 0.0013865 | 0.00034696 | -0.0013864 | -0.00034747 | 1.2335e-07 | -5.0608e-07 | 0.0021131 | 0.0021133 | 0.0021133 | 0.97631 | -0.1667 | 0.97622 | -0.16734 | 0.78269
51 | 0.002542 | 0.00063679 | -0.0025419 | -0.00063686 | 6.9429e-08 | -6.5661e-08 | 0.0038777 | 0.0038777 | 0.0038777 | 0.97543 | -0.17303 | 0.9754 | -0.17322 | 1.4362
52 | -0.013187 | -0.0033044 | 0.013191 | 0.0033058 | 4.3101e-06 | 1.4437e-06 | 0.020096 | 0.020096 | 0.020096 | 0.97644 | -0.16577 | 0.97677 | -0.1634 | 7.4429
53 | 0.001288 | 0.00032261 | -0.001288 | -0.0003228 | 3.9528e-08 | -1.8958e-07 | 0.0019649 | 0.001965 | 0.001965 | 0.9754 | -0.17322 | 0.97537 | -0.17344 | 0.72776
54 | -0.016251 | -0.0040726 | 0.016256 | 0.0040745 | 5.4402e-06 | 1.9143e-06 | 0.024756 | 0.024756 | 0.024756 | 0.97677 | -0.1634 | 0.97711 | -0.16099 | 9.1691
55 | -0.0076664 | -0.001921 | 0.0076666 | 0.001921 | 1.6268e-07 | 3.8414e-08 | 0.011651 | 0.011651 | 0.011651 | 0.97913 | -0.14671 | 0.97915 | -0.14656 | 4.3151
56 | 0.0064662 | 0.0016202 | -0.0064649 | -0.00162 | 1.2744e-06 | 2.2421e-07 | 0.0098267 | 0.0098268 | 0.0098268 | 0.97913 | -0.14671 | 0.97893 | -0.14814 | 3.6396
57 | -0.0093992 | -0.0023553 | 0.0094028 | 0.0023563 | 3.5311e-06 | 1.0091e-06 | 0.014284 | 0.014284 | 0.014284 | 0.97915 | -0.14656 | 0.97953 | -0.14385 | 5.2903
58 | 0.0051927 | 0.0013011 | -0.0051924 | -0.0013011 | 2.4378e-07 | 1.4927e-08 | 0.007893 | 0.007893 | 0.007893 | 0.97893 | -0.14814 | 0.97888 | -0.14848 | 2.9233
59 | -0.011159 | -0.0027964 | 0.011164 | 0.0027979 | 4.8491e-06 | 1.5245e-06 | 0.016951 | 0.016951 | 0.016951 | 0.97953 | -0.14385 | 0.97997 | -0.14071 | 6.2783
60 | 0.0027051 | 0.00067771 | -0.0027049 | -0.00067789 | 2.243e-07 | -1.8095e-07 | 0.004112 | 0.0041121 | 0.0041121 | 0.97888 | -0.14848 | 0.9788 | -0.14908 | 1.523
61 | -0.015918 | -0.0039895 | 0.015927 | 0.0039925 | 8.3987e-06 | 2.9399e-06 | 0.024171 | 0.024171 | 0.024171 | 0.97997 | -0.14071 | 0.9805 | -0.1369 | 8.9521
62 | 0.0017351 | 0.00043485 | -0.0017351 | -0.00043486 | 4.1775e-09 | -1.0486e-08 | 0.0026378 | 0.0026378 | 0.0026378 | 0.9788 | -0.14908 | 0.97879 | -0.14909 | 0.97696
63 | 0.0028791 | 0.00072138 | -0.002879 | -0.0007215 | 1.7499e-07 | -1.1725e-07 | 0.0043735 | 0.0043735 | 0.0043735 | 0.97957 | -0.14335 | 0.97951 | -0.14379 | 1.6198
64 | -0.0048537 | -0.0012162 | 0.0048548 | 0.0012163 | 1.0991e-06 | 1.4715e-08 | 0.0073729 | 0.0073727 | 0.0073729 | 0.97957 | -0.14335 | 0.9798 | -0.14171 | 2.7307
65 | 0.0016909 | 0.00042374 | -0.0016909 | -0.00042378 | 1.3217e-08 | -3.5324e-08 | 0.0025687 | 0.0025687 | 0.0025687 | 0.97951 | -0.14379 | 0.9795 | -0.14385 | 0.95137
66 | 0.028736 | 0.0072092 | -0.028722 | -0.007204 | 1.3885e-05 | 5.1934e-06 | 0.043643 | 0.043643 | 0.043643 | 0.9798 | -0.14171 | 0.97931 | -0.1452 | 16.1642
67 | -0.033591 | -0.0084254 | 0.033653 | 0.0084489 | 6.2368e-05 | 2.3503e-05 | 0.051016 | 0.051016 | 0.051016 | 0.9798 | -0.14171 | 0.98168 | -0.12835 | 18.8948
68 | 0.024965 | 0.0062624 | -0.024958 | -0.0062597 | 7.1315e-06 | 2.643e-06 | 0.037935 | 0.037935 | 0.037935 | 0.97931 | -0.1452 | 0.97903 | -0.14726 | 14.05
69 | -0.035471 | -0.0089046 | 0.035512 | 0.00892 | 4.0801e-05 | 1.5406e-05 | 0.053772 | 0.053772 | 0.053772 | 0.98168 | -0.12835 | 0.98284 | -0.12008 | 19.9154
70 | 0.022439 | 0.0056285 | -0.022426 | -0.0056238 | 1.2941e-05 | 4.7534e-06 | 0.034107 | 0.034107 | 0.034107 | 0.97903 | -0.14726 | 0.97844 | -0.15142 | 12.6322
71 | -0.03726 | -0.009358 | 0.037263 | 0.0093593 | 3.3692e-06 | 1.2743e-06 | 0.056418 | 0.056418 | 0.056418 | 0.98284 | -0.12008 | 0.98294 | -0.11943 | 20.8955
72 | 0.020827 | 0.005223 | -0.020818 | -0.0052196 | 9.5329e-06 | 3.4753e-06 | 0.031675 | 0.031675 | 0.031675 | 0.97844 | -0.15142 | 0.97798 | -0.15472 | 11.7316
73 | -0.04964 | -0.012461 | 0.04976 | 0.012507 | 0.00012031 | 4.584e-05 | 0.075154 | 0.075154 | 0.075154 | 0.98294 | -0.11943 | 0.98539 | -0.10202 | 27.8348
74 | -0.015706 | -0.0039359 | 0.01571 | 0.0039372 | 3.8719e-06 | 1.349e-06 | 0.023733 | 0.023733 | 0.023733 | 0.98474 | -0.10669 | 0.98499 | -0.10491 | 8.7899
75 | 0.0046778 | 0.001172 | -0.0046776 | -0.001172 | 2.1039e-07 | -4.9265e-09 | 0.0070685 | 0.0070685 | 0.0070685 | 0.98474 | -0.10669 | 0.98469 | -0.10701 | 2.618
76 | -0.01606 | -0.004025 | 0.016067 | 0.0040273 | 6.4243e-06 | 2.2482e-06 | 0.024262 | 0.024262 | 0.024262 | 0.98499 | -0.10491 | 0.98539 | -0.10202 | 8.9859
77 | 0.0020293 | 0.00050824 | -0.0020291 | -0.00050854 | 1.7051e-07 | -3.0404e-07 | 0.0030664 | 0.0030665 | 0.0030665 | 0.98469 | -0.10701 | 0.98461 | -0.10762 | 1.1358
78 | -0.065826 | -0.016534 | 0.065837 | 0.016538 | 1.0311e-05 | 3.9443e-06 | 0.099416 | 0.099416 | 0.099416 | 0.98539 | -0.10202 | 0.98555 | -0.10089 | 36.8207
79 | -0.068087 | -0.017102 | 0.068144 | 0.017124 | 5.7715e-05 | 2.2087e-05 | 0.10281 | 0.10281 | 0.10281 | 0.98555 | -0.10089 | 0.98641 | -0.094802 | 38.0788
80 | -0.06872 | -0.017268 | 0.068779 | 0.017291 | 5.9682e-05 | 2.2841e-05 | 0.10368 | 0.10368 | 0.10368 | 0.98641 | -0.094802 | 0.9873 | -0.088567 | 38.4002
81 | -0.11904 | -0.029994 | 0.1191 | 0.030016 | 5.8359e-05 | 2.2292e-05 | 0.17781 | 0.17781 | 0.17781 | 0.99654 | -0.024012 | 0.99704 | -0.02051 | 32.9282
82 | 0.010166 | 0.0025468 | -0.010165 | -0.0025466 | 7.6981e-07 | 2.2821e-07 | 0.015284 | 0.015284 | 0.015284 | 0.98973 | -0.071646 | 0.98965 | -0.072194 | 5.6607
83 | 0.019157 | 0.0048033 | -0.01914 | -0.0047973 | 1.6609e-05 | 5.9952e-06 | 0.029148 | 0.029149 | 0.029149 | 0.97798 | -0.15472 | 0.97711 | -0.16099 | 10.7958
84 | 0.0070831 | 0.0017752 | -0.007083 | -0.0017752 | 8.6608e-08 | 1.7027e-08 | 0.010557 | 0.010557 | 0.010557 | 0.99836 | -0.011426 | 0.99835 | -0.011514 | 3.91
85 | 0.010165 | 0.0025466 | -0.010162 | -0.0025457 | 3.0547e-06 | 9.057e-07 | 0.015284 | 0.015284 | 0.015284 | 0.98965 | -0.072194 | 0.98935 | -0.074366 | 5.6607
86 | 0.0088582 | 0.0022189 | -0.008858 | -0.0022188 | 2.3448e-07 | 6.2998e-08 | 0.013323 | 0.013323 | 0.013323 | 0.98935 | -0.074366 | 0.98932 | -0.074558 | 4.9343

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.24301 | 0.061112

## res_load
| p_mw | q_mvar
0 | 0.0040821 | 0.0010231
1 | 0.0054995 | 0.0013783
2 | 0.0029685 | 0.00074397
3 | 0.0059023 | 0.0014792
4 | 0.0012316 | 0.00030867
5 | 0.0047783 | 0.0011975
6 | 0.0034628 | 0.00086785
7 | 0.0027338 | 0.00068516
8 | 0.0088235 | 0.0022114
9 | 0.0070195 | 0.0017593
10 | 0.0011552 | 0.00028952
11 | 0.00098324 | 0.00024642
12 | 0.003164 | 0.00079296
13 | 0.014196 | 0.0035579
14 | 0.0062648 | 0.0015701
15 | 0.0028694 | 0.00071914
16 | 0.0054262 | 0.0013599
17 | 0.0019008 | 0.00047638
18 | 0.0047582 | 0.0011925
19 | 0.0056665 | 0.0014202
20 | 0.0035048 | 0.00087839
21 | 0.0061023 | 0.0015294
22 | 0.0071373 | 0.0017888
23 | 0.0014456 | 0.00036229
24 | 0.0022316 | 0.0005593
25 | 0.0032234 | 0.00080787
26 | 0.0035046 | 0.00087833
27 | 0.0017162 | 0.00043012
28 | 0.0057359 | 0.0014376
29 | 0.0013061 | 0.00032733
30 | 0.00092193 | 0.00023106
31 | 0.0012844 | 0.0003219
32 | 0.0013864 | 0.00034747
33 | 0.0012539 | 0.00031425
34 | 0.0030595 | 0.00076678
35 | 0.001288 | 0.0003228
36 | 0.0012002 | 0.00030081
37 | 0.0017327 | 0.00043425
38 | 0.0012722 | 0.00031885
39 | 0.0017561 | 0.00044011
40 | 0.0024874 | 0.00062339
41 | 0.0047545 | 0.0011916
42 | 0.00096974 | 0.00024304
43 | 0.003908 | 0.00097943
44 | 0.0017351 | 0.00043486
45 | 0.0019745 | 0.00049486
46 | 0.0011881 | 0.00029776
47 | 0.0016909 | 0.00042378
48 | 0.0037569 | 0.00094157
49 | 0.0018181 | 0.00045566
50 | 0.0025187 | 0.00063124
51 | 0.0017479 | 0.00043807
52 | 0.0015989 | 0.00040073
53 | 0.012377 | 0.0031018
54 | 0.011028 | 0.0027639
55 | 0.00035034 | 8.7802e-05
56 | 0.0026484 | 0.00066374
57 | 0.0020291 | 0.00050854
58 | 0.00225 | 0.0005639
59 | 0.00057523 | 0.00014417
60 | 0.0033881 | 0.00084913
61 | 0.0040887 | 0.0010247
62 | 0.0011634 | 0.00029158
63 | 0.00069327 | 0.00017375
64 | 0.0016608 | 0.00041624
65 | 0.0028841 | 0.00072283
66 | 0.0020084 | 0.00050335
67 | 0.0050403 | 0.0012632
68 | 0.007083 | 0.0017752
69 | 0.00070864 | 0.0001776
70 | 0.001304 | 0.00032681
71 | 0.0029656 | 0.00074324
72 | 0.00066846 | 0.00016753

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1