## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2575-11_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2575-11_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2575-11_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2575-11_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2575-11_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2575-11_0_2_node_27 | 0.4 | n |  | TRUE
6 | bus_LV_2575-11_0_2_node_26 | 0.4 | n |  | TRUE
7 | bus_LV_2575-11_0_2_node_17 | 0.4 | n |  | TRUE
8 | bus_LV_2575-11_0_2_node_21 | 0.4 | n |  | TRUE
9 | bus_LV_2575-11_0_2_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_2575-11_0_2_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_2575-11_0_2_node_33 | 0.4 | n |  | TRUE
12 | bus_LV_2575-11_0_2_node_32 | 0.4 | n |  | TRUE
13 | bus_LV_2575-11_0_2_node_25 | 0.4 | n |  | TRUE
14 | bus_LV_2575-11_0_2_node_30 | 0.4 | n |  | TRUE
15 | bus_LV_2575-11_0_2_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_2575-11_0_2_node_23 | 0.4 | n |  | TRUE
17 | bus_LV_2575-11_0_2_node_8 | 0.4 | n |  | TRUE
18 | bus_LV_2575-11_0_2_node_9 | 0.4 | n |  | TRUE
19 | bus_LV_2575-11_0_2_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_2575-11_0_2_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_2575-11_0_2_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_2575-11_0_2_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_2575-11_0_2_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_2575-11_0_2_node_34 | 0.4 | n |  | TRUE
25 | bus_LV_2575-11_0_2_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_2575-11_0_2_node_18 | 0.4 | n |  | TRUE
27 | bus_LV_2575-11_0_2_node_19 | 0.4 | n |  | TRUE
28 | bus_LV_2575-11_0_2_node_20 | 0.4 | n |  | TRUE
29 | bus_LV_2575-11_0_2_node_22 | 0.4 | n |  | TRUE
30 | bus_LV_2575-11_0_2_node_24 | 0.4 | n |  | TRUE
31 | bus_LV_2575-11_0_2_node_29 | 0.4 | n |  | TRUE
32 | bus_LV_2575-11_0_2_node_28 | 0.4 | n |  | TRUE
33 | bus_LV_2575-11_0_2_node_31 | 0.4 | n |  | TRUE
34 | bus_MV_397_0_node_25 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2575-11_0_2_load_0 | 0 | 0.00074911 | 0.00018775 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2575-11_0_2_load_1 | 1 | 0.00077085 | 0.00019319 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2575-11_0_2_load_3 | 3 | 0.00041817 | 0.0001048 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2575-11_0_2_load_27 | 5 | 0.00091552 | 0.00022945 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2575-11_0_2_load_26 | 6 | 0.00079413 | 0.00019903 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2575-11_0_2_load_17 | 7 | 0.00043439 | 0.00010887 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2575-11_0_2_load_5 | 9 | 0.00068713 | 0.00017221 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2575-11_0_2_load_6 | 10 | 0.002012 | 0.00050425 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2575-11_0_2_load_33 | 11 | 0.0025767 | 0.00064579 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2575-11_0_2_load_32 | 12 | 0.00069082 | 0.00017313 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2575-11_0_2_load_30 | 14 | 0.00027577 | 6.9115e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2575-11_0_2_load_13 | 15 | 0.00044668 | 0.00011195 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2575-11_0_2_load_23 | 16 | 0.0016238 | 0.00040696 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2575-11_0_2_load_8 | 17 | 0.00024083 | 6.0358e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2575-11_0_2_load_9 | 18 | 0.021732 | 0.0054465 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2575-11_0_2_load_11 | 20 | 0.072704 | 0.018221 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2575-11_0_2_load_12 | 21 | 0.00046658 | 0.00011694 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2575-11_0_2_load_15 | 23 | 0.00062714 | 0.00015717 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2575-11_0_2_load_34 | 24 | 0.0036221 | 0.00090778 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2575-11_0_2_load_16 | 25 | 0.00059581 | 0.00014933 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2575-11_0_2_load_18 | 26 | 0.001011 | 0.00025338 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2575-11_0_2_load_19 | 27 | 0.0021171 | 0.00053058 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2575-11_0_2_load_22 | 29 | 0.00089406 | 0.00022407 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2575-11_0_2_load_24 | 30 | 0.00069581 | 0.00017439 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2575-11_0_2_load_28 | 32 | 0.00053626 | 0.0001344 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2575-11_0_2_load_31 | 33 | 0.00058266 | 0.00014603 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 18 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2575-11_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0028033 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2575-11_0_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.014138 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2575-11_0_2_line_2 | NAYY 4x150 SE | 1 | 3 | 0.0057139 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2575-11_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.007856 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2575-11_0_2_line_4 | NAYY 4x150 SE | 3 | 5 | 0.014876 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2575-11_0_2_line_5 | NAYY 4x150 SE | 4 | 6 | 0.032736 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2575-11_0_2_line_6 | NAYY 4x150 SE | 5 | 7 | 0.00045084 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2575-11_0_2_line_7 | NAYY 4x150 SE | 6 | 8 | 0.026851 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2575-11_0_2_line_8 | NAYY 4x150 SE | 7 | 25 | 0.0074709 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2575-11_0_2_line_9 | NAYY 4x150 SE | 8 | 30 | 0.035668 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2575-11_0_2_line_10 | NAYY 4x150 SE | 8 | 27 | 0.030002 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2575-11_0_2_line_11 | NAYY 4x150 SE | 9 | 10 | 0.003168 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2575-11_0_2_line_12 | NAYY 4x150 SE | 10 | 11 | 0.22489 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2575-11_0_2_line_13 | NAYY 4x150 SE | 11 | 12 | 0.012328 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2575-11_0_2_line_14 | NAYY 4x150 SE | 12 | 33 | 0.017468 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2575-11_0_2_line_15 | NAYY 4x150 SE | 13 | 14 | 0.09998 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2575-11_0_2_line_16 | NAYY 4x150 SE | 13 | 15 | 0.021326 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2575-11_0_2_line_17 | NAYY 4x150 SE | 13 | 16 | 0.032408 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2575-11_0_2_line_18 | NAYY 4x150 SE | 14 | 33 | 0.00025665 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2575-11_0_2_line_19 | NAYY 4x150 SE | 16 | 30 | 0.0090382 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2575-11_0_2_line_20 | NAYY 4x150 SE | 17 | 18 | 0.034571 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2575-11_0_2_line_21 | NAYY 4x150 SE | 17 | 19 | 0.02505 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2575-11_0_2_line_22 | NAYY 4x150 SE | 18 | 20 | 0.039925 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2575-11_0_2_line_23 | NAYY 4x150 SE | 19 | 21 | 0.01629 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2575-11_0_2_line_24 | NAYY 4x150 SE | 20 | 22 | 0.0079927 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2575-11_0_2_line_25 | NAYY 4x150 SE | 21 | 23 | 0.0040883 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2575-11_0_2_line_26 | NAYY 4x150 SE | 22 | 24 | 0.10617 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2575-11_0_2_line_27 | NAYY 4x150 SE | 23 | 25 | 0.024193 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2575-11_0_2_line_28 | NAYY 4x150 SE | 26 | 27 | 0.045013 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2575-11_0_2_line_29 | NAYY 4x150 SE | 26 | 28 | 0.040413 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2575-11_0_2_line_30 | NAYY 4x150 SE | 28 | 29 | 0.01524 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2575-11_0_2_line_31 | NAYY 4x150 SE | 29 | 31 | 0.03766 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2575-11_0_2_line_32 | NAYY 4x150 SE | 31 | 32 | 0.049946 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2575-11_0_2_trafo_9 | 0.25 MVA 20/0.4 kV | 34 | 18 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2629637.3808 | 1236965.2519 | 2629634.6168 | 1236964.7839
1 | 2629651.3207 | 1236967.6122 | 2629637.3808 | 1236965.2519
2 | 2629634.6168 | 1236964.7839 | 2629628.9831 | 1236963.83
3 | 2629651.6473 | 1236959.7645 | 2629651.3207 | 1236967.6122
4 | 2629614.3158 | 1236961.3466 | 2629628.9831 | 1236963.83
5 | 2629651.6473 | 1236959.7645 | 2629653.1529 | 1236927.0635
6 | 2629614.3158 | 1236961.3466 | 2629613.8713 | 1236961.2713
7 | 2629654.3879 | 1236900.241 | 2629653.1529 | 1236927.0635
8 | 2629613.8713 | 1236961.2713 | 2629606.5052 | 1236960.0241
9 | 2629654.3879 | 1236900.241 | 2629643.2277 | 1236900.3855 | 2629618.8556 | 1236897.8184
10 | 2629654.3879 | 1236900.241 | 2629655.4598 | 1236870.2578
11 | 2629254.4303 | 1236754.1945 | 2629257.1063 | 1236755.8902
12 | 2629449.2881 | 1236872.6797 | 2629257.1063 | 1236755.8902
13 | 2629449.2881 | 1236872.6797 | 2629452.1535 | 1236873.2864 | 2629461.4592 | 1236874.6053
14 | 2629478.7545 | 1236877.0568 | 2629461.4592 | 1236874.6053
15 | 2629577.637 | 1236893.477 | 2629479.0087 | 1236877.0928
16 | 2629577.637 | 1236893.477 | 2629572.3659 | 1236914.1408
17 | 2629577.637 | 1236893.477 | 2629609.8671 | 1236896.8717
18 | 2629478.7545 | 1236877.0568 | 2629479.0087 | 1236877.0928
19 | 2629618.8556 | 1236897.8184 | 2629609.8671 | 1236896.8717
20 | 2629556.1333 | 1236976.7946 | 2629550.5706 | 1236997.752 | 2629547.7721 | 1237010.3322
21 | 2629562.5597 | 1236952.5834 | 2629556.1333 | 1236976.7946
22 | 2629539.1023 | 1237049.3049 | 2629547.7721 | 1237010.3322
23 | 2629562.5597 | 1236952.5834 | 2629578.6213 | 1236955.3029
24 | 2629534.44 | 1237055.797 | 2629539.1023 | 1237049.3049 | 2629539.1023 | 1237049.3049
25 | 2629578.6213 | 1236955.3029 | 2629582.6522 | 1236955.9854
26 | 2629534.44 | 1237055.797 | 2629590.5892 | 1237145.8988
27 | 2629582.6522 | 1236955.9854 | 2629606.5052 | 1236960.0241
28 | 2629655.4598 | 1236870.2578 | 2629655.6012 | 1236866.3037 | 2629658.2228 | 1236825.3315
29 | 2629660.8034 | 1236785.0012 | 2629658.2228 | 1236825.3315
30 | 2629660.8034 | 1236785.0012 | 2629663.1477 | 1236769.9421
31 | 2629673.8972 | 1236734.0013 | 2629669.9978 | 1236743.699 | 2629666.7994 | 1236752.3996 | 2629664.3989 | 1236761.9047 | 2629663.1477 | 1236769.9421
32 | 2629673.8972 | 1236734.0013 | 2629672.102 | 1236732.9028 | 2629669.9017 | 1236731.1018 | 2629666.001 | 1236727.4023 | 2629662.8994 | 1236724.296 | 2629643.4042 | 1236702.5964 | 2629639.4686 | 1236697.9866

## bus_geodata
| x | y | coords
0 | 2629637.3808 | 1236965.2519
1 | 2629634.6168 | 1236964.7839
2 | 2629651.3207 | 1236967.6122
3 | 2629628.9831 | 1236963.83
4 | 2629651.6473 | 1236959.7645
5 | 2629614.3158 | 1236961.3466
6 | 2629653.1529 | 1236927.0635
7 | 2629613.8713 | 1236961.2713
8 | 2629654.3879 | 1236900.241
9 | 2629254.4303 | 1236754.1945
10 | 2629257.1063 | 1236755.8902
11 | 2629449.2881 | 1236872.6797
12 | 2629461.4591 | 1236874.6053
13 | 2629577.637 | 1236893.477
14 | 2629479.0087 | 1236877.0928
15 | 2629572.3659 | 1236914.1408
16 | 2629609.8671 | 1236896.8717
17 | 2629556.1333 | 1236976.7946
18 | 2629547.7721 | 1237010.3322
19 | 2629562.5597 | 1236952.5834
20 | 2629539.1023 | 1237049.3049
21 | 2629578.6213 | 1236955.3029
22 | 2629534.44 | 1237055.797
23 | 2629582.6522 | 1236955.9854
24 | 2629590.5892 | 1237145.8988
25 | 2629606.5052 | 1236960.0241
26 | 2629658.2228 | 1236825.3315
27 | 2629655.4598 | 1236870.2578
28 | 2629660.8034 | 1236785.0012
29 | 2629663.1477 | 1236769.9421
30 | 2629618.8556 | 1236897.8184
31 | 2629673.8972 | 1236734.0013
32 | 2629639.4686 | 1236697.9866
33 | 2629478.7545 | 1236877.0568
34 | 2629534.44 | 1237055.797

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99629 | -0.026044 | 0.00074911 | 0.00018775
1 | 0.99635 | -0.025599 | 0.00077085 | 0.00019319
2 | 0.99599 | -0.028179 | 0 | 0
3 | 0.99649 | -0.02465 | 0.00041817 | 0.0001048
4 | 0.99582 | -0.029366 | 0 | 0
5 | 0.99685 | -0.022115 | 0.00091552 | 0.00022945
6 | 0.99511 | -0.034316 | 0.00079413 | 0.00019903
7 | 0.99686 | -0.022034 | 0.00043439 | 0.00010887
8 | 0.99457 | -0.038165 | 0 | 0
9 | 0.99152 | -0.059721 | 0.00068713 | 0.00017221
10 | 0.99153 | -0.059699 | 0.002012 | 0.00050425
11 | 0.9924 | -0.053517 | 0.0025767 | 0.00064579
12 | 0.99249 | -0.052856 | 0.00069082 | 0.00017313
13 | 0.99362 | -0.044844 | 0 | 0
14 | 0.99264 | -0.051778 | 0.00027577 | 6.9115e-05
15 | 0.99361 | -0.04494 | 0.00044668 | 0.00011195
16 | 0.99396 | -0.04245 | 0.0016238 | 0.00040696
17 | 0.999 | -0.0069927 | 0.00024083 | 6.0358e-05
18 | 1 | 0 | -0.097729 | -0.024338
19 | 0.99829 | -0.012007 | 0 | 0
20 | 0.99564 | -0.030552 | 0.072704 | 0.018221
21 | 0.99782 | -0.015272 | 0.00046658 | 0.00011694
22 | 0.9956 | -0.030845 | 0 | 0
23 | 0.99771 | -0.016072 | 0.00062714 | 0.00015717
24 | 0.99505 | -0.034724 | 0.0036221 | 0.00090778
25 | 0.99705 | -0.020661 | 0.00059581 | 0.00014933
26 | 0.99422 | -0.040668 | 0.001011 | 0.00025338
27 | 0.99437 | -0.039551 | 0.0021171 | 0.00053058
28 | 0.99413 | -0.041256 | 0 | 0
29 | 0.9941 | -0.041478 | 0.00089406 | 0.00022407
30 | 0.99408 | -0.041634 | 0.00069581 | 0.00017439
31 | 0.99407 | -0.041685 | 0 | 0
32 | 0.99403 | -0.041956 | 0.00053626 | 0.0001344
33 | 0.99264 | -0.051795 | 0.00058266 | 0.00014603
34 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.015737 | -0.0039403 | 0.015738 | 0.0039406 | 9.6629e-07 | 3.3514e-07 | 0.023503 | 0.023503 | 0.023503 | 0.99629 | -0.026044 | 0.99635 | -0.025599 | 8.7049
1 | 0.014988 | 0.0037525 | -0.014984 | -0.003751 | 4.4205e-06 | 1.5161e-06 | 0.022384 | 0.022384 | 0.022384 | 0.99629 | -0.026044 | 0.99599 | -0.028179 | 8.2905
2 | -0.016509 | -0.0041338 | 0.016511 | 0.0041346 | 2.1672e-06 | 7.5912e-07 | 0.024654 | 0.024654 | 0.024654 | 0.99635 | -0.025599 | 0.99649 | -0.02465 | 9.1313
3 | 0.014984 | 0.003751 | -0.014981 | -0.0037502 | 2.4563e-06 | 8.425e-07 | 0.022384 | 0.022384 | 0.022384 | 0.99599 | -0.028179 | 0.99582 | -0.029366 | 8.2905
4 | -0.016929 | -0.0042394 | 0.016935 | 0.0042415 | 5.9318e-06 | 2.0876e-06 | 0.025279 | 0.025279 | 0.025279 | 0.99649 | -0.02465 | 0.99685 | -0.022115 | 9.3625
5 | 0.014981 | 0.0037502 | -0.014971 | -0.0037467 | 1.0235e-05 | 3.5111e-06 | 0.022384 | 0.022385 | 0.022385 | 0.99582 | -0.029366 | 0.99511 | -0.034316 | 8.2906
6 | -0.017851 | -0.0044709 | 0.017851 | 0.004471 | 1.9973e-07 | 7.0942e-08 | 0.026645 | 0.026645 | 0.026645 | 0.99685 | -0.022115 | 0.99686 | -0.022034 | 9.8687
7 | 0.014177 | 0.0035476 | -0.014169 | -0.0035451 | 7.5284e-06 | 2.5469e-06 | 0.021197 | 0.021197 | 0.021197 | 0.99511 | -0.034316 | 0.99457 | -0.038165 | 7.8508
8 | -0.018285 | -0.0045798 | 0.018289 | 0.0045811 | 3.4729e-06 | 1.2383e-06 | 0.027294 | 0.027294 | 0.027294 | 0.99686 | -0.022034 | 0.99705 | -0.020661 | 10.1088
9 | 0.0096096 | 0.0024049 | -0.009605 | -0.0024036 | 4.5999e-06 | 1.3066e-06 | 0.014376 | 0.014376 | 0.014376 | 0.99457 | -0.038165 | 0.99408 | -0.041634 | 5.3245
10 | 0.0045598 | 0.0011402 | -0.0045589 | -0.0011402 | 8.711e-07 | -5.4232e-08 | 0.0068212 | 0.0068213 | 0.0068213 | 0.99457 | -0.038165 | 0.99437 | -0.039551 | 2.5264
11 | -0.00068713 | -0.00017221 | 0.00068713 | 0.00017217 | 2.1021e-09 | -4.0053e-08 | 0.0010312 | 0.0010312 | 0.0010312 | 0.99152 | -0.059721 | 0.99153 | -0.059699 | 0.38193
12 | -0.0026991 | -0.00067642 | 0.0027014 | 0.0006744 | 2.3019e-06 | -2.0178e-06 | 0.0040506 | 0.0040496 | 0.0040506 | 0.99153 | -0.059699 | 0.9924 | -0.053517 | 1.5002
13 | -0.0052781 | -0.0013202 | 0.0052786 | 0.0013202 | 4.8168e-07 | 2.5967e-08 | 0.0079132 | 0.0079131 | 0.0079132 | 0.9924 | -0.053517 | 0.99249 | -0.052856 | 2.9308
14 | -0.0059694 | -0.0014933 | 0.0059703 | 0.0014935 | 8.729e-07 | 1.0995e-07 | 0.0089488 | 0.0089488 | 0.0089488 | 0.99249 | -0.052856 | 0.99264 | -0.051795 | 3.3144
15 | 0.0068353 | 0.0017098 | -0.0068287 | -0.0017086 | 6.5359e-06 | 1.2201e-06 | 0.010235 | 0.010236 | 0.010236 | 0.99362 | -0.044844 | 0.99264 | -0.051778 | 3.791
16 | 0.00044669 | 0.00011168 | -0.00044668 | -0.00011195 | 5.9539e-09 | -2.7393e-07 | 0.00066885 | 0.00066895 | 0.00066895 | 0.99362 | -0.044844 | 0.99361 | -0.04494 | 0.24776
17 | -0.007282 | -0.0018215 | 0.0072844 | 0.001822 | 2.4044e-06 | 5.0485e-07 | 0.010904 | 0.010904 | 0.010904 | 0.99362 | -0.044844 | 0.99396 | -0.04245 | 4.0385
18 | 0.006553 | 0.0016395 | -0.006553 | -0.0016395 | 1.5451e-08 | 2.6247e-09 | 0.0098222 | 0.0098222 | 0.0098222 | 0.99264 | -0.051778 | 0.99264 | -0.051795 | 3.6378
19 | -0.0089082 | -0.002229 | 0.0089092 | 0.0022292 | 1.0028e-06 | 2.6855e-07 | 0.013335 | 0.013335 | 0.013335 | 0.99396 | -0.04245 | 0.99408 | -0.041634 | 4.9388
20 | -0.020256 | -0.0050782 | 0.020276 | 0.0050853 | 1.9639e-05 | 7.1003e-06 | 0.030172 | 0.030172 | 0.030172 | 0.999 | -0.0069927 | 1 | 0 | 11.175
21 | 0.020016 | 0.0050179 | -0.020002 | -0.0050129 | 1.3894e-05 | 5.016e-06 | 0.029814 | 0.029814 | 0.029814 | 0.999 | -0.0069927 | 0.99829 | -0.012007 | 11.0422
22 | 0.076653 | 0.019253 | -0.076329 | -0.019129 | 0.0003242 | 0.00012417 | 0.11408 | 0.11408 | 0.11408 | 1 | 0 | 0.99564 | -0.030552 | 42.2502
23 | 0.020002 | 0.0050129 | -0.019993 | -0.0050096 | 9.0354e-06 | 3.2623e-06 | 0.029814 | 0.029814 | 0.029814 | 0.99829 | -0.012007 | 0.99782 | -0.015272 | 11.0422
24 | 0.0036242 | 0.0009071 | -0.003624 | -0.00090715 | 1.463e-07 | -4.7672e-08 | 0.0054161 | 0.0054161 | 0.0054161 | 0.99564 | -0.030552 | 0.9956 | -0.030845 | 2.006
25 | 0.019526 | 0.0048927 | -0.019524 | -0.0048919 | 2.163e-06 | 7.7852e-07 | 0.029118 | 0.029118 | 0.029118 | 0.99782 | -0.015272 | 0.99771 | -0.016072 | 10.7845
26 | 0.003624 | 0.00090715 | -0.0036221 | -0.00090778 | 1.9435e-06 | -6.3232e-07 | 0.0054161 | 0.0054166 | 0.0054166 | 0.9956 | -0.030845 | 0.99505 | -0.034724 | 2.0061
27 | 0.018897 | 0.0047347 | -0.018885 | -0.0047304 | 1.1991e-05 | 4.296e-06 | 0.028183 | 0.028183 | 0.028183 | 0.99771 | -0.016072 | 0.99705 | -0.020661 | 10.4381
28 | -0.0024415 | -0.00061007 | 0.0024419 | 0.00060963 | 3.749e-07 | -4.3962e-07 | 0.0036535 | 0.0036533 | 0.0036535 | 0.99422 | -0.040668 | 0.99437 | -0.039551 | 1.3531
29 | 0.0014305 | 0.00035669 | -0.0014304 | -0.00035717 | 1.1554e-07 | -4.7959e-07 | 0.0021404 | 0.0021406 | 0.0021406 | 0.99422 | -0.040668 | 0.99413 | -0.041256 | 0.7928
30 | 0.0014304 | 0.00035717 | -0.0014304 | -0.00035735 | 4.3576e-08 | -1.8084e-07 | 0.0021406 | 0.0021406 | 0.0021406 | 0.99413 | -0.041256 | 0.9941 | -0.041478 | 0.79282
31 | 0.00053629 | 0.00013328 | -0.00053628 | -0.00013376 | 1.5132e-08 | -4.8243e-07 | 0.00080235 | 0.00080252 | 0.00080252 | 0.9941 | -0.041478 | 0.99407 | -0.041685 | 0.29723
32 | 0.00053628 | 0.00013376 | -0.00053626 | -0.0001344 | 2.0078e-08 | -6.3976e-07 | 0.00080252 | 0.00080275 | 0.00080275 | 0.99407 | -0.041685 | 0.99403 | -0.041956 | 0.29732

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -4.4415e-16 | -7.6913e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.564e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.11946 | 0.029785

## res_load
| p_mw | q_mvar
0 | 0.00074911 | 0.00018775
1 | 0.00077085 | 0.00019319
2 | 0.00041817 | 0.0001048
3 | 0.00091552 | 0.00022945
4 | 0.00079413 | 0.00019903
5 | 0.00043439 | 0.00010887
6 | 0.00068713 | 0.00017221
7 | 0.002012 | 0.00050425
8 | 0.0025767 | 0.00064579
9 | 0.00069082 | 0.00017313
10 | 0.00027577 | 6.9115e-05
11 | 0.00044668 | 0.00011195
12 | 0.0016238 | 0.00040696
13 | 0.00024083 | 6.0358e-05
14 | 0.021732 | 0.0054465
15 | 0.072704 | 0.018221
16 | 0.00046658 | 0.00011694
17 | 0.00062714 | 0.00015717
18 | 0.0036221 | 0.00090778
19 | 0.00059581 | 0.00014933
20 | 0.001011 | 0.00025338
21 | 0.0021171 | 0.00053058
22 | 0.00089406 | 0.00022407
23 | 0.00069581 | 0.00017439
24 | 0.00053626 | 0.0001344
25 | 0.00058266 | 0.00014603

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1