## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2575-2_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2575-2_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2575-2_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2575-2_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2575-2_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2575-2_0_2_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2575-2_0_2_node_38 | 0.4 | n |  | TRUE
7 | bus_LV_2575-2_0_2_node_58 | 0.4 | n |  | TRUE
8 | bus_LV_2575-2_0_2_node_55 | 0.4 | n |  | TRUE
9 | bus_LV_2575-2_0_2_node_13 | 0.4 | n |  | TRUE
10 | bus_LV_2575-2_0_2_node_39 | 0.4 | n |  | TRUE
11 | bus_LV_2575-2_0_2_node_59 | 0.4 | n |  | TRUE
12 | bus_LV_2575-2_0_2_node_56 | 0.4 | n |  | TRUE
13 | bus_LV_2575-2_0_2_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_2575-2_0_2_node_14 | 0.4 | n |  | TRUE
15 | bus_LV_2575-2_0_2_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_2575-2_0_2_node_15 | 0.4 | n |  | TRUE
17 | bus_LV_2575-2_0_2_node_16 | 0.4 | n |  | TRUE
18 | bus_LV_2575-2_0_2_node_17 | 0.4 | n |  | TRUE
19 | bus_LV_2575-2_0_2_node_18 | 0.4 | n |  | TRUE
20 | bus_LV_2575-2_0_2_node_19 | 0.4 | n |  | TRUE
21 | bus_LV_2575-2_0_2_node_40 | 0.4 | n |  | TRUE
22 | bus_LV_2575-2_0_2_node_37 | 0.4 | n |  | TRUE
23 | bus_LV_2575-2_0_2_node_29 | 0.4 | n |  | TRUE
24 | bus_LV_2575-2_0_2_node_41 | 0.4 | n |  | TRUE
25 | bus_LV_2575-2_0_2_node_62 | 0.4 | n |  | TRUE
26 | bus_LV_2575-2_0_2_node_28 | 0.4 | n |  | TRUE
27 | bus_LV_2575-2_0_2_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_2575-2_0_2_node_21 | 0.4 | n |  | TRUE
29 | bus_LV_2575-2_0_2_node_22 | 0.4 | n |  | TRUE
30 | bus_LV_2575-2_0_2_node_61 | 0.4 | n |  | TRUE
31 | bus_LV_2575-2_0_2_node_23 | 0.4 | n |  | TRUE
32 | bus_LV_2575-2_0_2_node_24 | 0.4 | n |  | TRUE
33 | bus_LV_2575-2_0_2_node_25 | 0.4 | n |  | TRUE
34 | bus_LV_2575-2_0_2_node_26 | 0.4 | n |  | TRUE
35 | bus_LV_2575-2_0_2_node_27 | 0.4 | n |  | TRUE
36 | bus_LV_2575-2_0_2_node_87 | 0.4 | n |  | TRUE
37 | bus_LV_2575-2_0_2_node_53 | 0.4 | n |  | TRUE
38 | bus_LV_2575-2_0_2_node_86 | 0.4 | n |  | TRUE
39 | bus_LV_2575-2_0_2_node_51 | 0.4 | n |  | TRUE
40 | bus_LV_2575-2_0_2_node_30 | 0.4 | n |  | TRUE
41 | bus_LV_2575-2_0_2_node_31 | 0.4 | n |  | TRUE
42 | bus_LV_2575-2_0_2_node_32 | 0.4 | n |  | TRUE
43 | bus_LV_2575-2_0_2_node_63 | 0.4 | n |  | TRUE
44 | bus_LV_2575-2_0_2_node_46 | 0.4 | n |  | TRUE
45 | bus_LV_2575-2_0_2_node_64 | 0.4 | n |  | TRUE
46 | bus_LV_2575-2_0_2_node_65 | 0.4 | n |  | TRUE
47 | bus_LV_2575-2_0_2_node_44 | 0.4 | n |  | TRUE
48 | bus_LV_2575-2_0_2_node_33 | 0.4 | n |  | TRUE
49 | bus_LV_2575-2_0_2_node_34 | 0.4 | n |  | TRUE
50 | bus_LV_2575-2_0_2_node_35 | 0.4 | n |  | TRUE
51 | bus_LV_2575-2_0_2_node_36 | 0.4 | n |  | TRUE
52 | bus_LV_2575-2_0_2_node_68 | 0.4 | n |  | TRUE
53 | bus_LV_2575-2_0_2_node_69 | 0.4 | n |  | TRUE
54 | bus_LV_2575-2_0_2_node_42 | 0.4 | n |  | TRUE
55 | bus_LV_2575-2_0_2_node_49 | 0.4 | n |  | TRUE
56 | bus_LV_2575-2_0_2_node_66 | 0.4 | n |  | TRUE
57 | bus_LV_2575-2_0_2_node_48 | 0.4 | n |  | TRUE
58 | bus_LV_2575-2_0_2_node_90 | 0.4 | n |  | TRUE
59 | bus_LV_2575-2_0_2_node_84 | 0.4 | n |  | TRUE
60 | bus_LV_2575-2_0_2_node_45 | 0.4 | n |  | TRUE
61 | bus_LV_2575-2_0_2_node_47 | 0.4 | n |  | TRUE
62 | bus_LV_2575-2_0_2_node_82 | 0.4 | n |  | TRUE
63 | bus_LV_2575-2_0_2_node_50 | 0.4 | n |  | TRUE
64 | bus_LV_2575-2_0_2_node_52 | 0.4 | n |  | TRUE
65 | bus_LV_2575-2_0_2_node_54 | 0.4 | n |  | TRUE
66 | bus_LV_2575-2_0_2_node_60 | 0.4 | n |  | TRUE
67 | bus_LV_2575-2_0_2_node_57 | 0.4 | n |  | TRUE
68 | bus_LV_2575-2_0_2_node_83 | 0.4 | n |  | TRUE
69 | bus_LV_2575-2_0_2_node_88 | 0.4 | n |  | TRUE
70 | bus_LV_2575-2_0_2_node_94 | 0.4 | n |  | TRUE
71 | bus_LV_2575-2_0_2_node_89 | 0.4 | n |  | TRUE
72 | bus_LV_2575-2_0_2_node_92 | 0.4 | n |  | TRUE
73 | bus_LV_2575-2_0_2_node_77 | 0.4 | n |  | TRUE
74 | bus_LV_2575-2_0_2_node_91 | 0.4 | n |  | TRUE
75 | bus_MV_397_0_node_27 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2575-2_0_2_load_0 | 0 | 0.0016504 | 0.00041364 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2575-2_0_2_load_1 | 1 | 0.0015327 | 0.00038413 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2575-2_0_2_load_3 | 3 | 0.00060627 | 0.00015194 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2575-2_0_2_load_38 | 6 | 0.0023947 | 0.00060017 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2575-2_0_2_load_58 | 7 | 0.0011909 | 0.00029847 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2575-2_0_2_load_55 | 8 | 0.0028626 | 0.00071745 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2575-2_0_2_load_13 | 9 | 0.0050832 | 0.001274 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2575-2_0_2_load_39 | 10 | 0.0027593 | 0.00069154 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2575-2_0_2_load_59 | 11 | 0.0011483 | 0.00028778 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2575-2_0_2_load_56 | 12 | 0.0017897 | 0.00044855 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2575-2_0_2_load_11 | 13 | 0.0020715 | 0.00051917 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2575-2_0_2_load_14 | 14 | 0.0012779 | 0.00032027 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2575-2_0_2_load_12 | 15 | 0.0027338 | 0.00068514 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2575-2_0_2_load_15 | 16 | 0.003165 | 0.00079322 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2575-2_0_2_load_16 | 17 | 0.0011785 | 0.00029536 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2575-2_0_2_load_17 | 18 | 0.0020741 | 0.00051983 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2575-2_0_2_load_18 | 19 | 0.0012642 | 0.00031685 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2575-2_0_2_load_40 | 21 | 0.0017805 | 0.00044623 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2575-2_0_2_load_37 | 22 | 0.0014112 | 0.00035368 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2575-2_0_2_load_29 | 23 | 0.0025446 | 0.00063774 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2575-2_0_2_load_62 | 25 | 0.0020818 | 0.00052174 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2575-2_0_2_load_28 | 26 | 0.001948 | 0.00048821 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2575-2_0_2_load_20 | 27 | 0.0025042 | 0.00062761 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2575-2_0_2_load_21 | 28 | 0.0023801 | 0.0005965 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2575-2_0_2_load_22 | 29 | 0.00099978 | 0.00025057 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2575-2_0_2_load_61 | 30 | 0.0019337 | 0.00048464 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2575-2_0_2_load_23 | 31 | 0.0016418 | 0.00041149 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2575-2_0_2_load_24 | 32 | 0.0015941 | 0.00039951 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2575-2_0_2_load_25 | 33 | 0.0015123 | 0.00037901 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2575-2_0_2_load_26 | 34 | 0.0016413 | 0.00041134 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2575-2_0_2_load_27 | 35 | 0.0016415 | 0.00041139 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2575-2_0_2_load_87 | 36 | 0.0016457 | 0.00041245 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2575-2_0_2_load_53 | 37 | 0.0015908 | 0.0003987 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2575-2_0_2_load_86 | 38 | 0.0022305 | 0.000559 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2575-2_0_2_load_51 | 39 | 0.0032309 | 0.00080974 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2575-2_0_2_load_31 | 41 | 0.0023533 | 0.00058978 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2575-2_0_2_load_32 | 42 | 0.00092787 | 0.00023255 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2575-2_0_2_load_46 | 44 | 0.00090117 | 0.00022586 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2575-2_0_2_load_64 | 45 | 0.002691 | 0.00067442 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2575-2_0_2_load_65 | 46 | 0.00092776 | 0.00023252 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2575-2_0_2_load_44 | 47 | 0.00093135 | 0.00023342 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2575-2_0_2_load_33 | 48 | 0.002104 | 0.0005273 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2575-2_0_2_load_34 | 49 | 0.0036877 | 0.00092423 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2575-2_0_2_load_35 | 50 | 0.00216 | 0.00054134 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2575-2_0_2_load_36 | 51 | 0.0015299 | 0.00038342 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2575-2_0_2_load_68 | 52 | 0.0025781 | 0.00064613 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2575-2_0_2_load_49 | 55 | 0.0007666 | 0.00019213 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2575-2_0_2_load_66 | 56 | 0.0021899 | 0.00054884 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2575-2_0_2_load_48 | 57 | 0.00083057 | 0.00020816 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2575-2_0_2_load_90 | 58 | 0.0052677 | 0.0013202 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2575-2_0_2_load_84 | 59 | 0.0023199 | 0.00058143 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2575-2_0_2_load_45 | 60 | 0.0016456 | 0.00041242 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2575-2_0_2_load_47 | 61 | 0.0015901 | 0.00039851 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2575-2_0_2_load_82 | 62 | 0.0015894 | 0.00039835 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2575-2_0_2_load_50 | 63 | 0.0015927 | 0.00039917 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2575-2_0_2_load_52 | 64 | 0.0016628 | 0.00041675 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2575-2_0_2_load_54 | 65 | 0.0011961 | 0.00029977 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2575-2_0_2_load_60 | 66 | 0.0011501 | 0.00028823 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2575-2_0_2_load_57 | 67 | 0.0043346 | 0.0010863 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2575-2_0_2_load_83 | 68 | 0.0017892 | 0.00044841 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2575-2_0_2_load_88 | 69 | 0.001547 | 0.00038772 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2575-2_0_2_load_94 | 70 | 0.0013553 | 0.00033968 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2575-2_0_2_load_89 | 71 | 0.0032308 | 0.00080972 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2575-2_0_2_load_92 | 72 | 0.0011009 | 0.0002759 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2575-2_0_2_load_77 | 73 | 0.00092695 | 0.00023232 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2575-2_0_2_load_91 | 74 | 0.00089939 | 0.00022541 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 33 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2575-2_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.014279 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2575-2_0_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.0030021 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2575-2_0_2_line_2 | NAYY 4x150 SE | 1 | 3 | 0.10921 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2575-2_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.011394 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2575-2_0_2_line_4 | NAYY 4x150 SE | 2 | 5 | 0.20285 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2575-2_0_2_line_5 | NAYY 4x150 SE | 3 | 6 | 0.0072759 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2575-2_0_2_line_6 | NAYY 4x150 SE | 4 | 7 | 0.027525 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2575-2_0_2_line_7 | NAYY 4x150 SE | 4 | 8 | 0.031921 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2575-2_0_2_line_8 | NAYY 4x150 SE | 5 | 9 | 0.025626 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2575-2_0_2_line_9 | NAYY 4x150 SE | 6 | 10 | 0.013935 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2575-2_0_2_line_10 | NAYY 4x150 SE | 7 | 11 | 0.0018046 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2575-2_0_2_line_11 | NAYY 4x150 SE | 8 | 12 | 0.022337 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2575-2_0_2_line_12 | NAYY 4x150 SE | 9 | 13 | 0.079451 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2575-2_0_2_line_13 | NAYY 4x150 SE | 11 | 66 | 0.00424 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2575-2_0_2_line_14 | NAYY 4x150 SE | 12 | 67 | 0.014552 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2575-2_0_2_line_15 | NAYY 4x150 SE | 13 | 15 | 0.0073959 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2575-2_0_2_line_16 | NAYY 4x150 SE | 14 | 15 | 0.023319 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2575-2_0_2_line_17 | NAYY 4x150 SE | 16 | 17 | 0.019342 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2575-2_0_2_line_18 | NAYY 4x150 SE | 16 | 18 | 0.0014392 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2575-2_0_2_line_19 | NAYY 4x150 SE | 17 | 19 | 0.018458 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2575-2_0_2_line_20 | NAYY 4x150 SE | 18 | 20 | 0.019912 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2575-2_0_2_line_21 | NAYY 4x150 SE | 19 | 21 | 0.0038993 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2575-2_0_2_line_22 | NAYY 4x150 SE | 20 | 22 | 0.015267 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2575-2_0_2_line_23 | NAYY 4x150 SE | 20 | 23 | 0.038121 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2575-2_0_2_line_24 | NAYY 4x150 SE | 21 | 24 | 0.072844 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2575-2_0_2_line_25 | NAYY 4x150 SE | 22 | 25 | 0.018876 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2575-2_0_2_line_26 | NAYY 4x150 SE | 23 | 26 | 0.0054766 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2575-2_0_2_line_27 | NAYY 4x150 SE | 24 | 54 | 0.29381 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2575-2_0_2_line_28 | NAYY 4x150 SE | 25 | 30 | 0.0024947 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2575-2_0_2_line_29 | NAYY 4x150 SE | 26 | 40 | 0.012077 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2575-2_0_2_line_30 | NAYY 4x150 SE | 27 | 28 | 0.0033925 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2575-2_0_2_line_31 | NAYY 4x150 SE | 28 | 29 | 0.010902 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2575-2_0_2_line_32 | NAYY 4x150 SE | 29 | 30 | 0.011491 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2575-2_0_2_line_33 | NAYY 4x150 SE | 31 | 32 | 0.0049068 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2575-2_0_2_line_34 | NAYY 4x150 SE | 31 | 33 | 0.0014897 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2575-2_0_2_line_35 | NAYY 4x150 SE | 32 | 34 | 0.0049123 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2575-2_0_2_line_36 | NAYY 4x150 SE | 33 | 35 | 0.0075202 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2575-2_0_2_line_37 | NAYY 4x150 SE | 34 | 36 | 0.0013745 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2575-2_0_2_line_38 | NAYY 4x150 SE | 35 | 37 | 0.0024124 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_2575-2_0_2_line_39 | NAYY 4x150 SE | 36 | 38 | 0.0036964 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_2575-2_0_2_line_40 | NAYY 4x150 SE | 37 | 39 | 0.00077151 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_2575-2_0_2_line_41 | NAYY 4x150 SE | 38 | 62 | 0.0020004 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_2575-2_0_2_line_42 | NAYY 4x150 SE | 39 | 63 | 0.0034611 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_2575-2_0_2_line_43 | NAYY 4x150 SE | 40 | 41 | 0.015316 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_2575-2_0_2_line_44 | NAYY 4x150 SE | 40 | 42 | 0.022351 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_2575-2_0_2_line_45 | NAYY 4x150 SE | 41 | 43 | 0.014065 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_2575-2_0_2_line_46 | NAYY 4x150 SE | 42 | 44 | 0.0056996 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_2575-2_0_2_line_47 | NAYY 4x150 SE | 43 | 45 | 0.036008 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_2575-2_0_2_line_48 | NAYY 4x150 SE | 43 | 46 | 0.00646 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_2575-2_0_2_line_49 | NAYY 4x150 SE | 44 | 47 | 0.0017781 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_2575-2_0_2_line_50 | NAYY 4x150 SE | 45 | 69 | 0.0011402 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_2575-2_0_2_line_51 | NAYY 4x150 SE | 46 | 70 | 0.0067215 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_2575-2_0_2_line_52 | NAYY 4x150 SE | 47 | 60 | 0.011924 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_2575-2_0_2_line_53 | NAYY 4x150 SE | 48 | 49 | 0.010952 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_2575-2_0_2_line_54 | NAYY 4x150 SE | 48 | 50 | 0.014512 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_2575-2_0_2_line_55 | NAYY 4x150 SE | 49 | 51 | 0.018686 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_2575-2_0_2_line_56 | NAYY 4x150 SE | 51 | 52 | 0.0016206 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_2575-2_0_2_line_57 | NAYY 4x150 SE | 52 | 53 | 0.018758 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_2575-2_0_2_line_58 | NAYY 4x150 SE | 53 | 73 | 0.029018 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_2575-2_0_2_line_59 | NAYY 4x150 SE | 54 | 55 | 0.018849 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_2575-2_0_2_line_60 | NAYY 4x150 SE | 54 | 56 | 0.088332 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_2575-2_0_2_line_61 | NAYY 4x150 SE | 55 | 57 | 0.022853 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_2575-2_0_2_line_62 | NAYY 4x150 SE | 58 | 59 | 0.017385 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_2575-2_0_2_line_63 | NAYY 4x150 SE | 59 | 68 | 0.052251 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_2575-2_0_2_line_64 | NAYY 4x150 SE | 60 | 61 | 0.0017648 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_2575-2_0_2_line_65 | NAYY 4x150 SE | 61 | 62 | 0.005645 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_2575-2_0_2_line_66 | NAYY 4x150 SE | 63 | 64 | 0.0042992 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_2575-2_0_2_line_67 | NAYY 4x150 SE | 64 | 65 | 0.006381 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_2575-2_0_2_line_68 | NAYY 4x150 SE | 65 | 66 | 0.0043008 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_2575-2_0_2_line_69 | NAYY 4x150 SE | 67 | 68 | 0.004234 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_2575-2_0_2_line_70 | NAYY 4x150 SE | 69 | 71 | 0.008479 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_2575-2_0_2_line_71 | NAYY 4x150 SE | 70 | 72 | 0.00074273 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_2575-2_0_2_line_72 | NAYY 4x150 SE | 72 | 74 | 0.0019972 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_2575-2_0_2_line_73 | NAYY 4x150 SE | 73 | 74 | 0.0024514 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2575-2_0_2_trafo_25 | 0.25 MVA 20/0.4 kV | 75 | 33 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12
0 | 2629247.2954 | 1235858.7171 | 2629246.6488 | 1235858.6306 | 2629233.1411 | 1235856.8316
1 | 2629250.271 | 1235859.1154 | 2629247.2954 | 1235858.7171
2 | 2629124.9186 | 1235842.1692 | 2629133.7994 | 1235843.6011 | 2629233.1411 | 1235856.8316
3 | 2629261.6465 | 1235860.2053 | 2629250.271 | 1235859.1154
4 | 2629127.1054 | 1236019.1662 | 2629128.8976 | 1236013.2268 | 2629199.1412 | 1235929.886 | 2629246.8995 | 1235869.2051 | 2629250.271 | 1235859.1154
5 | 2629124.9186 | 1235842.1692 | 2629117.7354 | 1235841.0111
6 | 2629261.6465 | 1235860.2053 | 2629263.6602 | 1235847.7297 | 2629266.6288 | 1235841.1068 | 2629272.1224 | 1235835.8118
7 | 2629261.6465 | 1235860.2053 | 2629265.8359 | 1235860.7707 | 2629293.2801 | 1235864.4816
8 | 2629127.1054 | 1236019.1662 | 2629117.5354 | 1236020.2867 | 2629104.7132 | 1236024.2042 | 2629102.2635 | 1236025.0231
9 | 2629103.9791 | 1235838.7878 | 2629104.0012 | 1235838.7967 | 2629117.7354 | 1235841.0111
10 | 2629272.1224 | 1235835.8118 | 2629273.4217 | 1235834.5594
11 | 2629293.2801 | 1235864.4816 | 2629315.4159 | 1235867.4747
12 | 2629102.2635 | 1236025.0231 | 2629044.5949 | 1236044.3007 | 2629038.5936 | 1236047.5846 | 2629031.9182 | 1236052.5217 | 2629029.7957 | 1236055.3066
13 | 2629276.4745 | 1235831.617 | 2629273.4217 | 1235834.5594
14 | 2629329.8368 | 1235869.4247 | 2629315.4159 | 1235867.4747
15 | 2629025.3125 | 1236061.1887 | 2629029.7957 | 1236055.3066
16 | 2629025.3125 | 1236061.1887 | 2629011.1768 | 1236079.7353
17 | 2629407.236 | 1235809.7269 | 2629422.3881 | 1235821.749
18 | 2629406.1086 | 1235808.8324 | 2629407.236 | 1235809.7269
19 | 2629436.8476 | 1235833.2217 | 2629422.3881 | 1235821.749
20 | 2629390.5105 | 1235796.4563 | 2629406.1086 | 1235808.8324
21 | 2629439.9023 | 1235835.6453 | 2629436.8476 | 1235833.2217
22 | 2629390.5105 | 1235796.4563 | 2629380.2126 | 1235807.7273
23 | 2629390.5105 | 1235796.4563 | 2629361.9188 | 1235771.2428
24 | 2629499.4455 | 1235877.579 | 2629478.9646 | 1235863.2353 | 2629451.785 | 1235844.6558 | 2629445.9112 | 1235840.413 | 2629439.9023 | 1235835.6453
25 | 2629380.2126 | 1235807.7273 | 2629367.4802 | 1235821.6628
26 | 2629357.4653 | 1235768.1369 | 2629359.5745 | 1235769.1756 | 2629361.9188 | 1235771.2428
27 | 2629498.989 | 1235788.0767 | 2629501.498 | 1235788.734 | 2629506.205 | 1235791.737 | 2629517.6691 | 1235800.8995 | 2629551.7151 | 1235831.0539 | 2629570.9848 | 1235850.0503 | 2629588.1994 | 1235868.4028 | 2629593.5092 | 1235876.4453 | 2629596.147 | 1235884.6747 | 2629596.7297 | 1235892.2712 | 2629594.9972 | 1235899.8006 | 2629588.4272 | 1235933.6334 | 2629499.4455 | 1235877.579
28 | 2629365.7975 | 1235823.5045 | 2629367.4802 | 1235821.6628
29 | 2629346.0901 | 1235764.5173 | 2629351.9578 | 1235765.4246 | 2629357.4653 | 1235768.1369
30 | 2629350.6936 | 1235840.0356 | 2629348.4053 | 1235842.5402
31 | 2629350.6936 | 1235840.0356 | 2629358.0469 | 1235831.9875
32 | 2629365.7975 | 1235823.5045 | 2629358.0469 | 1235831.9875
33 | 2629298.5322 | 1235810.3565 | 2629302.065 | 1235806.9513
34 | 2629297.4596 | 1235811.3903 | 2629298.5322 | 1235810.3565
35 | 2629305.6019 | 1235803.5423 | 2629302.065 | 1235806.9513
36 | 2629297.4596 | 1235811.3903 | 2629292.0451 | 1235816.6091
37 | 2629305.6019 | 1235803.5423 | 2629306.5915 | 1235802.5884
38 | 2629292.0451 | 1235816.6091 | 2629290.3082 | 1235818.2832
39 | 2629309.2529 | 1235800.0232 | 2629306.5915 | 1235802.5884
40 | 2629290.3082 | 1235818.2832 | 2629289.7527 | 1235818.8186
41 | 2629309.2529 | 1235800.0232 | 2629310.6932 | 1235798.635
42 | 2629287.2607 | 1235821.2206 | 2629289.7527 | 1235818.8186
43 | 2629346.0901 | 1235764.5173 | 2629347.2242 | 1235758.597 | 2629345.8578 | 1235754.8546 | 2629342.1758 | 1235751.0369
44 | 2629346.0901 | 1235764.5173 | 2629329.9974 | 1235780.0285
45 | 2629332.4116 | 1235740.913 | 2629342.1758 | 1235751.0369
46 | 2629329.9974 | 1235780.0285 | 2629325.8937 | 1235783.9838
47 | 2629332.4116 | 1235740.913 | 2629357.1034 | 1235714.7037
48 | 2629332.4116 | 1235740.913 | 2629327.8285 | 1235736.3603
49 | 2629324.6135 | 1235785.2178 | 2629325.8937 | 1235783.9838
50 | 2629357.1034 | 1235714.7037 | 2629357.8852 | 1235713.8738
51 | 2629327.8285 | 1235736.3603 | 2629323.0598 | 1235731.6234
52 | 2629324.6135 | 1235785.2178 | 2629316.0282 | 1235793.4928
53 | 2629324.4922 | 1235678.8243 | 2629317.2096 | 1235670.6451
54 | 2629307.5595 | 1235659.8069 | 2629317.2096 | 1235670.6451
55 | 2629313.0664 | 1235692.9748 | 2629324.0919 | 1235681.7464 | 2629324.4922 | 1235678.8243 | 2629324.4922 | 1235678.8243
56 | 2629313.0664 | 1235692.9748 | 2629311.931 | 1235694.1312
57 | 2629298.7886 | 1235707.5155 | 2629311.931 | 1235694.1312
58 | 2629298.7886 | 1235707.5155 | 2629311.7936 | 1235720.432 | 2629319.3768 | 1235727.9648
59 | 2629498.989 | 1235788.0767 | 2629496.0987 | 1235791.042 | 2629490.6633 | 1235796.0627 | 2629485.9683 | 1235801.6637
60 | 2629498.989 | 1235788.0767 | 2629496.5035 | 1235787.2417 | 2629482.404 | 1235787.6387 | 2629474.5007 | 1235786.7435 | 2629468.8021 | 1235785.3366 | 2629462.447 | 1235782.0142 | 2629457.3986 | 1235777.6531 | 2629428.7308 | 1235744.355
61 | 2629471.2874 | 1235819.1777 | 2629485.9683 | 1235801.6637
62 | 2629396.4058 | 1235898.144 | 2629383.9415 | 1235888.4921 | 2629382.5666 | 1235887.6338
63 | 2629334.0275 | 1235870.024 | 2629354.261 | 1235873.7142 | 2629370.0836 | 1235879.8406 | 2629382.5666 | 1235887.6338
64 | 2629316.0282 | 1235793.4928 | 2629314.7576 | 1235794.7175
65 | 2629314.7576 | 1235794.7175 | 2629310.6932 | 1235798.635
66 | 2629287.2607 | 1235821.2206 | 2629284.1653 | 1235824.2041
67 | 2629284.1653 | 1235824.2041 | 2629279.571 | 1235828.6324
68 | 2629279.571 | 1235828.6324 | 2629276.4745 | 1235831.617
69 | 2629329.8368 | 1235869.4247 | 2629333.3343 | 1235869.8976 | 2629334.0275 | 1235870.024
70 | 2629363.6995 | 1235707.7022 | 2629357.8852 | 1235713.8738
71 | 2629322.5329 | 1235731.1 | 2629323.0598 | 1235731.6234
72 | 2629322.5329 | 1235731.1 | 2629321.116 | 1235729.6925
73 | 2629319.3768 | 1235727.9648 | 2629321.116 | 1235729.6925

## bus_geodata
| x | y | coords
0 | 2629247.2954 | 1235858.7171
1 | 2629233.1411 | 1235856.8316
2 | 2629250.271 | 1235859.1154
3 | 2629124.9186 | 1235842.1692
4 | 2629261.6465 | 1235860.2053
5 | 2629127.1054 | 1236019.1662
6 | 2629117.7354 | 1235841.0111
7 | 2629272.1224 | 1235835.8118
8 | 2629293.2801 | 1235864.4816
9 | 2629102.2635 | 1236025.0231
10 | 2629103.9791 | 1235838.7878
11 | 2629273.4217 | 1235834.5594
12 | 2629315.4159 | 1235867.4747
13 | 2629029.7957 | 1236055.3066
14 | 2629011.1768 | 1236079.7353
15 | 2629025.3125 | 1236061.1887
16 | 2629407.236 | 1235809.7269
17 | 2629422.3881 | 1235821.749
18 | 2629406.1086 | 1235808.8324
19 | 2629436.8476 | 1235833.2217
20 | 2629390.5105 | 1235796.4563
21 | 2629439.9023 | 1235835.6453
22 | 2629380.2126 | 1235807.7273
23 | 2629361.9188 | 1235771.2428
24 | 2629499.4455 | 1235877.579
25 | 2629367.4802 | 1235821.6628
26 | 2629357.4653 | 1235768.1369
27 | 2629348.4053 | 1235842.5402
28 | 2629350.6936 | 1235840.0356
29 | 2629358.0469 | 1235831.9875
30 | 2629365.7975 | 1235823.5045
31 | 2629298.5322 | 1235810.3565
32 | 2629302.065 | 1235806.9513
33 | 2629297.4596 | 1235811.3903
34 | 2629305.6019 | 1235803.5423
35 | 2629292.0451 | 1235816.6091
36 | 2629306.5915 | 1235802.5884
37 | 2629290.3082 | 1235818.2832
38 | 2629309.2529 | 1235800.0232
39 | 2629289.7527 | 1235818.8186
40 | 2629346.0901 | 1235764.5173
41 | 2629342.1758 | 1235751.0369
42 | 2629329.9974 | 1235780.0285
43 | 2629332.4116 | 1235740.913
44 | 2629325.8937 | 1235783.9838
45 | 2629357.1034 | 1235714.7037
46 | 2629327.8285 | 1235736.3603
47 | 2629324.6135 | 1235785.2178
48 | 2629317.2096 | 1235670.6451
49 | 2629324.4922 | 1235678.8243
50 | 2629307.5595 | 1235659.8069
51 | 2629313.0664 | 1235692.9748
52 | 2629311.931 | 1235694.1312
53 | 2629298.7886 | 1235707.5155
54 | 2629498.989 | 1235788.0767
55 | 2629485.9683 | 1235801.6637
56 | 2629428.7308 | 1235744.355
57 | 2629471.2874 | 1235819.1777
58 | 2629396.4058 | 1235898.144
59 | 2629382.5666 | 1235887.6338
60 | 2629316.0282 | 1235793.4928
61 | 2629314.7576 | 1235794.7175
62 | 2629310.6932 | 1235798.635
63 | 2629287.2607 | 1235821.2206
64 | 2629284.1653 | 1235824.2041
65 | 2629279.571 | 1235828.6324
66 | 2629276.4745 | 1235831.617
67 | 2629329.8368 | 1235869.4247
68 | 2629334.0275 | 1235870.024
69 | 2629357.8852 | 1235713.8738
70 | 2629323.0598 | 1235731.6234
71 | 2629363.6995 | 1235707.7022
72 | 2629322.5329 | 1235731.1
73 | 2629319.3768 | 1235727.9648
74 | 2629321.116 | 1235729.6925
75 | 2629261.6465 | 1235860.2053

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9958 | -0.029396 | 0.0016504 | 0.00041364
1 | 0.99565 | -0.030446 | 0.0015327 | 0.00038413
2 | 0.99584 | -0.029125 | 0 | 0
3 | 0.99475 | -0.036793 | 0.00060627 | 0.00015194
4 | 0.99617 | -0.026814 | 0 | 0
5 | 0.99259 | -0.052043 | 0 | 0
6 | 0.9947 | -0.037172 | 0.0023947 | 0.00060017
7 | 0.99769 | -0.016163 | 0.0011909 | 0.00029847
8 | 0.99533 | -0.032719 | 0.0028626 | 0.00071745
9 | 0.99217 | -0.054945 | 0.0050832 | 0.001274
10 | 0.99464 | -0.03756 | 0.0027593 | 0.00069154
11 | 0.99779 | -0.015444 | 0.0011483 | 0.00028778
12 | 0.99483 | -0.036211 | 0.0017897 | 0.00044855
13 | 0.99148 | -0.059854 | 0.0020715 | 0.00051917
14 | 0.99139 | -0.060459 | 0.0012779 | 0.00032027
15 | 0.99144 | -0.060156 | 0.0027338 | 0.00068514
16 | 0.99164 | -0.058667 | 0.003165 | 0.00079322
17 | 0.99142 | -0.06025 | 0.0011785 | 0.00029536
18 | 0.99166 | -0.058503 | 0.0020741 | 0.00051983
19 | 0.99123 | -0.06154 | 0.0012642 | 0.00031685
20 | 0.99204 | -0.055816 | 0 | 0
21 | 0.9912 | -0.061763 | 0.0017805 | 0.00044623
22 | 0.99179 | -0.057569 | 0.0014112 | 0.00035368
23 | 0.99339 | -0.046311 | 0.0025446 | 0.00063774
24 | 0.99081 | -0.064599 | 0 | 0
25 | 0.99152 | -0.059466 | 0.0020818 | 0.00052174
26 | 0.9936 | -0.044806 | 0.001948 | 0.00048821
27 | 0.99131 | -0.060978 | 0.0025042 | 0.00062761
28 | 0.99132 | -0.060892 | 0.0023801 | 0.0005965
29 | 0.9914 | -0.060351 | 0.00099978 | 0.00025057
30 | 0.9915 | -0.059664 | 0.0019337 | 0.00048464
31 | 0.99985 | -0.0010791 | 0.0016418 | 0.00041149
32 | 0.99935 | -0.0045555 | 0.0015941 | 0.00039951
33 | 1 | 0 | -0.12689 | -0.031677
34 | 0.99886 | -0.0079609 | 0.0016413 | 0.00041134
35 | 0.99943 | -0.003976 | 0.0016415 | 0.00041139
36 | 0.99872 | -0.0088918 | 0.0016457 | 0.00041245
37 | 0.99925 | -0.0052128 | 0.0015908 | 0.0003987
38 | 0.99837 | -0.011336 | 0.0022305 | 0.000559
39 | 0.9992 | -0.0055962 | 0.0032309 | 0.00080974
40 | 0.99411 | -0.041253 | 0 | 0
41 | 0.99351 | -0.045449 | 0.0023533 | 0.00058978
42 | 0.99591 | -0.028584 | 0.00092787 | 0.00023255
43 | 0.99301 | -0.048971 | 0 | 0
44 | 0.99638 | -0.025307 | 0.00090117 | 0.00022586
45 | 0.99262 | -0.051695 | 0.002691 | 0.00067442
46 | 0.99285 | -0.050101 | 0.00092776 | 0.00023252
47 | 0.99652 | -0.02427 | 0.00093135 | 0.00023342
48 | 0.99146 | -0.059914 | 0.002104 | 0.0005273
49 | 0.99153 | -0.05944 | 0.0036877 | 0.00092423
50 | 0.99141 | -0.060233 | 0.00216 | 0.00054134
51 | 0.99174 | -0.057931 | 0.0015299 | 0.00038342
52 | 0.99176 | -0.057775 | 0.0025781 | 0.00064613
53 | 0.99209 | -0.05548 | 0 | 0
54 | 0.9892 | -0.076008 | 0 | 0
55 | 0.98916 | -0.076316 | 0.0007666 | 0.00019213
56 | 0.98892 | -0.077986 | 0.0021899 | 0.00054884
57 | 0.98913 | -0.07651 | 0.00083057 | 0.00020816
58 | 0.99379 | -0.043556 | 0.0052677 | 0.0013202
59 | 0.99392 | -0.042631 | 0.0023199 | 0.00058143
60 | 0.99753 | -0.017208 | 0.0016456 | 0.00041242
61 | 0.99769 | -0.016134 | 0.0015901 | 0.00039851
62 | 0.99819 | -0.012614 | 0.0015894 | 0.00039835
63 | 0.99897 | -0.0072047 | 0.0015927 | 0.00039917
64 | 0.99869 | -0.0091353 | 0.0016628 | 0.00041675
65 | 0.9983 | -0.011896 | 0.0011961 | 0.00029977
66 | 0.99804 | -0.013707 | 0.0011501 | 0.00028823
67 | 0.99455 | -0.038225 | 0.0043346 | 0.0010863
68 | 0.99449 | -0.038626 | 0.0017892 | 0.00044841
69 | 0.99262 | -0.051751 | 0.001547 | 0.00038772
70 | 0.99269 | -0.051214 | 0.0013553 | 0.00033968
71 | 0.99258 | -0.052028 | 0.0032308 | 0.00080972
72 | 0.99268 | -0.051327 | 0.0011009 | 0.0002759
73 | 0.99259 | -0.051931 | 0.00092695 | 0.00023232
74 | 0.99264 | -0.051608 | 0.00089939 | 0.00022541
75 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0072995 | 0.0018284 | -0.0072984 | -0.0018282 | 1.06e-06 | 2.2197e-07 | 0.010907 | 0.010907 | 0.010907 | 0.9958 | -0.029396 | 0.99565 | -0.030446 | 4.0397
1 | -0.0089499 | -0.0022421 | 0.0089503 | 0.0022421 | 3.3504e-07 | 8.9805e-08 | 0.013373 | 0.013373 | 0.013373 | 0.9958 | -0.029396 | 0.99584 | -0.029125 | 4.9531
2 | 0.0057657 | 0.0014441 | -0.0057607 | -0.0014435 | 5.0601e-06 | 5.2711e-07 | 0.0086166 | 0.0086171 | 0.0086171 | 0.99565 | -0.030446 | 0.99475 | -0.036793 | 3.1915
3 | -0.020161 | -0.0050534 | 0.020167 | 0.0050557 | 6.4524e-06 | 2.3334e-06 | 0.030125 | 0.030125 | 0.030125 | 0.99584 | -0.029125 | 0.99617 | -0.026814 | 11.1575
4 | 0.011211 | 0.0028112 | -0.011175 | -0.0028002 | 3.5524e-05 | 1.1032e-05 | 0.016752 | 0.016753 | 0.016753 | 0.99584 | -0.029125 | 0.99259 | -0.052043 | 6.2048
5 | 0.0051544 | 0.0012916 | -0.0051541 | -0.0012916 | 2.699e-07 | 9.3586e-09 | 0.0077102 | 0.0077103 | 0.0077103 | 0.99475 | -0.036793 | 0.9947 | -0.037172 | 2.8556
6 | -0.038563 | -0.0096685 | 0.03862 | 0.00969 | 5.6993e-05 | 2.1561e-05 | 0.057604 | 0.057604 | 0.057604 | 0.99617 | -0.026814 | 0.99769 | -0.016163 | 21.3349
7 | 0.018396 | 0.0046128 | -0.018381 | -0.0046074 | 1.5041e-05 | 5.3697e-06 | 0.027479 | 0.027479 | 0.027479 | 0.99617 | -0.026814 | 0.99533 | -0.032719 | 10.1775
8 | 0.011175 | 0.0028002 | -0.011171 | -0.0027988 | 4.4879e-06 | 1.395e-06 | 0.016753 | 0.016753 | 0.016753 | 0.99259 | -0.052043 | 0.99217 | -0.054945 | 6.2048
9 | 0.0027594 | 0.00069141 | -0.0027593 | -0.00069154 | 1.4817e-07 | -1.2389e-07 | 0.0041279 | 0.004128 | 0.004128 | 0.9947 | -0.037172 | 0.99464 | -0.03756 | 1.5289
10 | -0.039811 | -0.0099885 | 0.039815 | 0.00999 | 3.9706e-06 | 1.5036e-06 | 0.05938 | 0.05938 | 0.05938 | 0.99769 | -0.016163 | 0.99779 | -0.015444 | 21.9927
11 | 0.015518 | 0.0038899 | -0.01551 | -0.0038874 | 7.5019e-06 | 2.5952e-06 | 0.023199 | 0.0232 | 0.0232 | 0.99533 | -0.032719 | 0.99483 | -0.036211 | 8.5924
12 | 0.0060875 | 0.0015248 | -0.0060834 | -0.0015243 | 4.1323e-06 | 5.6397e-07 | 0.0091295 | 0.0091298 | 0.0091298 | 0.99217 | -0.054945 | 0.99148 | -0.059854 | 3.3814
13 | -0.040963 | -0.010278 | 0.040973 | 0.010282 | 9.8747e-06 | 3.7426e-06 | 0.061093 | 0.061093 | 0.061093 | 0.99779 | -0.015444 | 0.99804 | -0.013707 | 22.6269
14 | 0.013721 | 0.0034388 | -0.013717 | -0.0034375 | 3.8245e-06 | 1.2821e-06 | 0.020523 | 0.020523 | 0.020523 | 0.99483 | -0.036211 | 0.99455 | -0.038225 | 7.601
15 | 0.0040119 | 0.0010051 | -0.0040117 | -0.0010051 | 1.673e-07 | -3.1031e-08 | 0.0060209 | 0.0060209 | 0.0060209 | 0.99148 | -0.059854 | 0.99144 | -0.060156 | 2.23
16 | -0.0012779 | -0.00032027 | 0.0012779 | 0.00031999 | 5.3529e-08 | -2.8012e-07 | 0.001918 | 0.0019179 | 0.001918 | 0.99139 | -0.060459 | 0.99144 | -0.060156 | 0.71038
17 | 0.0080215 | 0.002005 | -0.0080198 | -0.0020045 | 1.7481e-06 | 4.2289e-07 | 0.012035 | 0.012035 | 0.012035 | 0.99164 | -0.058667 | 0.99142 | -0.06025 | 4.4574
18 | -0.011187 | -0.0027982 | 0.011187 | 0.0027983 | 2.5299e-07 | 7.8736e-08 | 0.016784 | 0.016784 | 0.016784 | 0.99164 | -0.058667 | 0.99166 | -0.058503 | 6.2164
19 | 0.0068413 | 0.0017092 | -0.0068401 | -0.001709 | 1.2139e-06 | 2.2892e-07 | 0.010266 | 0.010266 | 0.010266 | 0.99142 | -0.06025 | 0.99123 | -0.06154 | 3.8023
20 | -0.013261 | -0.0033181 | 0.013266 | 0.0033197 | 4.9186e-06 | 1.6348e-06 | 0.019896 | 0.019896 | 0.019896 | 0.99166 | -0.058503 | 0.99204 | -0.055816 | 7.3691
21 | 0.0055758 | 0.0013921 | -0.0055756 | -0.0013921 | 1.704e-07 | 1.5275e-08 | 0.0083684 | 0.0083684 | 0.0083684 | 0.99123 | -0.06154 | 0.9912 | -0.061763 | 3.0994
22 | 0.011317 | 0.0028364 | -0.011315 | -0.0028356 | 2.7452e-06 | 8.5879e-07 | 0.016975 | 0.016975 | 0.016975 | 0.99204 | -0.055816 | 0.99179 | -0.057569 | 6.2872
23 | -0.024583 | -0.0061562 | 0.024615 | 0.0061681 | 3.2339e-05 | 1.1945e-05 | 0.036872 | 0.036872 | 0.036872 | 0.99204 | -0.055816 | 0.99339 | -0.046311 | 13.6562
24 | 0.0037952 | 0.00094586 | -0.0037937 | -0.00094623 | 1.4746e-06 | -3.7139e-07 | 0.0056955 | 0.0056959 | 0.0056959 | 0.9912 | -0.061763 | 0.99081 | -0.064599 | 2.1096
25 | 0.0099033 | 0.0024819 | -0.0099007 | -0.0024811 | 2.6004e-06 | 7.5661e-07 | 0.014858 | 0.014858 | 0.014858 | 0.99179 | -0.057569 | 0.99152 | -0.059466 | 5.5031
26 | -0.02716 | -0.0068058 | 0.027166 | 0.0068079 | 5.6562e-06 | 2.1045e-06 | 0.040683 | 0.040683 | 0.040683 | 0.99339 | -0.046311 | 0.9936 | -0.044806 | 15.0678
27 | 0.0037937 | 0.00094623 | -0.0037878 | -0.00094772 | 5.9494e-06 | -1.4897e-06 | 0.0056959 | 0.0056972 | 0.0056972 | 0.99081 | -0.064599 | 0.9892 | -0.076008 | 2.1101
28 | 0.0078189 | 0.0019594 | -0.0078187 | -0.0019593 | 2.1434e-07 | 5.0262e-08 | 0.011734 | 0.011734 | 0.011734 | 0.99152 | -0.059466 | 0.9915 | -0.059664 | 4.346
29 | -0.029114 | -0.0072962 | 0.029128 | 0.0073015 | 1.4325e-05 | 5.3533e-06 | 0.0436 | 0.0436 | 0.0436 | 0.9936 | -0.044806 | 0.99411 | -0.041253 | 16.1483
30 | -0.0025042 | -0.00062761 | 0.0025042 | 0.00062758 | 2.9911e-08 | -3.2233e-08 | 0.0037589 | 0.0037589 | 0.0037589 | 0.99131 | -0.060978 | 0.99132 | -0.060892 | 1.3922
31 | -0.0048843 | -0.0012241 | 0.0048847 | 0.0012241 | 3.6564e-07 | 7.1076e-11 | 0.0073315 | 0.0073314 | 0.0073315 | 0.99132 | -0.060892 | 0.9914 | -0.060351 | 2.7154
32 | -0.0058844 | -0.0014746 | 0.005885 | 0.0014747 | 5.593e-07 | 6.6935e-08 | 0.008832 | 0.008832 | 0.008832 | 0.9914 | -0.060351 | 0.9915 | -0.059664 | 3.2711
33 | 0.071308 | 0.017922 | -0.071273 | -0.017909 | 3.4494e-05 | 1.3203e-05 | 0.10614 | 0.10614 | 0.10614 | 0.99985 | -0.0010791 | 0.99935 | -0.0045555 | 39.3116
34 | -0.07295 | -0.018333 | 0.072961 | 0.018338 | 1.096e-05 | 4.1959e-06 | 0.10858 | 0.10858 | 0.10858 | 0.99985 | -0.0010791 | 1 | 0 | 40.2166
35 | 0.069679 | 0.017509 | -0.069646 | -0.017497 | 3.3006e-05 | 1.263e-05 | 0.10377 | 0.10377 | 0.10377 | 0.99935 | -0.0045555 | 0.99886 | -0.0079609 | 38.4325
36 | 0.053128 | 0.01334 | -0.053099 | -0.013329 | 2.9334e-05 | 1.1184e-05 | 0.079064 | 0.079065 | 0.079065 | 1 | 0 | 0.99943 | -0.003976 | 29.2832
37 | 0.068005 | 0.017085 | -0.067996 | -0.017082 | 8.8052e-06 | 3.3686e-06 | 0.10132 | 0.10132 | 0.10132 | 0.99886 | -0.0079609 | 0.99872 | -0.0088918 | 37.527
38 | 0.051458 | 0.012917 | -0.051449 | -0.012914 | 8.8372e-06 | 3.3673e-06 | 0.076621 | 0.076621 | 0.076621 | 0.99943 | -0.003976 | 0.99925 | -0.0052128 | 28.378
39 | 0.06635 | 0.016669 | -0.066328 | -0.016661 | 2.2548e-05 | 8.6238e-06 | 0.098871 | 0.098871 | 0.098871 | 0.99872 | -0.0088918 | 0.99837 | -0.011336 | 36.6188
40 | 0.049858 | 0.012515 | -0.049855 | -0.012514 | 2.6542e-06 | 1.0108e-06 | 0.074252 | 0.074252 | 0.074252 | 0.99925 | -0.0052128 | 0.9992 | -0.0055962 | 27.5006
41 | 0.064097 | 0.016102 | -0.064086 | -0.016097 | 1.1396e-05 | 4.3568e-06 | 0.095546 | 0.095546 | 0.095546 | 0.99837 | -0.011336 | 0.99819 | -0.012614 | 35.3876
42 | 0.046624 | 0.011704 | -0.046614 | -0.0117 | 1.0414e-05 | 3.9601e-06 | 0.06944 | 0.06944 | 0.06944 | 0.9992 | -0.0055962 | 0.99897 | -0.0072047 | 25.7186
43 | 0.027141 | 0.0068065 | -0.027126 | -0.0068006 | 1.5775e-05 | 5.869e-06 | 0.040628 | 0.040628 | 0.040628 | 0.99411 | -0.041253 | 0.99351 | -0.045449 | 15.0474
44 | -0.056269 | -0.014108 | 0.056368 | 0.014146 | 9.8946e-05 | 3.7766e-05 | 0.084228 | 0.084228 | 0.084228 | 0.99411 | -0.041253 | 0.99591 | -0.028584 | 31.1956
45 | 0.024772 | 0.0062108 | -0.02476 | -0.0062064 | 1.2083e-05 | 4.4651e-06 | 0.037103 | 0.037103 | 0.037103 | 0.99351 | -0.045449 | 0.99301 | -0.048971 | 13.742
46 | -0.057296 | -0.014378 | 0.057322 | 0.014388 | 2.6069e-05 | 9.9523e-06 | 0.085614 | 0.085614 | 0.085614 | 0.99591 | -0.028584 | 0.99638 | -0.025307 | 31.7091
47 | 0.0074718 | 0.0018724 | -0.007469 | -0.0018718 | 2.8168e-06 | 6.1773e-07 | 0.011196 | 0.011197 | 0.011197 | 0.99301 | -0.048971 | 0.99262 | -0.051695 | 4.1469
48 | 0.017289 | 0.0043339 | -0.017286 | -0.004333 | 2.7055e-06 | 9.5703e-07 | 0.025907 | 0.025907 | 0.025907 | 0.99301 | -0.048971 | 0.99285 | -0.050101 | 9.5952
49 | -0.058223 | -0.014614 | 0.058232 | 0.014617 | 8.3904e-06 | 3.2039e-06 | 0.08696 | 0.08696 | 0.08696 | 0.99638 | -0.025307 | 0.99652 | -0.02427 | 32.2075
50 | 0.004778 | 0.0011974 | -0.004778 | -0.0011974 | 3.65e-08 | -6.9987e-10 | 0.0071626 | 0.0071626 | 0.0071626 | 0.99262 | -0.051695 | 0.99262 | -0.051751 | 2.6528
51 | 0.016358 | 0.0041005 | -0.016356 | -0.0040996 | 2.521e-06 | 8.827e-07 | 0.024517 | 0.024517 | 0.024517 | 0.99285 | -0.050101 | 0.99269 | -0.051214 | 9.0802
52 | -0.059163 | -0.014851 | 0.059221 | 0.014873 | 5.808e-05 | 2.2183e-05 | 0.088351 | 0.088351 | 0.088351 | 0.99652 | -0.02427 | 0.99753 | -0.017208 | 32.7226
53 | -0.004264 | -0.0010685 | 0.0042643 | 0.0010685 | 2.7987e-07 | -3.36e-08 | 0.0063996 | 0.0063995 | 0.0063996 | 0.99146 | -0.059914 | 0.99153 | -0.05944 | 2.3702
54 | 0.0021601 | 0.00054119 | -0.00216 | -0.00054134 | 9.5171e-08 | -1.5053e-07 | 0.0032419 | 0.0032419 | 0.0032419 | 0.99146 | -0.059914 | 0.99141 | -0.060233 | 1.2007
55 | -0.0079521 | -0.0019927 | 0.0079537 | 0.0019931 | 1.6606e-06 | 3.9761e-07 | 0.011934 | 0.011934 | 0.011934 | 0.99153 | -0.05944 | 0.99174 | -0.057931 | 4.4199
56 | -0.0094836 | -0.0023765 | 0.0094838 | 0.0023766 | 2.0474e-07 | 5.7836e-08 | 0.014229 | 0.014229 | 0.014229 | 0.99174 | -0.057931 | 0.99176 | -0.057775 | 5.27
57 | -0.012062 | -0.0030227 | 0.012066 | 0.0030239 | 3.8335e-06 | 1.2323e-06 | 0.018097 | 0.018097 | 0.018097 | 0.99176 | -0.057775 | 0.99209 | -0.05548 | 6.7027
58 | -0.012066 | -0.0030239 | 0.012072 | 0.0030258 | 5.9302e-06 | 1.906e-06 | 0.018097 | 0.018097 | 0.018097 | 0.99209 | -0.05548 | 0.99259 | -0.051931 | 6.7026
59 | 0.0015973 | 0.00039979 | -0.0015972 | -0.0004 | 6.7891e-08 | -2.1585e-07 | 0.0024025 | 0.0024026 | 0.0024026 | 0.9892 | -0.076008 | 0.98916 | -0.076316 | 0.88985
60 | 0.0021905 | 0.00054793 | -0.0021899 | -0.00054884 | 5.9839e-07 | -9.0349e-07 | 0.0032947 | 0.0032951 | 0.0032951 | 0.9892 | -0.076008 | 0.98892 | -0.077986 | 1.2204
61 | 0.00083059 | 0.00020787 | -0.00083057 | -0.00020816 | 2.2261e-08 | -2.8478e-07 | 0.0012494 | 0.0012495 | 0.0012495 | 0.98916 | -0.076316 | 0.98913 | -0.07651 | 0.46277
62 | -0.0052677 | -0.0013202 | 0.0052684 | 0.0013202 | 6.7489e-07 | 3.4284e-08 | 0.0078874 | 0.0078873 | 0.0078874 | 0.99379 | -0.043556 | 0.99392 | -0.042631 | 2.9213
63 | -0.0075883 | -0.0019017 | 0.0075925 | 0.0019026 | 4.2079e-06 | 9.4086e-07 | 0.011361 | 0.01136 | 0.011361 | 0.99392 | -0.042631 | 0.99449 | -0.038626 | 4.2076
64 | -0.060867 | -0.015285 | 0.060876 | 0.015289 | 9.0802e-06 | 3.4693e-06 | 0.090806 | 0.090806 | 0.090806 | 0.99753 | -0.017208 | 0.99769 | -0.016134 | 33.6317
65 | -0.062466 | -0.015687 | 0.062497 | 0.015699 | 3.0582e-05 | 1.1689e-05 | 0.093177 | 0.093177 | 0.093177 | 0.99769 | -0.016134 | 0.99819 | -0.012614 | 34.51
66 | 0.045021 | 0.011301 | -0.045009 | -0.011297 | 1.2067e-05 | 4.5849e-06 | 0.067068 | 0.067068 | 0.067068 | 0.99897 | -0.0072047 | 0.99869 | -0.0091353 | 24.8399
67 | 0.043346 | 0.01088 | -0.04333 | -0.010874 | 1.6611e-05 | 6.3056e-06 | 0.06459 | 0.06459 | 0.06459 | 0.99869 | -0.0091353 | 0.9983 | -0.011896 | 23.9223
68 | 0.042134 | 0.010574 | -0.042123 | -0.01057 | 1.0586e-05 | 4.0155e-06 | 0.062807 | 0.062807 | 0.062807 | 0.9983 | -0.011896 | 0.99804 | -0.013707 | 23.262
69 | 0.0093822 | 0.0023512 | -0.0093817 | -0.002351 | 5.206e-07 | 1.4529e-07 | 0.014037 | 0.014037 | 0.014037 | 0.99455 | -0.038225 | 0.99449 | -0.038626 | 5.199
70 | 0.0032309 | 0.00080966 | -0.0032308 | -0.00080972 | 1.2412e-07 | -6.1859e-08 | 0.0048434 | 0.0048435 | 0.0048435 | 0.99262 | -0.051751 | 0.99258 | -0.052028 | 1.7939
71 | 0.015 | 0.0037599 | -0.015 | -0.0037598 | 2.3432e-07 | 8.052e-08 | 0.022485 | 0.022485 | 0.022485 | 0.99269 | -0.051214 | 0.99268 | -0.051327 | 8.3278
72 | 0.013899 | 0.0034839 | -0.013899 | -0.0034837 | 5.4098e-07 | 1.8225e-07 | 0.020835 | 0.020835 | 0.020835 | 0.99268 | -0.051327 | 0.99264 | -0.051608 | 7.7166
73 | -0.012999 | -0.0032581 | 0.012999 | 0.0032583 | 5.8086e-07 | 1.9172e-07 | 0.019487 | 0.019487 | 0.019487 | 0.99259 | -0.051931 | 0.99264 | -0.051608 | 7.2173

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -4.4415e-16 | -7.6913e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.564e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.1284 | 0.032056

## res_load
| p_mw | q_mvar
0 | 0.0016504 | 0.00041364
1 | 0.0015327 | 0.00038413
2 | 0.00060627 | 0.00015194
3 | 0.0023947 | 0.00060017
4 | 0.0011909 | 0.00029847
5 | 0.0028626 | 0.00071745
6 | 0.0050832 | 0.001274
7 | 0.0027593 | 0.00069154
8 | 0.0011483 | 0.00028778
9 | 0.0017897 | 0.00044855
10 | 0.0020715 | 0.00051917
11 | 0.0012779 | 0.00032027
12 | 0.0027338 | 0.00068514
13 | 0.003165 | 0.00079322
14 | 0.0011785 | 0.00029536
15 | 0.0020741 | 0.00051983
16 | 0.0012642 | 0.00031685
17 | 0.0017805 | 0.00044623
18 | 0.0014112 | 0.00035368
19 | 0.0025446 | 0.00063774
20 | 0.0020818 | 0.00052174
21 | 0.001948 | 0.00048821
22 | 0.0025042 | 0.00062761
23 | 0.0023801 | 0.0005965
24 | 0.00099978 | 0.00025057
25 | 0.0019337 | 0.00048464
26 | 0.0016418 | 0.00041149
27 | 0.0015941 | 0.00039951
28 | 0.0015123 | 0.00037901
29 | 0.0016413 | 0.00041134
30 | 0.0016415 | 0.00041139
31 | 0.0016457 | 0.00041245
32 | 0.0015908 | 0.0003987
33 | 0.0022305 | 0.000559
34 | 0.0032309 | 0.00080974
35 | 0.0023533 | 0.00058978
36 | 0.00092787 | 0.00023255
37 | 0.00090117 | 0.00022586
38 | 0.002691 | 0.00067442
39 | 0.00092776 | 0.00023252
40 | 0.00093135 | 0.00023342
41 | 0.002104 | 0.0005273
42 | 0.0036877 | 0.00092423
43 | 0.00216 | 0.00054134
44 | 0.0015299 | 0.00038342
45 | 0.0025781 | 0.00064613
46 | 0.0007666 | 0.00019213
47 | 0.0021899 | 0.00054884
48 | 0.00083057 | 0.00020816
49 | 0.0052677 | 0.0013202
50 | 0.0023199 | 0.00058143
51 | 0.0016456 | 0.00041242
52 | 0.0015901 | 0.00039851
53 | 0.0015894 | 0.00039835
54 | 0.0015927 | 0.00039917
55 | 0.0016628 | 0.00041675
56 | 0.0011961 | 0.00029977
57 | 0.0011501 | 0.00028823
58 | 0.0043346 | 0.0010863
59 | 0.0017892 | 0.00044841
60 | 0.001547 | 0.00038772
61 | 0.0013553 | 0.00033968
62 | 0.0032308 | 0.00080972
63 | 0.0011009 | 0.0002759
64 | 0.00092695 | 0.00023232
65 | 0.00089939 | 0.00022541

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1