## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2575-4_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2575-4_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2575-4_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2575-4_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2575-4_0_4_node_91 | 0.4 | n |  | TRUE
5 | bus_LV_2575-4_0_4_node_92 | 0.4 | n |  | TRUE
6 | bus_LV_2575-4_0_4_node_29 | 0.4 | n |  | TRUE
7 | bus_LV_2575-4_0_4_node_30 | 0.4 | n |  | TRUE
8 | bus_LV_2575-4_0_4_node_28 | 0.4 | n |  | TRUE
9 | bus_LV_2575-4_0_4_node_4 | 0.4 | n |  | TRUE
10 | bus_LV_2575-4_0_4_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_2575-4_0_4_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_2575-4_0_4_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_2575-4_0_4_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_2575-4_0_4_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_2575-4_0_4_node_123 | 0.4 | n |  | TRUE
16 | bus_LV_2575-4_0_4_node_81 | 0.4 | n |  | TRUE
17 | bus_LV_2575-4_0_4_node_111 | 0.4 | n |  | TRUE
18 | bus_LV_2575-4_0_4_node_25 | 0.4 | n |  | TRUE
19 | bus_LV_2575-4_0_4_node_24 | 0.4 | n |  | TRUE
20 | bus_LV_2575-4_0_4_node_80 | 0.4 | n |  | TRUE
21 | bus_LV_2575-4_0_4_node_89 | 0.4 | n |  | TRUE
22 | bus_LV_2575-4_0_4_node_10 | 0.4 | n |  | TRUE
23 | bus_LV_2575-4_0_4_node_11 | 0.4 | n |  | TRUE
24 | bus_LV_2575-4_0_4_node_12 | 0.4 | n |  | TRUE
25 | bus_LV_2575-4_0_4_node_13 | 0.4 | n |  | TRUE
26 | bus_LV_2575-4_0_4_node_14 | 0.4 | n |  | TRUE
27 | bus_LV_2575-4_0_4_node_15 | 0.4 | n |  | TRUE
28 | bus_LV_2575-4_0_4_node_93 | 0.4 | n |  | TRUE
29 | bus_LV_2575-4_0_4_node_117 | 0.4 | n |  | TRUE
30 | bus_LV_2575-4_0_4_node_74 | 0.4 | n |  | TRUE
31 | bus_LV_2575-4_0_4_node_94 | 0.4 | n |  | TRUE
32 | bus_LV_2575-4_0_4_node_39 | 0.4 | n |  | TRUE
33 | bus_LV_2575-4_0_4_node_72 | 0.4 | n |  | TRUE
34 | bus_LV_2575-4_0_4_node_16 | 0.4 | n |  | TRUE
35 | bus_LV_2575-4_0_4_node_17 | 0.4 | n |  | TRUE
36 | bus_LV_2575-4_0_4_node_18 | 0.4 | n |  | TRUE
37 | bus_LV_2575-4_0_4_node_109 | 0.4 | n |  | TRUE
38 | bus_LV_2575-4_0_4_node_51 | 0.4 | n |  | TRUE
39 | bus_LV_2575-4_0_4_node_19 | 0.4 | n |  | TRUE
40 | bus_LV_2575-4_0_4_node_20 | 0.4 | n |  | TRUE
41 | bus_LV_2575-4_0_4_node_21 | 0.4 | n |  | TRUE
42 | bus_LV_2575-4_0_4_node_22 | 0.4 | n |  | TRUE
43 | bus_LV_2575-4_0_4_node_23 | 0.4 | n |  | TRUE
44 | bus_LV_2575-4_0_4_node_84 | 0.4 | n |  | TRUE
45 | bus_LV_2575-4_0_4_node_121 | 0.4 | n |  | TRUE
46 | bus_LV_2575-4_0_4_node_44 | 0.4 | n |  | TRUE
47 | bus_LV_2575-4_0_4_node_71 | 0.4 | n |  | TRUE
48 | bus_LV_2575-4_0_4_node_26 | 0.4 | n |  | TRUE
49 | bus_LV_2575-4_0_4_node_27 | 0.4 | n |  | TRUE
50 | bus_LV_2575-4_0_4_node_118 | 0.4 | n |  | TRUE
51 | bus_LV_2575-4_0_4_node_55 | 0.4 | n |  | TRUE
52 | bus_LV_2575-4_0_4_node_31 | 0.4 | n |  | TRUE
53 | bus_LV_2575-4_0_4_node_32 | 0.4 | n |  | TRUE
54 | bus_LV_2575-4_0_4_node_33 | 0.4 | n |  | TRUE
55 | bus_LV_2575-4_0_4_node_34 | 0.4 | n |  | TRUE
56 | bus_LV_2575-4_0_4_node_35 | 0.4 | n |  | TRUE
57 | bus_LV_2575-4_0_4_node_108 | 0.4 | n |  | TRUE
58 | bus_LV_2575-4_0_4_node_113 | 0.4 | n |  | TRUE
59 | bus_LV_2575-4_0_4_node_106 | 0.4 | n |  | TRUE
60 | bus_LV_2575-4_0_4_node_36 | 0.4 | n |  | TRUE
61 | bus_LV_2575-4_0_4_node_37 | 0.4 | n |  | TRUE
62 | bus_LV_2575-4_0_4_node_38 | 0.4 | n |  | TRUE
63 | bus_LV_2575-4_0_4_node_40 | 0.4 | n |  | TRUE
64 | bus_LV_2575-4_0_4_node_63 | 0.4 | n |  | TRUE
65 | bus_LV_2575-4_0_4_node_65 | 0.4 | n |  | TRUE
66 | bus_LV_2575-4_0_4_node_62 | 0.4 | n |  | TRUE
67 | bus_LV_2575-4_0_4_node_105 | 0.4 | n |  | TRUE
68 | bus_LV_2575-4_0_4_node_41 | 0.4 | n |  | TRUE
69 | bus_LV_2575-4_0_4_node_42 | 0.4 | n |  | TRUE
70 | bus_LV_2575-4_0_4_node_43 | 0.4 | n |  | TRUE
71 | bus_LV_2575-4_0_4_node_45 | 0.4 | n |  | TRUE
72 | bus_LV_2575-4_0_4_node_53 | 0.4 | n |  | TRUE
73 | bus_LV_2575-4_0_4_node_46 | 0.4 | n |  | TRUE
74 | bus_LV_2575-4_0_4_node_47 | 0.4 | n |  | TRUE
75 | bus_LV_2575-4_0_4_node_48 | 0.4 | n |  | TRUE
76 | bus_LV_2575-4_0_4_node_49 | 0.4 | n |  | TRUE
77 | bus_LV_2575-4_0_4_node_50 | 0.4 | n |  | TRUE
78 | bus_LV_2575-4_0_4_node_97 | 0.4 | n |  | TRUE
79 | bus_LV_2575-4_0_4_node_125 | 0.4 | n |  | TRUE
80 | bus_LV_2575-4_0_4_node_98 | 0.4 | n |  | TRUE
81 | bus_LV_2575-4_0_4_node_52 | 0.4 | n |  | TRUE
82 | bus_LV_2575-4_0_4_node_54 | 0.4 | n |  | TRUE
83 | bus_LV_2575-4_0_4_node_56 | 0.4 | n |  | TRUE
84 | bus_LV_2575-4_0_4_node_57 | 0.4 | n |  | TRUE
85 | bus_LV_2575-4_0_4_node_58 | 0.4 | n |  | TRUE
86 | bus_LV_2575-4_0_4_node_59 | 0.4 | n |  | TRUE
87 | bus_LV_2575-4_0_4_node_60 | 0.4 | n |  | TRUE
88 | bus_LV_2575-4_0_4_node_61 | 0.4 | n |  | TRUE
89 | bus_LV_2575-4_0_4_node_104 | 0.4 | n |  | TRUE
90 | bus_LV_2575-4_0_4_node_100 | 0.4 | n |  | TRUE
91 | bus_LV_2575-4_0_4_node_124 | 0.4 | n |  | TRUE
92 | bus_LV_2575-4_0_4_node_99 | 0.4 | n |  | TRUE
93 | bus_LV_2575-4_0_4_node_122 | 0.4 | n |  | TRUE
94 | bus_LV_2575-4_0_4_node_64 | 0.4 | n |  | TRUE
95 | bus_LV_2575-4_0_4_node_79 | 0.4 | n |  | TRUE
96 | bus_LV_2575-4_0_4_node_76 | 0.4 | n |  | TRUE
97 | bus_LV_2575-4_0_4_node_96 | 0.4 | n |  | TRUE
98 | bus_LV_2575-4_0_4_node_77 | 0.4 | n |  | TRUE
99 | bus_LV_2575-4_0_4_node_66 | 0.4 | n |  | TRUE
100 | bus_LV_2575-4_0_4_node_67 | 0.4 | n |  | TRUE
101 | bus_LV_2575-4_0_4_node_68 | 0.4 | n |  | TRUE
102 | bus_LV_2575-4_0_4_node_69 | 0.4 | n |  | TRUE
103 | bus_LV_2575-4_0_4_node_70 | 0.4 | n |  | TRUE
104 | bus_LV_2575-4_0_4_node_83 | 0.4 | n |  | TRUE
105 | bus_LV_2575-4_0_4_node_82 | 0.4 | n |  | TRUE
106 | bus_LV_2575-4_0_4_node_73 | 0.4 | n |  | TRUE
107 | bus_LV_2575-4_0_4_node_75 | 0.4 | n |  | TRUE
108 | bus_LV_2575-4_0_4_node_78 | 0.4 | n |  | TRUE
109 | bus_LV_2575-4_0_4_node_116 | 0.4 | n |  | TRUE
110 | bus_LV_2575-4_0_4_node_119 | 0.4 | n |  | TRUE
111 | bus_LV_2575-4_0_4_node_115 | 0.4 | n |  | TRUE
112 | bus_LV_2575-4_0_4_node_120 | 0.4 | n |  | TRUE
113 | bus_LV_2575-4_0_4_node_85 | 0.4 | n |  | TRUE
114 | bus_LV_2575-4_0_4_node_86 | 0.4 | n |  | TRUE
115 | bus_LV_2575-4_0_4_node_87 | 0.4 | n |  | TRUE
116 | bus_LV_2575-4_0_4_node_88 | 0.4 | n |  | TRUE
117 | bus_LV_2575-4_0_4_node_112 | 0.4 | n |  | TRUE
118 | bus_LV_2575-4_0_4_node_110 | 0.4 | n |  | TRUE
119 | bus_LV_2575-4_0_4_node_127 | 0.4 | n |  | TRUE
120 | bus_LV_2575-4_0_4_node_95 | 0.4 | n |  | TRUE
121 | bus_LV_2575-4_0_4_node_103 | 0.4 | n |  | TRUE
122 | bus_LV_2575-4_0_4_node_101 | 0.4 | n |  | TRUE
123 | bus_LV_2575-4_0_4_node_102 | 0.4 | n |  | TRUE
124 | bus_LV_2575-4_0_4_node_107 | 0.4 | n |  | TRUE
125 | bus_LV_2575-4_0_4_node_114 | 0.4 | n |  | TRUE
126 | bus_MV_397_0_node_33 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2575-4_0_4_load_0 | 0 | 0.0012698 | 0.00031823 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2575-4_0_4_load_2 | 2 | 0.00066358 | 0.00016631 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2575-4_0_4_load_3 | 3 | 0.0019695 | 0.0004936 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2575-4_0_4_load_91 | 4 | 0.00062152 | 0.00015577 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2575-4_0_4_load_92 | 5 | 0.0010955 | 0.00027455 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2575-4_0_4_load_29 | 6 | 0.00087274 | 0.00021873 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2575-4_0_4_load_30 | 7 | 0.00037058 | 9.2877e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2575-4_0_4_load_28 | 8 | 0.0025759 | 0.00064559 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2575-4_0_4_load_4 | 9 | 0.0016761 | 0.00042006 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2575-4_0_4_load_5 | 10 | 0.0055343 | 0.001387 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2575-4_0_4_load_9 | 14 | 0.0026386 | 0.00066131 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2575-4_0_4_load_123 | 15 | 0.0024653 | 0.00061786 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2575-4_0_4_load_81 | 16 | 0.0022256 | 0.00055779 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2575-4_0_4_load_25 | 18 | 0.0090514 | 0.0022685 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2575-4_0_4_load_24 | 19 | 0.0022463 | 0.00056298 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2575-4_0_4_load_80 | 20 | 0.0050349 | 0.0012619 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2575-4_0_4_load_89 | 21 | 0.0015666 | 0.00039262 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2575-4_0_4_load_10 | 22 | 0.0018004 | 0.00045122 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2575-4_0_4_load_11 | 23 | 0.0022748 | 0.00057011 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2575-4_0_4_load_13 | 25 | 0.0019685 | 0.00049335 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2575-4_0_4_load_14 | 26 | 0.00092673 | 0.00023226 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2575-4_0_4_load_15 | 27 | 0.00061575 | 0.00015432 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2575-4_0_4_load_93 | 28 | 0.0016006 | 0.00040114 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2575-4_0_4_load_117 | 29 | 0.00033418 | 8.3754e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2575-4_0_4_load_74 | 30 | 0.0019095 | 0.00047855 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2575-4_0_4_load_94 | 31 | 0.0016688 | 0.00041825 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2575-4_0_4_load_39 | 32 | 0.0003044 | 7.6289e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2575-4_0_4_load_72 | 33 | 0.0013336 | 0.00033422 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2575-4_0_4_load_16 | 34 | 0.0011283 | 0.00028278 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2575-4_0_4_load_17 | 35 | 0.0012606 | 0.00031594 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2575-4_0_4_load_18 | 36 | 0.0011731 | 0.000294 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2575-4_0_4_load_51 | 38 | 0.0017491 | 0.00043835 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2575-4_0_4_load_19 | 39 | 0.0061971 | 0.0015531 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2575-4_0_4_load_20 | 40 | 0.0087085 | 0.0021826 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2575-4_0_4_load_21 | 41 | 0.015742 | 0.0039453 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2575-4_0_4_load_22 | 42 | 0.0023866 | 0.00059814 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2575-4_0_4_load_23 | 43 | 0.0059279 | 0.0014857 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2575-4_0_4_load_84 | 44 | 0.0023866 | 0.00059814 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2575-4_0_4_load_121 | 45 | 0.0014828 | 0.00037162 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2575-4_0_4_load_44 | 46 | 0.0047158 | 0.0011819 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2575-4_0_4_load_71 | 47 | 0.0010607 | 0.00026584 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2575-4_0_4_load_26 | 48 | 0.0019494 | 0.00048855 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2575-4_0_4_load_27 | 49 | 0.0013572 | 0.00034014 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2575-4_0_4_load_118 | 50 | 0.0031732 | 0.00079527 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2575-4_0_4_load_31 | 52 | 0.00077053 | 0.00019311 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2575-4_0_4_load_32 | 53 | 0.00098762 | 0.00024752 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2575-4_0_4_load_33 | 54 | 0.0010507 | 0.00026332 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2575-4_0_4_load_34 | 55 | 0.00026811 | 6.7196e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2575-4_0_4_load_35 | 56 | 0.0042816 | 0.0010731 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2575-4_0_4_load_113 | 58 | 0.0041527 | 0.0010408 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2575-4_0_4_load_36 | 60 | 0.00039832 | 9.9829e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2575-4_0_4_load_37 | 61 | 0.00047242 | 0.0001184 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2575-4_0_4_load_38 | 62 | 0.00098119 | 0.00024591 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2575-4_0_4_load_62 | 66 | 0.0012621 | 0.00031631 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2575-4_0_4_load_105 | 67 | 0.0013848 | 0.00034707 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2575-4_0_4_load_41 | 68 | 0.0045636 | 0.0011437 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2575-4_0_4_load_42 | 69 | 0.00030788 | 7.7162e-05 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2575-4_0_4_load_43 | 70 | 0.00018552 | 4.6496e-05 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2575-4_0_4_load_45 | 71 | 0.00044049 | 0.0001104 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2575-4_0_4_load_53 | 72 | 0.00065264 | 0.00016357 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2575-4_0_4_load_46 | 73 | 0.0010557 | 0.00026459 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2575-4_0_4_load_47 | 74 | 0.0010268 | 0.00025735 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2575-4_0_4_load_49 | 76 | 0.0020119 | 0.00050424 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2575-4_0_4_load_50 | 77 | 0.0030412 | 0.0007622 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2575-4_0_4_load_97 | 78 | 0.00071301 | 0.0001787 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2575-4_0_4_load_125 | 79 | 0.0039589 | 0.0009922 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2575-4_0_4_load_98 | 80 | 0.0017305 | 0.0004337 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2575-4_0_4_load_52 | 81 | 0.00054967 | 0.00013776 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2575-4_0_4_load_54 | 82 | 0.00087081 | 0.00021825 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2575-4_0_4_load_56 | 83 | 0.00061522 | 0.00015419 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2575-4_0_4_load_57 | 84 | 0.0016951 | 0.00042483 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2575-4_0_4_load_58 | 85 | 0.0019517 | 0.00048915 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2575-4_0_4_load_60 | 87 | 0.00086312 | 0.00021632 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2575-4_0_4_load_104 | 89 | 0.0012663 | 0.00031736 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2575-4_0_4_load_100 | 90 | 0.0032247 | 0.00080818 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2575-4_0_4_load_124 | 91 | 0.0011872 | 0.00029754 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2575-4_0_4_load_99 | 92 | 0.0019395 | 0.0004861 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2575-4_0_4_load_122 | 93 | 0.0053589 | 0.0013431 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2575-4_0_4_load_64 | 94 | 0.00027404 | 6.8682e-05 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2575-4_0_4_load_79 | 95 | 0.0034382 | 0.0008617 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2575-4_0_4_load_76 | 96 | 0.0046442 | 0.0011639 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2575-4_0_4_load_96 | 97 | 0.0042608 | 0.0010679 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2575-4_0_4_load_77 | 98 | 0.0014183 | 0.00035547 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2575-4_0_4_load_66 | 99 | 0.00196 | 0.00049122 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2575-4_0_4_load_67 | 100 | 0.0013782 | 0.0003454 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2575-4_0_4_load_69 | 102 | 0.0036991 | 0.00092707 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2575-4_0_4_load_70 | 103 | 0.0044868 | 0.0011245 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2575-4_0_4_load_83 | 104 | 0.005378 | 0.0013478 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2575-4_0_4_load_82 | 105 | 0.00042286 | 0.00010598 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2575-4_0_4_load_73 | 106 | 0.0023135 | 0.00057982 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2575-4_0_4_load_75 | 107 | 0.0019946 | 0.00049989 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2575-4_0_4_load_116 | 109 | 0.0017815 | 0.00044648 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2575-4_0_4_load_119 | 110 | 0.0013137 | 0.00032923 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2575-4_0_4_load_120 | 112 | 0.0017354 | 0.00043494 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2575-4_0_4_load_85 | 113 | 0.0034495 | 0.00086452 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2575-4_0_4_load_86 | 114 | 0.0016085 | 0.00040312 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2575-4_0_4_load_110 | 118 | 0.00085546 | 0.0002144 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2575-4_0_4_load_127 | 119 | 0.0050955 | 0.0012771 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2575-4_0_4_load_95 | 120 | 0.0011408 | 0.00028591 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2575-4_0_4_load_103 | 121 | 0.0018556 | 0.00046506 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2575-4_0_4_load_102 | 123 | 0.0029505 | 0.00073946 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2575-4_0_4_load_107 | 124 | 0.00346 | 0.00086717 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2575-4_0_4_load_114 | 125 | 0.0016909 | 0.00042378 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 96 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2575-4_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.019731 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2575-4_0_4_line_1 | NAYY 4x150 SE | 1 | 2 | 0.02417 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2575-4_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.01008 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2575-4_0_4_line_3 | NAYY 4x150 SE | 3 | 7 | 0.015231 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2575-4_0_4_line_4 | NAYY 4x150 SE | 4 | 5 | 0.048878 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2575-4_0_4_line_5 | NAYY 4x150 SE | 4 | 6 | 0.090134 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2575-4_0_4_line_6 | NAYY 4x150 SE | 5 | 83 | 0.02865 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2575-4_0_4_line_7 | NAYY 4x150 SE | 6 | 8 | 0.0016113 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2575-4_0_4_line_8 | NAYY 4x150 SE | 7 | 8 | 0.025136 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2575-4_0_4_line_9 | NAYY 4x150 SE | 9 | 10 | 0.025085 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2575-4_0_4_line_10 | NAYY 4x150 SE | 9 | 11 | 0.010444 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2575-4_0_4_line_11 | NAYY 4x150 SE | 10 | 12 | 0.02007 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2575-4_0_4_line_12 | NAYY 4x150 SE | 11 | 13 | 0.0315 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2575-4_0_4_line_13 | NAYY 4x150 SE | 11 | 14 | 0.026091 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2575-4_0_4_line_14 | NAYY 4x150 SE | 12 | 15 | 0.037548 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2575-4_0_4_line_15 | NAYY 4x150 SE | 13 | 16 | 0.011232 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2575-4_0_4_line_16 | NAYY 4x150 SE | 14 | 17 | 0.018323 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2575-4_0_4_line_17 | NAYY 4x150 SE | 16 | 20 | 0.02418 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2575-4_0_4_line_18 | NAYY 4x150 SE | 17 | 21 | 0.007814 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2575-4_0_4_line_19 | NAYY 4x150 SE | 18 | 19 | 0.0013845 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2575-4_0_4_line_20 | NAYY 4x150 SE | 19 | 48 | 0.012766 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2575-4_0_4_line_21 | NAYY 4x150 SE | 20 | 105 | 0.0060096 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2575-4_0_4_line_22 | NAYY 4x150 SE | 21 | 115 | 0.030312 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2575-4_0_4_line_23 | NAYY 4x150 SE | 22 | 23 | 0.0096213 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2575-4_0_4_line_24 | NAYY 4x150 SE | 22 | 24 | 0.01556 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2575-4_0_4_line_25 | NAYY 4x150 SE | 23 | 25 | 0.012679 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2575-4_0_4_line_26 | NAYY 4x150 SE | 24 | 26 | 0.0074619 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2575-4_0_4_line_27 | NAYY 4x150 SE | 24 | 27 | 0.0030051 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2575-4_0_4_line_28 | NAYY 4x150 SE | 25 | 28 | 0.003929 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2575-4_0_4_line_29 | NAYY 4x150 SE | 26 | 29 | 0.031111 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2575-4_0_4_line_30 | NAYY 4x150 SE | 27 | 30 | 0.013746 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2575-4_0_4_line_31 | NAYY 4x150 SE | 28 | 31 | 0.017373 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2575-4_0_4_line_32 | NAYY 4x150 SE | 29 | 32 | 0.0297 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2575-4_0_4_line_33 | NAYY 4x150 SE | 30 | 33 | 0.024765 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2575-4_0_4_line_34 | NAYY 4x150 SE | 31 | 120 | 9.901e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2575-4_0_4_line_35 | NAYY 4x150 SE | 32 | 61 | 0.032278 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2575-4_0_4_line_36 | NAYY 4x150 SE | 33 | 106 | 0.01942 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2575-4_0_4_line_37 | NAYY 4x150 SE | 34 | 35 | 0.021226 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2575-4_0_4_line_38 | NAYY 4x150 SE | 35 | 36 | 0.022166 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_2575-4_0_4_line_39 | NAYY 4x150 SE | 36 | 37 | 0.037273 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_2575-4_0_4_line_40 | NAYY 4x150 SE | 37 | 38 | 0.017687 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_2575-4_0_4_line_41 | NAYY 4x150 SE | 38 | 75 | 0.048853 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_2575-4_0_4_line_42 | NAYY 4x150 SE | 39 | 40 | 0.061603 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_2575-4_0_4_line_43 | NAYY 4x150 SE | 39 | 41 | 0.0020002 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_2575-4_0_4_line_44 | NAYY 4x150 SE | 40 | 42 | 0.024461 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_2575-4_0_4_line_45 | NAYY 4x150 SE | 41 | 43 | 0.042412 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_2575-4_0_4_line_46 | NAYY 4x150 SE | 42 | 44 | 0.0010974 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_2575-4_0_4_line_47 | NAYY 4x150 SE | 43 | 45 | 0.0078647 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_2575-4_0_4_line_48 | NAYY 4x150 SE | 44 | 46 | 0.0017385 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_2575-4_0_4_line_49 | NAYY 4x150 SE | 45 | 47 | 0.0017457 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_2575-4_0_4_line_50 | NAYY 4x150 SE | 46 | 69 | 0.044258 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_2575-4_0_4_line_51 | NAYY 4x150 SE | 47 | 101 | 0.04496 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
52 | LV_2575-4_0_4_line_52 | NAYY 4x150 SE | 48 | 49 | 0.010944 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_2575-4_0_4_line_53 | NAYY 4x150 SE | 49 | 50 | 0.056296 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_2575-4_0_4_line_54 | NAYY 4x150 SE | 50 | 51 | 0.010624 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_2575-4_0_4_line_55 | NAYY 4x150 SE | 51 | 72 | 0.022526 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_2575-4_0_4_line_56 | NAYY 4x150 SE | 51 | 71 | 0.019331 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_2575-4_0_4_line_57 | NAYY 4x150 SE | 52 | 53 | 0.039701 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_2575-4_0_4_line_58 | NAYY 4x150 SE | 52 | 54 | 4.4166e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_2575-4_0_4_line_59 | NAYY 4x150 SE | 53 | 55 | 0.022125 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_2575-4_0_4_line_60 | NAYY 4x150 SE | 54 | 56 | 0.019595 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_2575-4_0_4_line_61 | NAYY 4x150 SE | 56 | 57 | 0.025868 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_2575-4_0_4_line_62 | NAYY 4x150 SE | 57 | 58 | 0.016483 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_2575-4_0_4_line_63 | NAYY 4x150 SE | 57 | 59 | 0.004198 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_2575-4_0_4_line_64 | NAYY 4x150 SE | 58 | 123 | 0.0030845 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_2575-4_0_4_line_65 | NAYY 4x150 SE | 59 | 67 | 0.014391 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_2575-4_0_4_line_66 | NAYY 4x150 SE | 59 | 63 | 0.035541 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_2575-4_0_4_line_67 | NAYY 4x150 SE | 60 | 61 | 0.037753 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_2575-4_0_4_line_68 | NAYY 4x150 SE | 60 | 62 | 0.033505 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_2575-4_0_4_line_69 | NAYY 4x150 SE | 62 | 63 | 0.022804 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_2575-4_0_4_line_70 | NAYY 4x150 SE | 63 | 64 | 0.028308 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_2575-4_0_4_line_71 | NAYY 4x150 SE | 64 | 65 | 0.016499 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_2575-4_0_4_line_72 | NAYY 4x150 SE | 64 | 66 | 0.044128 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_2575-4_0_4_line_73 | NAYY 4x150 SE | 65 | 95 | 0.019497 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
74 | LV_2575-4_0_4_line_74 | NAYY 4x150 SE | 65 | 96 | 0.024666 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
75 | LV_2575-4_0_4_line_75 | NAYY 4x150 SE | 66 | 94 | 0.021331 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_2575-4_0_4_line_76 | NAYY 4x150 SE | 67 | 124 | 0.030629 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_2575-4_0_4_line_77 | NAYY 4x150 SE | 68 | 69 | 0.0029707 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_2575-4_0_4_line_78 | NAYY 4x150 SE | 68 | 70 | 0.021852 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_2575-4_0_4_line_79 | NAYY 4x150 SE | 70 | 71 | 0.0051277 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_2575-4_0_4_line_80 | NAYY 4x150 SE | 72 | 81 | 0.014746 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_2575-4_0_4_line_81 | NAYY 4x150 SE | 73 | 74 | 0.036916 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_2575-4_0_4_line_82 | NAYY 4x150 SE | 73 | 75 | 0.015599 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_2575-4_0_4_line_83 | NAYY 4x150 SE | 74 | 76 | 0.033011 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_2575-4_0_4_line_84 | NAYY 4x150 SE | 75 | 77 | 0.078 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_2575-4_0_4_line_85 | NAYY 4x150 SE | 77 | 78 | 0.019737 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_2575-4_0_4_line_86 | NAYY 4x150 SE | 77 | 79 | 0.29972 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_2575-4_0_4_line_87 | NAYY 4x150 SE | 78 | 80 | 0.041802 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_2575-4_0_4_line_88 | NAYY 4x150 SE | 80 | 93 | 0.029392 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_2575-4_0_4_line_89 | NAYY 4x150 SE | 81 | 82 | 0.020899 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_2575-4_0_4_line_90 | NAYY 4x150 SE | 82 | 83 | 0.0061806 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_2575-4_0_4_line_91 | NAYY 4x150 SE | 84 | 85 | 0.0010592 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_2575-4_0_4_line_92 | NAYY 4x150 SE | 84 | 86 | 0.017192 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_2575-4_0_4_line_93 | NAYY 4x150 SE | 85 | 87 | 0.027345 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_2575-4_0_4_line_94 | NAYY 4x150 SE | 86 | 88 | 0.054815 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_2575-4_0_4_line_95 | NAYY 4x150 SE | 87 | 89 | 0.0035625 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_2575-4_0_4_line_96 | NAYY 4x150 SE | 88 | 90 | 0.012319 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_2575-4_0_4_line_97 | NAYY 4x150 SE | 88 | 91 | 0.034203 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_2575-4_0_4_line_98 | NAYY 4x150 SE | 90 | 92 | 0.0052243 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_2575-4_0_4_line_99 | NAYY 4x150 SE | 91 | 93 | 0.045706 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_2575-4_0_4_line_100 | NAYY 4x150 SE | 92 | 122 | 0.012412 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_2575-4_0_4_line_101 | NAYY 4x150 SE | 95 | 97 | 0.022729 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
102 | LV_2575-4_0_4_line_102 | NAYY 4x150 SE | 96 | 98 | 0.034124 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_2575-4_0_4_line_103 | NAYY 4x150 SE | 97 | 103 | 0.022941 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
104 | LV_2575-4_0_4_line_104 | NAYY 4x150 SE | 98 | 108 | 0.011716 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_2575-4_0_4_line_105 | NAYY 4x150 SE | 99 | 100 | 0.0058154 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_2575-4_0_4_line_106 | NAYY 4x150 SE | 99 | 101 | 0.012948 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_2575-4_0_4_line_107 | NAYY 4x150 SE | 100 | 102 | 0.00059042 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_2575-4_0_4_line_108 | NAYY 4x150 SE | 101 | 103 | 0.0048959 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
109 | LV_2575-4_0_4_line_109 | NAYY 4x150 SE | 102 | 104 | 0.0078239 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_2575-4_0_4_line_110 | NAYY 4x150 SE | 104 | 105 | 0.022396 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_2575-4_0_4_line_111 | NAYY 4x150 SE | 106 | 107 | 0.0026899 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_2575-4_0_4_line_112 | NAYY 4x150 SE | 108 | 109 | 0.012319 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_2575-4_0_4_line_113 | NAYY 4x150 SE | 108 | 110 | 0.016406 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_2575-4_0_4_line_114 | NAYY 4x150 SE | 109 | 111 | 0.014692 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_2575-4_0_4_line_115 | NAYY 4x150 SE | 110 | 112 | 0.016071 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_2575-4_0_4_line_116 | NAYY 4x150 SE | 111 | 125 | 0.039213 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_2575-4_0_4_line_117 | NAYY 4x150 SE | 113 | 114 | 0.062543 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_2575-4_0_4_line_118 | NAYY 4x150 SE | 113 | 115 | 0.018564 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_2575-4_0_4_line_119 | NAYY 4x150 SE | 114 | 116 | 0.029278 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_2575-4_0_4_line_120 | NAYY 4x150 SE | 116 | 117 | 0.04913 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_2575-4_0_4_line_121 | NAYY 4x150 SE | 116 | 118 | 0.03779 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_2575-4_0_4_line_122 | NAYY 4x150 SE | 117 | 119 | 0.045556 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_2575-4_0_4_line_123 | NAYY 4x150 SE | 120 | 121 | 0.019412 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
124 | LV_2575-4_0_4_line_124 | NAYY 4x150 SE | 122 | 123 | 0.02856 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2575-4_0_4_trafo_76 | 0.25 MVA 20/0.4 kV | 126 | 96 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2629744.9014 | 1236623.9984 | 2629736.3012 | 1236634.1062 | 2629732.6981 | 1236639.4675
1 | 2629744.9014 | 1236623.9984 | 2629765.1436 | 1236637.2067
2 | 2629744.9014 | 1236623.9984 | 2629751.4742 | 1236616.3556
3 | 2629751.4742 | 1236616.3556 | 2629761.4055 | 1236604.8074
4 | 2629842.5376 | 1236520.7403 | 2629858.0998 | 1236506.003 | 2629868.1569 | 1236496.6588 | 2629878.2049 | 1236487.3208
5 | 2629842.5376 | 1236520.7403 | 2629778.95 | 1236584.6216
6 | 2629900.0511 | 1236468.8524 | 2629890.3844 | 1236476.002 | 2629878.2049 | 1236487.3208
7 | 2629777.8457 | 1236585.7949 | 2629778.95 | 1236584.6216
8 | 2629777.8457 | 1236585.7949 | 2629776.8042 | 1236586.9016 | 2629761.4055 | 1236604.8074
9 | 2630072.5722 | 1236327.8864 | 2630069.4117 | 1236317.0162 | 2630067.1762 | 1236303.4343
10 | 2630076.8448 | 1236337.4109 | 2630072.7138 | 1236328.3732 | 2630072.5722 | 1236327.8864
11 | 2630064.3373 | 1236283.5697 | 2630065.8 | 1236295.0731 | 2630067.1762 | 1236303.4343
12 | 2630092.7859 | 1236364.5973 | 2630089.5626 | 1236358.6106 | 2630076.8448 | 1236337.4109
13 | 2630076.8448 | 1236337.4109 | 2630095.6795 | 1236326.5883 | 2630098.9153 | 1236323.6541
14 | 2630064.3373 | 1236283.5697 | 2630071.5544 | 1236282.3276 | 2630077.5469 | 1236273.3968 | 2630084.6607 | 1236255.2731
15 | 2630092.7859 | 1236364.5973 | 2630096.0284 | 1236369.7613 | 2630098.9894 | 1236373.9564
16 | 2630111.1376 | 1236310.1785 | 2630107.0435 | 1236316.2838 | 2630098.9153 | 1236323.6541
17 | 2630112.5092 | 1236394.0025 | 2630110.7564 | 1236391.4271 | 2630102.9842 | 1236379.7805 | 2630100.9191 | 1236376.6904 | 2630098.9894 | 1236373.9564
18 | 2630111.1376 | 1236310.1785 | 2630114.2413 | 1236303.0074
19 | 2630029.409 | 1236385.444 | 2630030.7372 | 1236385.0531
20 | 2630029.409 | 1236385.444 | 2630017.1621 | 1236389.0485
21 | 2630112.5092 | 1236394.0025 | 2630115.8906 | 1236398.9706
22 | 2630126.2814 | 1236275.1889 | 2630114.2413 | 1236303.0074
23 | 2630320.4044 | 1236511.6741 | 2630314.8479 | 1236519.5287
24 | 2630329.3907 | 1236498.9712 | 2630320.4044 | 1236511.6741
25 | 2630314.8479 | 1236519.5287 | 2630307.5253 | 1236529.8798
26 | 2630329.3907 | 1236498.9712 | 2630324.0384 | 1236493.7719
27 | 2630329.3907 | 1236498.9712 | 2630331.4944 | 1236501.1172
28 | 2630305.2562 | 1236533.0874 | 2630307.5253 | 1236529.8798
29 | 2630301.3685 | 1236472.4871 | 2630306.9544 | 1236477.1766 | 2630324.0384 | 1236493.7719
30 | 2630331.4944 | 1236501.1172 | 2630341.1168 | 1236510.9331
31 | 2630305.2562 | 1236533.0874 | 2630295.2228 | 1236547.2704
32 | 2630301.3685 | 1236472.4871 | 2630279.3873 | 1236454.033 | 2630278.5197 | 1236453.5372
33 | 2630358.4527 | 1236528.6178 | 2630341.1168 | 1236510.9331
34 | 2630295.1656 | 1236547.3513 | 2630295.2228 | 1236547.2704
35 | 2630278.5197 | 1236453.5372 | 2630275.4416 | 1236451.7782 | 2630271.62 | 1236451.8921 | 2630268.4514 | 1236453.0545 | 2630255.1944 | 1236470.0243
36 | 2630358.4527 | 1236528.6178 | 2630372.047 | 1236542.4855
37 | 2630506.3852 | 1236871.1537 | 2630486.8364 | 1236879.4234
38 | 2630466.4221 | 1236888.0592 | 2630486.8364 | 1236879.4234
39 | 2630432.0947 | 1236902.5807 | 2630466.4221 | 1236888.0592
40 | 2630432.0947 | 1236902.5807 | 2630425.1552 | 1236886.3116
41 | 2630405.9881 | 1236841.3757 | 2630425.1552 | 1236886.3116
42 | 2630031.9665 | 1236520.4836 | 2630053.0112 | 1236539.3829 | 2630056.4346 | 1236540.1896 | 2630060.667 | 1236538.1096 | 2630076.6275 | 1236518.757
43 | 2630077.9002 | 1236517.2139 | 2630076.6275 | 1236518.757
44 | 2630031.9665 | 1236520.4836 | 2630021.5122 | 1236511.0951 | 2630014.1394 | 1236503.7458
45 | 2630077.9002 | 1236517.2139 | 2630104.8851 | 1236484.4939
46 | 2630013.3622 | 1236502.9711 | 2630014.1394 | 1236503.7458
47 | 2630104.8851 | 1236484.4939 | 2630109.889 | 1236478.4265
48 | 2630013.3622 | 1236502.9711 | 2630012.1309 | 1236501.7438
49 | 2630110.9998 | 1236477.0797 | 2630109.889 | 1236478.4265
50 | 2629981.4291 | 1236469.9178 | 2629986.6031 | 1236476.2974 | 2630012.1309 | 1236501.7438
51 | 2630139.606 | 1236442.3938 | 2630110.9998 | 1236477.0797
52 | 2630017.1621 | 1236389.0485 | 2630014.0656 | 1236389.9599 | 2630007.0437 | 1236393.1583
53 | 2629960.2831 | 1236424.2044 | 2629974.002 | 1236413.9062 | 2629989.9039 | 1236402.4014 | 2629998.3974 | 1236397.0964 | 2630007.0437 | 1236393.1583
54 | 2629951.7864 | 1236430.5825 | 2629960.2831 | 1236424.2044
55 | 2629951.7864 | 1236430.5825 | 2629933.6773 | 1236443.9797
56 | 2629951.7864 | 1236430.5825 | 2629962.9311 | 1236446.3776
57 | 2630246.4523 | 1236538.5911 | 2630262.5519 | 1236515.0631 | 2630269.5225 | 1236506.3069
58 | 2630246.4523 | 1236538.5911 | 2630246.4274 | 1236538.6276
59 | 2630283.3026 | 1236488.9969 | 2630269.5225 | 1236506.3069
60 | 2630246.4274 | 1236538.6276 | 2630235.3619 | 1236554.7988
61 | 2630218.948 | 1236574.5564 | 2630226.3357 | 1236567.9898 | 2630235.3619 | 1236554.7988
62 | 2630218.948 | 1236574.5564 | 2630228.5221 | 1236587.9743
63 | 2630216.4685 | 1236571.1639 | 2630218.948 | 1236574.5564
64 | 2630230.3137 | 1236590.4851 | 2630228.5221 | 1236587.9743
65 | 2630216.4685 | 1236571.1639 | 2630205.9406 | 1236580.976
66 | 2630216.4685 | 1236571.1639 | 2630195.4365 | 1236542.4726
67 | 2630255.1944 | 1236470.0243 | 2630231.9525 | 1236499.7754
68 | 2630211.3257 | 1236526.1788 | 2630231.9525 | 1236499.7754
69 | 2630195.4365 | 1236542.4726 | 2630207.8066 | 1236530.6836 | 2630211.3257 | 1236526.1788
70 | 2630195.4365 | 1236542.4726 | 2630179.5379 | 1236519.0217
71 | 2630179.5379 | 1236519.0217 | 2630170.2705 | 1236505.3551
72 | 2630179.5379 | 1236519.0217 | 2630185.2404 | 1236513.5361 | 2630199.7277 | 1236494.5645 | 2630206.4867 | 1236484.2347
73 | 2630170.2705 | 1236505.3551 | 2630161.1694 | 1236488.1125
74 | 2630170.2705 | 1236505.3551 | 2630165.3717 | 1236509.0326 | 2630154.1364 | 1236523.7807
75 | 2630218.1661 | 1236466.385 | 2630206.4867 | 1236484.2347
76 | 2630186.5785 | 1236604.6664 | 2630203.56 | 1236583.1947 | 2630205.9406 | 1236580.976
77 | 2629979.5579 | 1236467.6105 | 2629981.4291 | 1236469.9178
78 | 2629965.8874 | 1236450.5674 | 2629966.9019 | 1236452.0053 | 2629979.5579 | 1236467.6105
79 | 2629962.9311 | 1236446.3776 | 2629965.8874 | 1236450.5674
80 | 2629921.8227 | 1236452.7497 | 2629921.9776 | 1236452.6351 | 2629933.6773 | 1236443.9797
81 | 2630419.1073 | 1236832.9362 | 2630435.9263 | 1236822.1167 | 2630450.6319 | 1236813.7526
82 | 2630405.9881 | 1236841.3757 | 2630419.1073 | 1236832.9362
83 | 2630450.6319 | 1236813.7526 | 2630479.3261 | 1236797.4321
84 | 2630405.9881 | 1236841.3757 | 2630398.8781 | 1236829.1873 | 2630392.1971 | 1236818.9023 | 2630364.7297 | 1236791.4116 | 2630356.1407 | 1236781.9698
85 | 2630356.1407 | 1236781.9698 | 2630353.1358 | 1236778.6667 | 2630344.9206 | 1236765.793
86 | 2630356.1407 | 1236781.9698 | 2630125.6596 | 1236973.5727
87 | 2630344.9206 | 1236765.793 | 2630342.53 | 1236762.0467 | 2630329.3377 | 1236739.2763 | 2630323.8012 | 1236729.7225
88 | 2630323.8012 | 1236729.7225 | 2630318.2228 | 1236720.0966 | 2630309.0653 | 1236704.2919
89 | 2629921.8227 | 1236452.7497 | 2629905.0202 | 1236465.1771
90 | 2629900.0511 | 1236468.8524 | 2629905.0202 | 1236465.1771
91 | 2630221.7063 | 1236675.0395 | 2630220.8578 | 1236674.4054
92 | 2630235.4767 | 1236685.3316 | 2630221.7063 | 1236675.0395
93 | 2630198.9549 | 1236658.0349 | 2630220.8578 | 1236674.4054
94 | 2630263.8154 | 1236638.4576 | 2630258.4086 | 1236649.7705 | 2630235.4767 | 1236685.3316
95 | 2630196.1013 | 1236655.9022 | 2630198.9549 | 1236658.0349
96 | 2630263.8154 | 1236638.4576 | 2630256.8599 | 1236628.29
97 | 2630263.8154 | 1236638.4576 | 2630283.4026 | 1236666.4967
98 | 2630253.9102 | 1236623.9781 | 2630256.8599 | 1236628.29
99 | 2630283.4026 | 1236666.4967 | 2630294.0032 | 1236681.6715 | 2630305.4428 | 1236698.0399 | 2630309.0653 | 1236704.2919
100 | 2630246.9024 | 1236613.7339 | 2630253.9102 | 1236623.9781
101 | 2630151.09 | 1236467.7516 | 2630155.1247 | 1236476.6604 | 2630161.1694 | 1236488.1125
102 | 2630154.1364 | 1236523.7807 | 2630133.4577 | 1236550.925
103 | 2630141.6257 | 1236446.8537 | 2630151.09 | 1236467.7516
104 | 2630126.358 | 1236560.2446 | 2630133.4577 | 1236550.925
105 | 2630131.5859 | 1236425.4305 | 2630134.0715 | 1236430.6879
106 | 2630139.606 | 1236442.3938 | 2630134.0715 | 1236430.6879
107 | 2630131.5859 | 1236425.4305 | 2630131.3335 | 1236424.8967
108 | 2630139.606 | 1236442.3938 | 2630141.6257 | 1236446.8537
109 | 2630127.7741 | 1236417.9368 | 2630129.2153 | 1236420.4164 | 2630131.3335 | 1236424.8967
110 | 2630127.7741 | 1236417.9368 | 2630121.7818 | 1236407.6263 | 2630115.8906 | 1236398.9706
111 | 2630372.047 | 1236542.4855 | 2630373.93 | 1236544.4064
112 | 2630126.358 | 1236560.2446 | 2630118.8927 | 1236570.0439
113 | 2630126.358 | 1236560.2446 | 2630139.6716 | 1236569.8319
114 | 2630109.9895 | 1236581.7307 | 2630118.8927 | 1236570.0439
115 | 2630152.7131 | 1236579.2232 | 2630139.6716 | 1236569.8319
116 | 2630109.9895 | 1236581.7307 | 2630140.1946 | 1236606.7364
117 | 2630143.4865 | 1236282.1615 | 2630163.9533 | 1236290.4559 | 2630158.1155 | 1236304.6685 | 2630167.9368 | 1236309.1433 | 2630177.2972 | 1236310.5138 | 2630181.8545 | 1236312.1495
118 | 2630126.2814 | 1236275.1889 | 2630143.4865 | 1236282.1615
119 | 2630209.4113 | 1236322.0395 | 2630181.8545 | 1236312.1495
120 | 2630253.6145 | 1236317.5947 | 2630245.4036 | 1236326.7698 | 2630233.0318 | 1236328.3857 | 2630209.4113 | 1236322.0395
121 | 2630209.4113 | 1236322.0395 | 2630203.2853 | 1236322.9646 | 2630198.6985 | 1236327.7331 | 2630195.8894 | 1236337.058 | 2630188.4254 | 1236340.7224 | 2630181.5134 | 1236340.3103
122 | 2630253.6145 | 1236317.5947 | 2630295.9568 | 1236334.4026
123 | 2630295.1656 | 1236547.3513 | 2630283.9549 | 1236563.1985
124 | 2630246.9024 | 1236613.7339 | 2630230.3137 | 1236590.4851

## bus_geodata
| x | y | coords
0 | 2629732.6981 | 1236639.4675
1 | 2629744.9014 | 1236623.9984
2 | 2629765.1436 | 1236637.2067
3 | 2629751.4742 | 1236616.3556
4 | 2629842.5376 | 1236520.7403
5 | 2629878.2049 | 1236487.3208
6 | 2629778.95 | 1236584.6216
7 | 2629761.4055 | 1236604.8074
8 | 2629777.8457 | 1236585.7949
9 | 2630072.5722 | 1236327.8864
10 | 2630067.1762 | 1236303.4343
11 | 2630076.8448 | 1236337.4109
12 | 2630064.3373 | 1236283.5697
13 | 2630092.7859 | 1236364.5973
14 | 2630098.9153 | 1236323.6541
15 | 2630084.6607 | 1236255.2731
16 | 2630098.9894 | 1236373.9564
17 | 2630111.1376 | 1236310.1785
18 | 2630030.7372 | 1236385.0531
19 | 2630029.409 | 1236385.444
20 | 2630112.5092 | 1236394.0025
21 | 2630114.2413 | 1236303.0074
22 | 2630320.4044 | 1236511.6741
23 | 2630314.8479 | 1236519.5287
24 | 2630329.3907 | 1236498.9712
25 | 2630307.5253 | 1236529.8798
26 | 2630324.0384 | 1236493.772
27 | 2630331.4944 | 1236501.1172
28 | 2630305.2562 | 1236533.0874
29 | 2630301.3685 | 1236472.4871
30 | 2630341.1168 | 1236510.9331
31 | 2630295.2228 | 1236547.2704
32 | 2630278.5197 | 1236453.5372
33 | 2630358.4527 | 1236528.6178
34 | 2630506.3852 | 1236871.1537
35 | 2630486.8364 | 1236879.4234
36 | 2630466.4221 | 1236888.0592
37 | 2630432.0947 | 1236902.5807
38 | 2630425.1552 | 1236886.3116
39 | 2630076.6275 | 1236518.757
40 | 2630031.9665 | 1236520.4836
41 | 2630077.9002 | 1236517.2139
42 | 2630014.1394 | 1236503.7458
43 | 2630104.8851 | 1236484.4939
44 | 2630013.3622 | 1236502.9711
45 | 2630109.889 | 1236478.4265
46 | 2630012.1309 | 1236501.7438
47 | 2630110.9998 | 1236477.0797
48 | 2630017.1621 | 1236389.0485
49 | 2630007.0437 | 1236393.1583
50 | 2629960.2831 | 1236424.2044
51 | 2629951.7864 | 1236430.5825
52 | 2630246.4523 | 1236538.5911
53 | 2630269.5225 | 1236506.3069
54 | 2630246.4274 | 1236538.6276
55 | 2630283.3026 | 1236488.9969
56 | 2630235.3619 | 1236554.7988
57 | 2630218.948 | 1236574.5564
58 | 2630228.5221 | 1236587.9743
59 | 2630216.4685 | 1236571.1639
60 | 2630231.9525 | 1236499.7754
61 | 2630255.1944 | 1236470.0243
62 | 2630211.3257 | 1236526.1788
63 | 2630195.4365 | 1236542.4726
64 | 2630179.5379 | 1236519.0217
65 | 2630170.2705 | 1236505.3551
66 | 2630206.4867 | 1236484.2347
67 | 2630205.9406 | 1236580.976
68 | 2629979.5579 | 1236467.6105
69 | 2629981.4291 | 1236469.9178
70 | 2629965.8874 | 1236450.5674
71 | 2629962.9311 | 1236446.3776
72 | 2629933.6773 | 1236443.9797
73 | 2630419.1073 | 1236832.9362
74 | 2630450.6319 | 1236813.7526
75 | 2630405.9881 | 1236841.3757
76 | 2630479.3261 | 1236797.4321
77 | 2630356.1407 | 1236781.9699
78 | 2630344.9206 | 1236765.793
79 | 2630125.6596 | 1236973.5727
80 | 2630323.8012 | 1236729.7225
81 | 2629921.8227 | 1236452.7497
82 | 2629905.0202 | 1236465.1771
83 | 2629900.0511 | 1236468.8524
84 | 2630221.7063 | 1236675.0395
85 | 2630220.8578 | 1236674.4054
86 | 2630235.4767 | 1236685.3316
87 | 2630198.9549 | 1236658.0349
88 | 2630263.8154 | 1236638.4576
89 | 2630196.1013 | 1236655.9022
90 | 2630256.8599 | 1236628.29
91 | 2630283.4026 | 1236666.4967
92 | 2630253.9102 | 1236623.9781
93 | 2630309.0653 | 1236704.2919
94 | 2630218.1661 | 1236466.385
95 | 2630161.1694 | 1236488.1125
96 | 2630154.1364 | 1236523.7807
97 | 2630151.09 | 1236467.7516
98 | 2630133.4577 | 1236550.925
99 | 2630134.0715 | 1236430.6879
100 | 2630131.5859 | 1236425.4305
101 | 2630139.606 | 1236442.3938
102 | 2630131.3335 | 1236424.8967
103 | 2630141.6257 | 1236446.8537
104 | 2630127.7741 | 1236417.9368
105 | 2630115.8906 | 1236398.9706
106 | 2630372.047 | 1236542.4855
107 | 2630373.93 | 1236544.4064
108 | 2630126.358 | 1236560.2446
109 | 2630118.8927 | 1236570.0439
110 | 2630139.6716 | 1236569.8319
111 | 2630109.9895 | 1236581.7307
112 | 2630152.7131 | 1236579.2232
113 | 2630143.4865 | 1236282.1615
114 | 2630181.8545 | 1236312.1495
115 | 2630126.2814 | 1236275.1889
116 | 2630209.4113 | 1236322.0395
117 | 2630253.6145 | 1236317.5947
118 | 2630181.5134 | 1236340.3103
119 | 2630295.9568 | 1236334.4026
120 | 2630295.1656 | 1236547.3513
121 | 2630283.9549 | 1236563.1985
122 | 2630246.9024 | 1236613.7339
123 | 2630230.3137 | 1236590.4851
124 | 2630186.5785 | 1236604.6664
125 | 2630140.1946 | 1236606.7364
126 | 2630170.2705 | 1236505.3551

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97037 | -0.20907 | 0.0012698 | 0.00031823
1 | 0.9704 | -0.20881 | 0 | 0
2 | 0.97038 | -0.20898 | 0.00066358 | 0.00016631
3 | 0.97043 | -0.2086 | 0.0019695 | 0.0004936
4 | 0.97172 | -0.19933 | 0.00062152 | 0.00015577
5 | 0.97231 | -0.19502 | 0.0010955 | 0.00027455
6 | 0.97069 | -0.20671 | 0.00087274 | 0.00021873
7 | 0.97052 | -0.20797 | 0.00037058 | 9.2877e-05
8 | 0.97068 | -0.20683 | 0.0025759 | 0.00064559
9 | 0.98709 | -0.090275 | 0.0016761 | 0.00042006
10 | 0.9868 | -0.092333 | 0.0055343 | 0.001387
11 | 0.98724 | -0.089239 | 0 | 0
12 | 0.98673 | -0.092841 | 0 | 0
13 | 0.98837 | -0.081207 | 0 | 0
14 | 0.98666 | -0.093314 | 0.0026386 | 0.00066131
15 | 0.9866 | -0.093791 | 0.0024653 | 0.00061786
16 | 0.98877 | -0.078347 | 0.0022256 | 0.00055779
17 | 0.98633 | -0.095683 | 0 | 0
18 | 0.97186 | -0.19826 | 0.0090514 | 0.0022685
19 | 0.97188 | -0.19813 | 0.0022463 | 0.00056298
20 | 0.98972 | -0.071649 | 0.0050349 | 0.0012619
21 | 0.98619 | -0.096693 | 0.0015666 | 0.00039262
22 | 0.9856 | -0.10085 | 0.0018004 | 0.00045122
23 | 0.98546 | -0.10189 | 0.0022748 | 0.00057011
24 | 0.98588 | -0.098886 | 0 | 0
25 | 0.98531 | -0.10297 | 0.0019685 | 0.00049335
26 | 0.9861 | -0.097317 | 0.00092673 | 0.00023226
27 | 0.98584 | -0.099138 | 0.00061575 | 0.00015432
28 | 0.98527 | -0.10322 | 0.0016006 | 0.00040114
29 | 0.98706 | -0.090484 | 0.00033418 | 8.3754e-05
30 | 0.98569 | -0.10021 | 0.0019095 | 0.00047855
31 | 0.98515 | -0.10405 | 0.0016688 | 0.00041825
32 | 0.988 | -0.083871 | 0.0003044 | 7.6289e-05
33 | 0.98549 | -0.10164 | 0.0013336 | 0.00033422
34 | 0.97774 | -0.15684 | 0.0011283 | 0.00028278
35 | 0.97778 | -0.15659 | 0.0012606 | 0.00031594
36 | 0.97786 | -0.15603 | 0.0011731 | 0.000294
37 | 0.97805 | -0.15465 | 0 | 0
38 | 0.97814 | -0.15399 | 0.0017491 | 0.00043835
39 | 0.9849 | -0.10536 | 0.0061971 | 0.0015531
40 | 0.98007 | -0.13953 | 0.0087085 | 0.0021826
41 | 0.98507 | -0.10413 | 0.015742 | 0.0039453
42 | 0.97846 | -0.15098 | 0.0023866 | 0.00059814
43 | 0.98974 | -0.071308 | 0.0059279 | 0.0014857
44 | 0.97839 | -0.15146 | 0.0023866 | 0.00059814
45 | 0.99068 | -0.064782 | 0.0014828 | 0.00037162
46 | 0.97829 | -0.15219 | 0.0047158 | 0.0011819
47 | 0.99089 | -0.063308 | 0.0010607 | 0.00026584
48 | 0.97209 | -0.19661 | 0.0019494 | 0.00048855
49 | 0.9723 | -0.19508 | 0.0013572 | 0.00034014
50 | 0.97351 | -0.1864 | 0.0031732 | 0.00079527
51 | 0.97379 | -0.18442 | 0 | 0
52 | 0.98862 | -0.079466 | 0.00077053 | 0.00019311
53 | 0.98855 | -0.079977 | 0.00098762 | 0.00024752
54 | 0.98862 | -0.079465 | 0.0010507 | 0.00026332
55 | 0.98854 | -0.080038 | 0.00026811 | 6.7196e-05
56 | 0.98871 | -0.078848 | 0.0042816 | 0.0010731
57 | 0.98898 | -0.076903 | 0 | 0
58 | 0.98794 | -0.084232 | 0.0041527 | 0.0010408
59 | 0.98929 | -0.074723 | 0 | 0
60 | 0.99026 | -0.067927 | 0.00039832 | 9.9829e-05
61 | 0.98903 | -0.076598 | 0.00047242 | 0.0001184
62 | 0.99137 | -0.060112 | 0.00098119 | 0.00024591
63 | 0.99215 | -0.054576 | 0 | 0
64 | 0.99541 | -0.031783 | 0 | 0
65 | 0.99735 | -0.018311 | 0 | 0
66 | 0.99532 | -0.032468 | 0.0012621 | 0.00031631
67 | 0.98919 | -0.075435 | 0.0013848 | 0.00034707
68 | 0.97584 | -0.16968 | 0.0045636 | 0.0011437
69 | 0.97599 | -0.16859 | 0.00030788 | 7.7162e-05
70 | 0.97486 | -0.17669 | 0.00018552 | 4.6496e-05
71 | 0.97463 | -0.17833 | 0.00044049 | 0.0001104
72 | 0.97339 | -0.1873 | 0.00065264 | 0.00016357
73 | 0.97843 | -0.15194 | 0.0010557 | 0.00026459
74 | 0.97826 | -0.15312 | 0.0010268 | 0.00025735
75 | 0.97852 | -0.15128 | 0 | 0
76 | 0.97817 | -0.15381 | 0.0020119 | 0.00050424
77 | 0.97959 | -0.14362 | 0.0030412 | 0.0007622
78 | 0.98006 | -0.14024 | 0.00071301 | 0.0001787
79 | 0.97786 | -0.15602 | 0.0039589 | 0.0009922
80 | 0.9811 | -0.13279 | 0.0017305 | 0.0004337
81 | 0.97314 | -0.18909 | 0.00054967 | 0.00013776
82 | 0.9728 | -0.1915 | 0.00087081 | 0.00021825
83 | 0.97271 | -0.19216 | 0.00061522 | 0.00015419
84 | 0.98418 | -0.11087 | 0.0016951 | 0.00042483
85 | 0.98417 | -0.11092 | 0.0019517 | 0.00048915
86 | 0.98432 | -0.10985 | 0 | 0
87 | 0.98409 | -0.11152 | 0.00086312 | 0.00021632
88 | 0.98478 | -0.10658 | 0 | 0
89 | 0.98408 | -0.11156 | 0.0012663 | 0.00031736
90 | 0.98534 | -0.10262 | 0.0032247 | 0.00080818
91 | 0.98352 | -0.11556 | 0.0011872 | 0.00029754
92 | 0.9856 | -0.10077 | 0.0019395 | 0.0004861
93 | 0.98191 | -0.12703 | 0.0053589 | 0.0013431
94 | 0.99531 | -0.032527 | 0.00027404 | 6.8682e-05
95 | 0.99602 | -0.027539 | 0.0034382 | 0.0008617
96 | 1 | 0 | -0.23459 | -0.059032
97 | 0.99451 | -0.038065 | 0.0042608 | 0.0010679
98 | 0.99961 | -0.0027093 | 0.0014183 | 0.00035547
99 | 0.99188 | -0.056435 | 0.00196 | 0.00049122
100 | 0.99152 | -0.058977 | 0.0013782 | 0.0003454
101 | 0.99272 | -0.050524 | 0 | 0
102 | 0.99148 | -0.059227 | 0.0036991 | 0.00092707
103 | 0.99303 | -0.04839 | 0.0044868 | 0.0011245
104 | 0.99105 | -0.062247 | 0.005378 | 0.0013478
105 | 0.99 | -0.069678 | 0.00042286 | 0.00010598
106 | 0.98537 | -0.1025 | 0.0023135 | 0.00057982
107 | 0.98536 | -0.10256 | 0.0019946 | 0.00049989
108 | 0.9995 | -0.0034737 | 0 | 0
109 | 0.99944 | -0.0039018 | 0.0017815 | 0.00044648
110 | 0.99943 | -0.0039739 | 0.0013137 | 0.00032923
111 | 0.99941 | -0.0041507 | 0 | 0
112 | 0.99939 | -0.0042527 | 0.0017354 | 0.00043494
113 | 0.98541 | -0.10223 | 0.0034495 | 0.00086452
114 | 0.98472 | -0.10711 | 0.0016085 | 0.00040312
115 | 0.9857 | -0.10013 | 0 | 0
116 | 0.98447 | -0.1089 | 0 | 0
117 | 0.98411 | -0.11149 | 0 | 0
118 | 0.98442 | -0.10924 | 0.00085546 | 0.0002144
119 | 0.98377 | -0.11388 | 0.0050955 | 0.0012771
120 | 0.98515 | -0.10406 | 0.0011408 | 0.00028591
121 | 0.9851 | -0.10443 | 0.0018556 | 0.00046506
122 | 0.98626 | -0.096131 | 0 | 0
123 | 0.98776 | -0.085474 | 0.0029505 | 0.00073946
124 | 0.98904 | -0.076517 | 0.00346 | 0.00086717
125 | 0.99931 | -0.004814 | 0.0016909 | 0.00042378
126 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0012698 | -0.00031823 | 0.0012698 | 0.00031801 | 4.6677e-08 | -2.258e-07 | 0.0019471 | 0.001947 | 0.0019471 | 0.97037 | -0.20907 | 0.9704 | -0.20881 | 0.72116
1 | 0.0006636 | 0.00016602 | -0.00066358 | -0.00016631 | 1.5615e-08 | -2.9259e-07 | 0.0010174 | 0.0010176 | 0.0010176 | 0.9704 | -0.20881 | 0.97038 | -0.20898 | 0.37687
2 | -0.0019334 | -0.00048402 | 0.0019335 | 0.00048392 | 5.5278e-08 | -1.0328e-07 | 0.0029645 | 0.0029644 | 0.0029645 | 0.9704 | -0.20881 | 0.97043 | -0.2086 | 1.098
3 | -0.003903 | -0.00097752 | 0.0039033 | 0.00097746 | 3.4037e-07 | -5.7286e-08 | 0.0059844 | 0.0059843 | 0.0059844 | 0.97043 | -0.2086 | 0.97052 | -0.20797 | 2.2164
4 | -0.0083527 | -0.0020923 | 0.0083577 | 0.0020936 | 4.9895e-06 | 1.3132e-06 | 0.01279 | 0.01279 | 0.01279 | 0.97172 | -0.19933 | 0.97231 | -0.19502 | 4.7372
5 | 0.0077312 | 0.0019365 | -0.0077233 | -0.0019346 | 7.883e-06 | 1.9165e-06 | 0.011839 | 0.011839 | 0.011839 | 0.97172 | -0.19933 | 0.97069 | -0.20671 | 4.3848
6 | -0.0094532 | -0.0023682 | 0.0094569 | 0.0023693 | 3.7415e-06 | 1.0835e-06 | 0.014467 | 0.014466 | 0.014467 | 0.97231 | -0.19502 | 0.97271 | -0.19216 | 5.358
7 | 0.0068506 | 0.0017159 | -0.0068505 | -0.0017159 | 1.1087e-07 | 2.2726e-08 | 0.010501 | 0.010501 | 0.010501 | 0.97069 | -0.20671 | 0.97068 | -0.20683 | 3.8893
8 | -0.0042739 | -0.0010703 | 0.0042746 | 0.0010703 | 6.7342e-07 | -5.1652e-08 | 0.0065525 | 0.0065524 | 0.0065525 | 0.97052 | -0.20797 | 0.97068 | -0.20683 | 2.4269
9 | 0.0080024 | 0.0020049 | -0.0080001 | -0.0020043 | 2.2778e-06 | 5.5553e-07 | 0.012063 | 0.012063 | 0.012063 | 0.98709 | -0.090275 | 0.9868 | -0.092333 | 4.4679
10 | -0.0096784 | -0.002425 | 0.0096798 | 0.0024254 | 1.3872e-06 | 4.0002e-07 | 0.01459 | 0.01459 | 0.01459 | 0.98709 | -0.090275 | 0.98724 | -0.089239 | 5.4036
11 | 0.0024658 | 0.00061731 | -0.0024656 | -0.0006175 | 1.7312e-07 | -1.8979e-07 | 0.003718 | 0.0037181 | 0.0037181 | 0.9868 | -0.092333 | 0.98673 | -0.092841 | 1.3771
12 | -0.024927 | -0.0062469 | 0.024955 | 0.0062572 | 2.7746e-05 | 1.0268e-05 | 0.037571 | 0.037571 | 0.037571 | 0.98724 | -0.089239 | 0.98837 | -0.081207 | 13.9152
13 | 0.015247 | 0.0038216 | -0.015239 | -0.0038186 | 8.5986e-06 | 2.9737e-06 | 0.022981 | 0.022982 | 0.022982 | 0.98724 | -0.089239 | 0.98666 | -0.093314 | 8.5117
14 | 0.0024656 | 0.0006175 | -0.0024653 | -0.00061786 | 3.2391e-07 | -3.5497e-07 | 0.0037181 | 0.0037182 | 0.0037182 | 0.98673 | -0.092841 | 0.9866 | -0.093791 | 1.3771
15 | -0.024955 | -0.0062572 | 0.024965 | 0.0062609 | 9.8938e-06 | 3.6613e-06 | 0.037571 | 0.037571 | 0.037571 | 0.98837 | -0.081207 | 0.98877 | -0.078347 | 13.9152
16 | 0.0126 | 0.0031573 | -0.012596 | -0.003156 | 4.1285e-06 | 1.3539e-06 | 0.019002 | 0.019002 | 0.019002 | 0.98666 | -0.093314 | 0.98633 | -0.095683 | 7.0379
17 | -0.02719 | -0.0068187 | 0.027215 | 0.0068281 | 2.5265e-05 | 9.4069e-06 | 0.04092 | 0.04092 | 0.04092 | 0.98877 | -0.078347 | 0.98972 | -0.071649 | 15.1557
18 | 0.012596 | 0.003156 | -0.012594 | -0.0031554 | 1.7606e-06 | 5.7745e-07 | 0.019002 | 0.019002 | 0.019002 | 0.98633 | -0.095683 | 0.98619 | -0.096693 | 7.0379
19 | -0.0090514 | -0.0022685 | 0.0090516 | 0.0022685 | 1.6593e-07 | 4.6663e-08 | 0.013859 | 0.013859 | 0.013859 | 0.97186 | -0.19826 | 0.97188 | -0.19813 | 5.1328
20 | -0.011298 | -0.0028315 | 0.0113 | 0.0028323 | 2.3836e-06 | 7.5854e-07 | 0.017298 | 0.017298 | 0.017298 | 0.97188 | -0.19813 | 0.97209 | -0.19661 | 6.4066
21 | -0.03225 | -0.0080899 | 0.032259 | 0.0080932 | 8.8173e-06 | 3.314e-06 | 0.04849 | 0.04849 | 0.04849 | 0.98972 | -0.071649 | 0.99 | -0.069678 | 17.9593
22 | 0.011027 | 0.0027628 | -0.011022 | -0.0027611 | 5.2364e-06 | 1.6274e-06 | 0.016639 | 0.016639 | 0.016639 | 0.98619 | -0.096693 | 0.9857 | -0.10013 | 6.1625
23 | 0.010513 | 0.0026344 | -0.010511 | -0.0026339 | 1.5124e-06 | 4.5908e-07 | 0.015871 | 0.015871 | 0.015871 | 0.9856 | -0.10085 | 0.98546 | -0.10189 | 5.8783
24 | -0.012313 | -0.0030856 | 0.012316 | 0.0030867 | 3.3553e-06 | 1.0922e-06 | 0.01859 | 0.01859 | 0.01859 | 0.9856 | -0.10085 | 0.98588 | -0.098886 | 6.885
25 | 0.0082364 | 0.0020638 | -0.0082352 | -0.0020635 | 1.2237e-06 | 3.0915e-07 | 0.012437 | 0.012437 | 0.012437 | 0.98546 | -0.10189 | 0.98531 | -0.10297 | 4.6062
26 | -0.020486 | -0.0051339 | 0.020491 | 0.0051355 | 4.4517e-06 | 1.617e-06 | 0.03092 | 0.03092 | 0.03092 | 0.98588 | -0.098886 | 0.9861 | -0.097317 | 11.452
27 | 0.0081699 | 0.0020472 | -0.0081696 | -0.0020471 | 2.8512e-07 | 7.1344e-08 | 0.012331 | 0.012331 | 0.012331 | 0.98588 | -0.098886 | 0.98584 | -0.099138 | 4.567
28 | 0.0062667 | 0.0015702 | -0.0062665 | -0.0015701 | 2.1959e-07 | 3.4417e-08 | 0.0094639 | 0.0094639 | 0.0094639 | 0.98531 | -0.10297 | 0.98527 | -0.10322 | 3.5051
29 | -0.021418 | -0.0053678 | 0.021438 | 0.0053752 | 2.0277e-05 | 7.4016e-06 | 0.032319 | 0.032319 | 0.032319 | 0.9861 | -0.097317 | 0.98706 | -0.090484 | 11.9699
30 | 0.0075539 | 0.0018928 | -0.0075527 | -0.0018925 | 1.115e-06 | 2.5361e-07 | 0.011401 | 0.011402 | 0.011402 | 0.98584 | -0.099138 | 0.98569 | -0.10021 | 4.2228
31 | 0.0046659 | 0.001169 | -0.0046654 | -0.001169 | 5.383e-07 | -1.4192e-08 | 0.0070466 | 0.0070467 | 0.0070467 | 0.98527 | -0.10322 | 0.98515 | -0.10405 | 2.6099
32 | -0.021772 | -0.0054589 | 0.021792 | 0.0054662 | 1.9966e-05 | 7.2991e-06 | 0.032822 | 0.032822 | 0.032822 | 0.98706 | -0.090484 | 0.988 | -0.083871 | 12.1565
33 | 0.0056433 | 0.001414 | -0.0056422 | -0.0014138 | 1.1215e-06 | 1.1575e-07 | 0.008519 | 0.0085191 | 0.0085191 | 0.98569 | -0.10021 | 0.98549 | -0.10164 | 3.1552
34 | 0.0029965 | 0.00075077 | -0.0029965 | -0.00075077 | 1.2651e-09 | -7.739e-10 | 0.004526 | 0.004526 | 0.004526 | 0.98515 | -0.10405 | 0.98515 | -0.10406 | 1.6763
35 | -0.022096 | -0.0055425 | 0.022119 | 0.0055507 | 2.2309e-05 | 8.1665e-06 | 0.033281 | 0.033281 | 0.033281 | 0.988 | -0.083871 | 0.98903 | -0.076598 | 12.3262
36 | 0.0043086 | 0.0010796 | -0.0043081 | -0.0010797 | 5.1286e-07 | -5.0148e-08 | 0.0065056 | 0.0065056 | 0.0065056 | 0.98549 | -0.10164 | 0.98537 | -0.1025 | 2.4095
37 | -0.0011283 | -0.00028278 | 0.0011283 | 0.00028253 | 3.9051e-08 | -2.512e-07 | 0.0017171 | 0.001717 | 0.0017171 | 0.97774 | -0.15684 | 0.97778 | -0.15659 | 0.63598
38 | -0.0023889 | -0.00059846 | 0.0023891 | 0.00059825 | 1.828e-07 | -2.0773e-07 | 0.0036355 | 0.0036354 | 0.0036355 | 0.97778 | -0.15659 | 0.97786 | -0.15603 | 1.3465
39 | -0.0035622 | -0.00089225 | 0.0035629 | 0.00089205 | 6.8333e-07 | -2.0485e-07 | 0.0054204 | 0.0054203 | 0.0054204 | 0.97786 | -0.15603 | 0.97805 | -0.15465 | 2.0076
40 | -0.0035629 | -0.00089205 | 0.0035632 | 0.00089195 | 3.2425e-07 | -9.7278e-08 | 0.0054203 | 0.0054202 | 0.0054203 | 0.97805 | -0.15465 | 0.97814 | -0.15399 | 2.0075
41 | -0.0053122 | -0.0013303 | 0.0053142 | 0.0013305 | 1.9906e-06 | 1.5219e-07 | 0.008081 | 0.0080807 | 0.008081 | 0.97814 | -0.15399 | 0.97852 | -0.15128 | 2.993
42 | 0.054142 | 0.013635 | -0.053885 | -0.013536 | 0.00025736 | 9.8206e-05 | 0.081823 | 0.081824 | 0.081824 | 0.9849 | -0.10536 | 0.98007 | -0.13953 | 30.3051
43 | -0.060339 | -0.015188 | 0.06035 | 0.015192 | 1.0378e-05 | 3.9661e-06 | 0.091186 | 0.091186 | 0.091186 | 0.9849 | -0.10536 | 0.98507 | -0.10413 | 33.7727
44 | 0.045176 | 0.011354 | -0.045105 | -0.011326 | 7.1835e-05 | 2.7321e-05 | 0.068602 | 0.068602 | 0.068602 | 0.98007 | -0.13953 | 0.97846 | -0.15098 | 25.4081
45 | -0.076092 | -0.019137 | 0.076442 | 0.019271 | 0.00034979 | 0.00013399 | 0.11497 | 0.11497 | 0.11497 | 0.98507 | -0.10413 | 0.98974 | -0.071308 | 42.5798
46 | 0.042718 | 0.010728 | -0.042715 | -0.010727 | 2.8907e-06 | 1.098e-06 | 0.064972 | 0.064972 | 0.064972 | 0.97846 | -0.15098 | 0.97839 | -0.15146 | 24.0639
47 | -0.08237 | -0.020757 | 0.082445 | 0.020786 | 7.531e-05 | 2.8864e-05 | 0.12388 | 0.12388 | 0.12388 | 0.98974 | -0.071308 | 0.99068 | -0.064782 | 45.8806
48 | 0.040329 | 0.010129 | -0.040324 | -0.010128 | 4.0821e-06 | 1.5482e-06 | 0.061343 | 0.061343 | 0.061343 | 0.97839 | -0.15146 | 0.97829 | -0.15219 | 22.7195
49 | -0.083928 | -0.021157 | 0.083945 | 0.021164 | 1.7323e-05 | 6.6401e-06 | 0.1261 | 0.1261 | 0.1261 | 0.99068 | -0.064782 | 0.99089 | -0.063308 | 46.7055
50 | 0.035609 | 0.0089456 | -0.035528 | -0.008915 | 8.1039e-05 | 3.0614e-05 | 0.05417 | 0.05417 | 0.05417 | 0.97829 | -0.15219 | 0.97599 | -0.16859 | 20.0629
51 | -0.085006 | -0.02143 | 0.085158 | 0.021487 | 0.00015249 | 5.6911e-05 | 0.1277 | 0.1277 | 0.1277 | 0.99089 | -0.063308 | 0.99272 | -0.050524 | 15.7651
52 | -0.01325 | -0.0033208 | 0.013252 | 0.0033218 | 2.8091e-06 | 9.4472e-07 | 0.020282 | 0.020282 | 0.020282 | 0.97209 | -0.19661 | 0.9723 | -0.19508 | 7.5118
53 | -0.01461 | -0.0036619 | 0.014627 | 0.003668 | 1.7561e-05 | 6.0552e-06 | 0.022359 | 0.022359 | 0.022359 | 0.9723 | -0.19508 | 0.97351 | -0.1864 | 8.281
54 | -0.0178 | -0.0044632 | 0.017805 | 0.004465 | 4.9079e-06 | 1.7555e-06 | 0.027209 | 0.027209 | 0.027209 | 0.97351 | -0.1864 | 0.97379 | -0.18442 | 10.0773
55 | 0.012158 | 0.0030469 | -0.012153 | -0.0030453 | 4.8512e-06 | 1.5857e-06 | 0.018578 | 0.018578 | 0.018578 | 0.97379 | -0.18442 | 0.97339 | -0.1873 | 6.8806
56 | -0.029963 | -0.0075119 | 0.029988 | 0.0075214 | 2.5288e-05 | 9.4853e-06 | 0.045786 | 0.045786 | 0.045786 | 0.97379 | -0.18442 | 0.97463 | -0.17833 | 16.9578
57 | 0.0012558 | 0.00031396 | -0.0012557 | -0.00031443 | 8.8495e-08 | -4.7499e-07 | 0.0018899 | 0.0018901 | 0.0018901 | 0.98862 | -0.079466 | 0.98855 | -0.079977 | 0.70004
58 | -0.0020264 | -0.00050707 | 0.0020264 | 0.00050707 | 2.5553e-10 | -4.6788e-10 | 0.0030497 | 0.0030497 | 0.0030497 | 0.98862 | -0.079466 | 0.98862 | -0.079465 | 1.1295
59 | 0.00026812 | 6.6913e-05 | -0.00026811 | -6.7196e-05 | 2.2482e-09 | -2.8279e-07 | 0.00040348 | 0.00040358 | 0.00040358 | 0.98855 | -0.079977 | 0.98854 | -0.080038 | 0.14948
60 | -0.003077 | -0.0007704 | 0.0030773 | 0.00077024 | 2.6223e-07 | -1.5041e-07 | 0.0046311 | 0.004631 | 0.0046311 | 0.98862 | -0.079465 | 0.98871 | -0.078848 | 1.7152
61 | -0.0073589 | -0.0018433 | 0.0073608 | 0.0018437 | 1.9798e-06 | 4.2961e-07 | 0.011075 | 0.011075 | 0.011075 | 0.98871 | -0.078848 | 0.98898 | -0.076903 | 4.1018
62 | 0.043729 | 0.010986 | -0.043685 | -0.010969 | 4.4539e-05 | 1.6919e-05 | 0.065805 | 0.065805 | 0.065805 | 0.98898 | -0.076903 | 0.98794 | -0.084232 | 24.3721
63 | -0.05109 | -0.01283 | 0.051106 | 0.012836 | 1.5483e-05 | 5.901e-06 | 0.076879 | 0.076879 | 0.076879 | 0.98898 | -0.076903 | 0.98929 | -0.074723 | 28.4738
64 | 0.039532 | 0.0099287 | -0.039525 | -0.0099261 | 6.8254e-06 | 2.5857e-06 | 0.05955 | 0.05955 | 0.05955 | 0.98794 | -0.084232 | 0.98776 | -0.085474 | 22.0555
65 | 0.0048459 | 0.001214 | -0.0048454 | -0.001214 | 4.7707e-07 | -1.2746e-09 | 0.0072886 | 0.0072887 | 0.0072887 | 0.98929 | -0.074723 | 0.98919 | -0.075435 | 2.6995
66 | -0.055952 | -0.01405 | 0.056109 | 0.01411 | 0.00015711 | 5.997e-05 | 0.084168 | 0.084168 | 0.084168 | 0.98929 | -0.074723 | 0.99215 | -0.054576 | 31.1733
67 | 0.022618 | 0.0056791 | -0.022591 | -0.0056691 | 2.7219e-05 | 9.9838e-06 | 0.033991 | 0.033991 | 0.033991 | 0.99026 | -0.067927 | 0.98903 | -0.076598 | 12.5894
68 | -0.023017 | -0.0057789 | 0.023042 | 0.0057881 | 2.5014e-05 | 9.1894e-06 | 0.03459 | 0.03459 | 0.03459 | 0.99026 | -0.067927 | 0.99137 | -0.060112 | 12.811
69 | -0.024023 | -0.006034 | 0.024041 | 0.0060408 | 1.8506e-05 | 6.8234e-06 | 0.036062 | 0.036062 | 0.036062 | 0.99137 | -0.060112 | 0.99215 | -0.054576 | 13.3564
70 | -0.08015 | -0.020151 | 0.080405 | 0.020249 | 0.00025534 | 9.7841e-05 | 0.12023 | 0.12023 | 0.12023 | 0.99215 | -0.054576 | 0.99541 | -0.031783 | 44.5296
71 | -0.081942 | -0.020633 | 0.082096 | 0.020692 | 0.00015456 | 5.9232e-05 | 0.12253 | 0.12253 | 0.12253 | 0.99541 | -0.031783 | 0.99735 | -0.018311 | 45.38
72 | 0.0015363 | 0.00038419 | -0.0015361 | -0.00038471 | 1.452e-07 | -5.1773e-07 | 0.0022962 | 0.0022964 | 0.0022964 | 0.99541 | -0.031783 | 0.99532 | -0.032468 | 0.85053
73 | 0.14317 | 0.036128 | -0.14298 | -0.036058 | 0.00018519 | 7.0463e-05 | 0.21369 | 0.21369 | 0.21369 | 0.99735 | -0.018311 | 0.99602 | -0.027539 | 26.3817
74 | -0.22527 | -0.05682 | 0.22585 | 0.057042 | 0.00057996 | 0.00022209 | 0.33622 | 0.33622 | 0.33622 | 0.99735 | -0.018311 | 1 | 0 | 41.5083
75 | 0.00027405 | 6.8406e-05 | -0.00027404 | -6.8682e-05 | 2.2338e-09 | -2.7638e-07 | 0.00040961 | 0.0004097 | 0.0004097 | 0.99532 | -0.032468 | 0.99531 | -0.032527 | 0.15174
76 | 0.0034606 | 0.00086697 | -0.00346 | -0.00086717 | 5.1792e-07 | -1.9393e-07 | 0.0052055 | 0.0052057 | 0.0052057 | 0.98919 | -0.075435 | 0.98904 | -0.076517 | 1.928
77 | -0.035214 | -0.0088358 | 0.03522 | 0.0088379 | 5.3457e-06 | 2.0189e-06 | 0.053701 | 0.053701 | 0.053701 | 0.97584 | -0.16968 | 0.97599 | -0.16859 | 19.8891
78 | 0.030651 | 0.0076921 | -0.030621 | -0.0076809 | 2.9791e-05 | 1.1185e-05 | 0.046742 | 0.046742 | 0.046742 | 0.97584 | -0.16968 | 0.97486 | -0.17669 | 17.3118
79 | 0.030435 | 0.0076344 | -0.030429 | -0.0076318 | 6.9063e-06 | 2.5923e-06 | 0.046459 | 0.046459 | 0.046459 | 0.97486 | -0.17669 | 0.97463 | -0.17833 | 17.2069
80 | 0.0115 | 0.0028818 | -0.011497 | -0.0028809 | 2.8438e-06 | 9.1051e-07 | 0.01758 | 0.01758 | 0.01758 | 0.97339 | -0.1873 | 0.97314 | -0.18909 | 6.5111
81 | 0.0030395 | 0.00076097 | -0.003039 | -0.00076125 | 4.9217e-07 | -2.7427e-07 | 0.0046222 | 0.0046224 | 0.0046224 | 0.97843 | -0.15194 | 0.97826 | -0.15312 | 1.712
82 | -0.0040952 | -0.0010256 | 0.0040955 | 0.0010255 | 3.7753e-07 | -5.0732e-08 | 0.0062278 | 0.0062277 | 0.0062278 | 0.97843 | -0.15194 | 0.97852 | -0.15128 | 2.3066
83 | 0.0020121 | 0.0005039 | -0.0020119 | -0.00050424 | 1.9295e-07 | -3.402e-07 | 0.0030605 | 0.0030606 | 0.0030606 | 0.97826 | -0.15312 | 0.97817 | -0.15381 | 1.1336
84 | -0.0094098 | -0.002356 | 0.0094197 | 0.0023588 | 9.9645e-06 | 2.8516e-06 | 0.014308 | 0.014308 | 0.014308 | 0.97852 | -0.15128 | 0.97959 | -0.14362 | 5.2994
85 | -0.016427 | -0.0041121 | 0.016434 | 0.0041148 | 7.6671e-06 | 2.7003e-06 | 0.024951 | 0.024951 | 0.024951 | 0.97959 | -0.14362 | 0.98006 | -0.14024 | 9.241
86 | 0.0039657 | 0.00099105 | -0.0039589 | -0.0009922 | 6.7862e-06 | -1.1565e-06 | 0.006023 | 0.0060244 | 0.0060244 | 0.97959 | -0.14362 | 0.97786 | -0.15602 | 2.2312
87 | -0.017147 | -0.0042935 | 0.017165 | 0.0042997 | 1.7678e-05 | 6.272e-06 | 0.026033 | 0.026033 | 0.026033 | 0.98006 | -0.14024 | 0.9811 | -0.13279 | 9.6419
88 | -0.018896 | -0.0047334 | 0.018911 | 0.0047389 | 1.5062e-05 | 5.4217e-06 | 0.028658 | 0.028658 | 0.028658 | 0.9811 | -0.13279 | 0.98191 | -0.12703 | 10.614
89 | 0.010947 | 0.0027431 | -0.010944 | -0.002742 | 3.6542e-06 | 1.1459e-06 | 0.01674 | 0.01674 | 0.01674 | 0.97314 | -0.18909 | 0.9728 | -0.1915 | 6.1999
90 | 0.010073 | 0.0025237 | -0.010072 | -0.0025234 | 9.1556e-07 | 2.7541e-07 | 0.015408 | 0.015408 | 0.015408 | 0.9728 | -0.1915 | 0.97271 | -0.19216 | 5.7065
91 | 0.0040813 | 0.0010225 | -0.0040813 | -0.0010225 | 2.5167e-08 | -3.7806e-09 | 0.0061706 | 0.0061706 | 0.0061706 | 0.98418 | -0.11087 | 0.98417 | -0.11092 | 2.2854
92 | -0.0057764 | -0.0014473 | 0.0057772 | 0.0014474 | 8.1822e-07 | 9.6205e-08 | 0.0087334 | 0.0087334 | 0.0087334 | 0.98418 | -0.11087 | 0.98432 | -0.10985 | 3.2346
93 | 0.0021296 | 0.00053335 | -0.0021294 | -0.00053363 | 1.7689e-07 | -2.7941e-07 | 0.0032197 | 0.0032198 | 0.0032198 | 0.98417 | -0.11092 | 0.98409 | -0.11152 | 1.1925
94 | -0.0057772 | -0.0014474 | 0.0057799 | 0.0014477 | 2.6088e-06 | 3.0628e-07 | 0.0087334 | 0.0087331 | 0.0087334 | 0.98432 | -0.10985 | 0.98478 | -0.10658 | 3.2346
95 | 0.0012663 | 0.00031732 | -0.0012663 | -0.00031736 | 8.1497e-09 | -4.2127e-08 | 0.0019147 | 0.0019147 | 0.0019147 | 0.98409 | -0.11152 | 0.98408 | -0.11156 | 0.70915
96 | -0.031307 | -0.0078532 | 0.031324 | 0.0078597 | 1.7204e-05 | 6.4599e-06 | 0.047307 | 0.047307 | 0.047307 | 0.98478 | -0.10658 | 0.98534 | -0.10262 | 17.5213
97 | 0.025527 | 0.0064055 | -0.025495 | -0.0063937 | 3.1758e-05 | 1.178e-05 | 0.038574 | 0.038574 | 0.038574 | 0.98478 | -0.10658 | 0.98352 | -0.11556 | 14.2869
98 | -0.034549 | -0.0086679 | 0.034558 | 0.0086712 | 8.8751e-06 | 3.3469e-06 | 0.052177 | 0.052177 | 0.052177 | 0.98534 | -0.10262 | 0.9856 | -0.10077 | 19.3249
99 | 0.024308 | 0.0060962 | -0.024269 | -0.0060819 | 3.8578e-05 | 1.4259e-05 | 0.036778 | 0.036779 | 0.036779 | 0.98352 | -0.11556 | 0.98191 | -0.12703 | 13.6217
100 | -0.036497 | -0.0091573 | 0.036521 | 0.0091662 | 2.3518e-05 | 8.8873e-06 | 0.055105 | 0.055105 | 0.055105 | 0.9856 | -0.10077 | 0.98626 | -0.096131 | 20.4094
101 | 0.13955 | 0.035196 | -0.13934 | -0.035118 | 0.00020563 | 7.8203e-05 | 0.20855 | 0.20856 | 0.20856 | 0.99602 | -0.027539 | 0.99451 | -0.038065 | 25.7476
102 | 0.0079442 | 0.0019897 | -0.0079412 | -0.001989 | 2.9753e-06 | 6.9682e-07 | 0.011821 | 0.011821 | 0.011821 | 1 | 0 | 0.99961 | -0.0027093 | 4.3781
103 | 0.13508 | 0.03405 | -0.13488 | -0.033976 | 0.00019505 | 7.4129e-05 | 0.20218 | 0.20218 | 0.20218 | 0.99451 | -0.038065 | 0.99303 | -0.04839 | 24.9605
104 | 0.0065228 | 0.0016335 | -0.0065222 | -0.0016334 | 6.892e-07 | 1.1151e-07 | 0.0097094 | 0.0097095 | 0.0097095 | 0.99961 | -0.0027093 | 0.9995 | -0.0034737 | 3.5961
105 | 0.043204 | 0.010845 | -0.043188 | -0.010839 | 1.5247e-05 | 5.7892e-06 | 0.06482 | 0.06482 | 0.06482 | 0.99188 | -0.056435 | 0.99152 | -0.058977 | 24.0074
106 | -0.045164 | -0.011336 | 0.045201 | 0.01135 | 3.7098e-05 | 1.4101e-05 | 0.06776 | 0.06776 | 0.06776 | 0.99188 | -0.056435 | 0.99272 | -0.050524 | 25.0964
107 | 0.04181 | 0.010493 | -0.041809 | -0.010493 | 1.4508e-06 | 5.5037e-07 | 0.062752 | 0.062752 | 0.062752 | 0.99152 | -0.058977 | 0.99148 | -0.059227 | 23.2414
108 | -0.13036 | -0.032836 | 0.1304 | 0.032851 | 3.8904e-05 | 1.4773e-05 | 0.19546 | 0.19546 | 0.19546 | 0.99272 | -0.050524 | 0.99303 | -0.04839 | 24.1305
109 | 0.03811 | 0.0095658 | -0.038094 | -0.0095598 | 1.5973e-05 | 6.0428e-06 | 0.0572 | 0.0572 | 0.0572 | 0.99148 | -0.059227 | 0.99105 | -0.062247 | 21.1853
110 | 0.032716 | 0.0082119 | -0.032682 | -0.0081992 | 3.3726e-05 | 1.2683e-05 | 0.049125 | 0.049126 | 0.049126 | 0.99105 | -0.062247 | 0.99 | -0.069678 | 18.1946
111 | 0.0019946 | 0.00049986 | -0.0019946 | -0.00049989 | 1.5228e-08 | -2.8407e-08 | 0.003012 | 0.003012 | 0.003012 | 0.98537 | -0.1025 | 0.98536 | -0.10256 | 1.1156
112 | 0.0034728 | 0.00086955 | -0.0034726 | -0.00086963 | 2.0545e-07 | -8.2425e-08 | 0.0051698 | 0.0051699 | 0.0051699 | 0.9995 | -0.0034737 | 0.99944 | -0.0039018 | 1.9148
113 | 0.0030494 | 0.00076386 | -0.0030492 | -0.00076399 | 2.1098e-07 | -1.3386e-07 | 0.0045396 | 0.0045397 | 0.0045397 | 0.9995 | -0.0034737 | 0.99943 | -0.0039739 | 1.6814
114 | 0.0016911 | 0.00042315 | -0.001691 | -0.00042332 | 5.8107e-08 | -1.7018e-07 | 0.0025176 | 0.0025176 | 0.0025176 | 0.99944 | -0.0039018 | 0.99941 | -0.0041507 | 0.93245
115 | 0.0017355 | 0.00043476 | -0.0017354 | -0.00043494 | 6.6953e-08 | -1.8484e-07 | 0.0025838 | 0.0025839 | 0.0025839 | 0.99943 | -0.0039739 | 0.99939 | -0.0042527 | 0.95701
116 | 0.001691 | 0.00042332 | -0.0016909 | -0.00042378 | 1.551e-07 | -4.5413e-07 | 0.0025176 | 0.0025178 | 0.0025178 | 0.99941 | -0.0041507 | 0.99931 | -0.004814 | 0.93252
117 | 0.0075695 | 0.0018956 | -0.0075644 | -0.0018944 | 5.0987e-06 | 1.1648e-06 | 0.01143 | 0.01143 | 0.01143 | 0.98541 | -0.10223 | 0.98472 | -0.10711 | 4.2334
118 | -0.011019 | -0.0027601 | 0.011022 | 0.0027611 | 3.207e-06 | 9.9691e-07 | 0.016639 | 0.016639 | 0.016639 | 0.98541 | -0.10223 | 0.9857 | -0.10013 | 6.1625
119 | 0.005956 | 0.0014913 | -0.0059545 | -0.0014911 | 1.4797e-06 | 1.9676e-07 | 0.0089996 | 0.0089997 | 0.0089997 | 0.98472 | -0.10711 | 0.98447 | -0.1089 | 3.3332
120 | 0.005099 | 0.0012772 | -0.0050972 | -0.0012771 | 1.8209e-06 | 7.5905e-08 | 0.0077068 | 0.0077071 | 0.0077071 | 0.98447 | -0.1089 | 0.98411 | -0.11149 | 2.8545
121 | 0.0008555 | 0.00021393 | -0.00085546 | -0.0002144 | 3.9423e-08 | -4.6531e-07 | 0.0012929 | 0.0012931 | 0.0012931 | 0.98447 | -0.1089 | 0.98442 | -0.10924 | 0.47892
122 | 0.0050972 | 0.0012771 | -0.0050955 | -0.0012771 | 1.6886e-06 | 7.083e-08 | 0.0077071 | 0.0077073 | 0.0077073 | 0.98411 | -0.11149 | 0.98377 | -0.11388 | 2.8545
123 | 0.0018557 | 0.00046485 | -0.0018556 | -0.00046506 | 9.5163e-08 | -2.1055e-07 | 0.0028029 | 0.002803 | 0.002803 | 0.98515 | -0.10406 | 0.9851 | -0.10443 | 1.0381
124 | -0.036521 | -0.0091662 | 0.036575 | 0.0091867 | 5.4117e-05 | 2.0449e-05 | 0.055105 | 0.055105 | 0.055105 | 0.98626 | -0.096131 | 0.98776 | -0.085474 | 20.4094

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.23923 | 0.060196

## res_load
| p_mw | q_mvar
0 | 0.0012698 | 0.00031823
1 | 0.00066358 | 0.00016631
2 | 0.0019695 | 0.0004936
3 | 0.00062152 | 0.00015577
4 | 0.0010955 | 0.00027455
5 | 0.00087274 | 0.00021873
6 | 0.00037058 | 9.2877e-05
7 | 0.0025759 | 0.00064559
8 | 0.0016761 | 0.00042006
9 | 0.0055343 | 0.001387
10 | 0.0026386 | 0.00066131
11 | 0.0024653 | 0.00061786
12 | 0.0022256 | 0.00055779
13 | 0.0090514 | 0.0022685
14 | 0.0022463 | 0.00056298
15 | 0.0050349 | 0.0012619
16 | 0.0015666 | 0.00039262
17 | 0.0018004 | 0.00045122
18 | 0.0022748 | 0.00057011
19 | 0.0019685 | 0.00049335
20 | 0.00092673 | 0.00023226
21 | 0.00061575 | 0.00015432
22 | 0.0016006 | 0.00040114
23 | 0.00033418 | 8.3754e-05
24 | 0.0019095 | 0.00047855
25 | 0.0016688 | 0.00041825
26 | 0.0003044 | 7.6289e-05
27 | 0.0013336 | 0.00033422
28 | 0.0011283 | 0.00028278
29 | 0.0012606 | 0.00031594
30 | 0.0011731 | 0.000294
31 | 0.0017491 | 0.00043835
32 | 0.0061971 | 0.0015531
33 | 0.0087085 | 0.0021826
34 | 0.015742 | 0.0039453
35 | 0.0023866 | 0.00059814
36 | 0.0059279 | 0.0014857
37 | 0.0023866 | 0.00059814
38 | 0.0014828 | 0.00037162
39 | 0.0047158 | 0.0011819
40 | 0.0010607 | 0.00026584
41 | 0.0019494 | 0.00048855
42 | 0.0013572 | 0.00034014
43 | 0.0031732 | 0.00079527
44 | 0.00077053 | 0.00019311
45 | 0.00098762 | 0.00024752
46 | 0.0010507 | 0.00026332
47 | 0.00026811 | 6.7196e-05
48 | 0.0042816 | 0.0010731
49 | 0.0041527 | 0.0010408
50 | 0.00039832 | 9.9829e-05
51 | 0.00047242 | 0.0001184
52 | 0.00098119 | 0.00024591
53 | 0.0012621 | 0.00031631
54 | 0.0013848 | 0.00034707
55 | 0.0045636 | 0.0011437
56 | 0.00030788 | 7.7162e-05
57 | 0.00018552 | 4.6496e-05
58 | 0.00044049 | 0.0001104
59 | 0.00065264 | 0.00016357
60 | 0.0010557 | 0.00026459
61 | 0.0010268 | 0.00025735
62 | 0.0020119 | 0.00050424
63 | 0.0030412 | 0.0007622
64 | 0.00071301 | 0.0001787
65 | 0.0039589 | 0.0009922
66 | 0.0017305 | 0.0004337
67 | 0.00054967 | 0.00013776
68 | 0.00087081 | 0.00021825
69 | 0.00061522 | 0.00015419
70 | 0.0016951 | 0.00042483
71 | 0.0019517 | 0.00048915
72 | 0.00086312 | 0.00021632
73 | 0.0012663 | 0.00031736
74 | 0.0032247 | 0.00080818
75 | 0.0011872 | 0.00029754
76 | 0.0019395 | 0.0004861
77 | 0.0053589 | 0.0013431
78 | 0.00027404 | 6.8682e-05
79 | 0.0034382 | 0.0008617
80 | 0.0046442 | 0.0011639
81 | 0.0042608 | 0.0010679
82 | 0.0014183 | 0.00035547
83 | 0.00196 | 0.00049122
84 | 0.0013782 | 0.0003454
85 | 0.0036991 | 0.00092707
86 | 0.0044868 | 0.0011245
87 | 0.005378 | 0.0013478
88 | 0.00042286 | 0.00010598
89 | 0.0023135 | 0.00057982
90 | 0.0019946 | 0.00049989
91 | 0.0017815 | 0.00044648
92 | 0.0013137 | 0.00032923
93 | 0.0017354 | 0.00043494
94 | 0.0034495 | 0.00086452
95 | 0.0016085 | 0.00040312
96 | 0.00085546 | 0.0002144
97 | 0.0050955 | 0.0012771
98 | 0.0011408 | 0.00028591
99 | 0.0018556 | 0.00046506
100 | 0.0029505 | 0.00073946
101 | 0.00346 | 0.00086717
102 | 0.0016909 | 0.00042378

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1