## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2578-1_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2578-1_0_2_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_2578-1_0_2_node_4 | 0.4 | n |  | TRUE
3 | bus_LV_2578-1_0_2_node_30 | 0.4 | n |  | TRUE
4 | bus_LV_2578-1_0_2_node_24 | 0.4 | n |  | TRUE
5 | bus_LV_2578-1_0_2_node_29 | 0.4 | n |  | TRUE
6 | bus_LV_2578-1_0_2_node_3 | 0.4 | n |  | TRUE
7 | bus_LV_2578-1_0_2_node_25 | 0.4 | n |  | TRUE
8 | bus_LV_2578-1_0_2_node_38 | 0.4 | n |  | TRUE
9 | bus_LV_2578-1_0_2_node_35 | 0.4 | n |  | TRUE
10 | bus_LV_2578-1_0_2_node_37 | 0.4 | n |  | TRUE
11 | bus_LV_2578-1_0_2_node_36 | 0.4 | n |  | TRUE
12 | bus_LV_2578-1_0_2_node_5 | 0.4 | n |  | TRUE
13 | bus_LV_2578-1_0_2_node_6 | 0.4 | n |  | TRUE
14 | bus_LV_2578-1_0_2_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_2578-1_0_2_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_2578-1_0_2_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_2578-1_0_2_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_2578-1_0_2_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_2578-1_0_2_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_2578-1_0_2_node_32 | 0.4 | n |  | TRUE
21 | bus_LV_2578-1_0_2_node_27 | 0.4 | n |  | TRUE
22 | bus_LV_2578-1_0_2_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_2578-1_0_2_node_28 | 0.4 | n |  | TRUE
24 | bus_LV_2578-1_0_2_node_14 | 0.4 | n |  | TRUE
25 | bus_LV_2578-1_0_2_node_15 | 0.4 | n |  | TRUE
26 | bus_LV_2578-1_0_2_node_20 | 0.4 | n |  | TRUE
27 | bus_LV_2578-1_0_2_node_17 | 0.4 | n |  | TRUE
28 | bus_LV_2578-1_0_2_node_16 | 0.4 | n |  | TRUE
29 | bus_LV_2578-1_0_2_node_18 | 0.4 | n |  | TRUE
30 | bus_LV_2578-1_0_2_node_19 | 0.4 | n |  | TRUE
31 | bus_LV_2578-1_0_2_node_21 | 0.4 | n |  | TRUE
32 | bus_LV_2578-1_0_2_node_22 | 0.4 | n |  | TRUE
33 | bus_LV_2578-1_0_2_node_26 | 0.4 | n |  | TRUE
34 | bus_MV_0_node_30 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2578-1_0_2_load_0 | 0 | 0.00060331 | 0.0001512 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2578-1_0_2_load_30 | 3 | 0.0035647 | 0.00089339 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2578-1_0_2_load_24 | 4 | 0.0075662 | 0.0018963 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2578-1_0_2_load_38 | 8 | 0.002754 | 0.00069021 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2578-1_0_2_load_35 | 9 | 0.0013293 | 0.00033314 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2578-1_0_2_load_5 | 12 | 0.0017742 | 0.00044466 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2578-1_0_2_load_8 | 15 | 0.0014758 | 0.00036987 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2578-1_0_2_load_9 | 16 | 0.00074944 | 0.00018783 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2578-1_0_2_load_10 | 17 | 0.001866 | 0.00046765 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2578-1_0_2_load_11 | 18 | 0.00078749 | 0.00019736 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2578-1_0_2_load_13 | 19 | 0.00049373 | 0.00012374 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2578-1_0_2_load_32 | 20 | 0.001984 | 0.00049724 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2578-1_0_2_load_27 | 21 | 0.00076669 | 0.00019215 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2578-1_0_2_load_12 | 22 | 0.002458 | 0.00061602 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2578-1_0_2_load_28 | 23 | 0.00060854 | 0.00015251 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2578-1_0_2_load_14 | 24 | 0.0025841 | 0.00064765 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2578-1_0_2_load_15 | 25 | 0.0018009 | 0.00045135 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2578-1_0_2_load_20 | 26 | 0.0034166 | 0.00085629 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2578-1_0_2_load_16 | 28 | 0.002505 | 0.00062782 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2578-1_0_2_load_18 | 29 | 0.0041688 | 0.0010448 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2578-1_0_2_load_19 | 30 | 0.0017805 | 0.00044623 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2578-1_0_2_load_21 | 31 | 0.002771 | 0.00069448 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2578-1_0_2_load_22 | 32 | 0.0018685 | 0.00046829 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2578-1_0_2_load_26 | 33 | 0.00286 | 0.00071678 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 3 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2578-1_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.013719 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2578-1_0_2_line_1 | NAYY 4x150 SE | 1 | 2 | 0.016277 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2578-1_0_2_line_2 | NAYY 4x150 SE | 2 | 9 | 0.020285 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2578-1_0_2_line_3 | NAYY 4x150 SE | 3 | 4 | 0.40241 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2578-1_0_2_line_4 | NAYY 4x150 SE | 3 | 5 | 0.018075 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2578-1_0_2_line_5 | NAYY 4x150 SE | 4 | 7 | 0.032797 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2578-1_0_2_line_6 | NAYY 4x150 SE | 5 | 33 | 0.032129 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2578-1_0_2_line_7 | NAYY 4x150 SE | 6 | 7 | 0.017481 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2578-1_0_2_line_8 | NAYY 4x150 SE | 6 | 8 | 0.0028056 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2578-1_0_2_line_9 | NAYY 4x150 SE | 8 | 10 | 0.015358 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2578-1_0_2_line_10 | NAYY 4x150 SE | 9 | 11 | 0.019125 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2578-1_0_2_line_11 | NAYY 4x150 SE | 10 | 11 | 0.030397 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2578-1_0_2_line_12 | NAYY 4x150 SE | 12 | 13 | 0.034259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2578-1_0_2_line_13 | NAYY 4x150 SE | 12 | 14 | 0.0346 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2578-1_0_2_line_14 | NAYY 4x150 SE | 13 | 15 | 0.01223 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2578-1_0_2_line_15 | NAYY 4x150 SE | 13 | 16 | 0.0077689 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2578-1_0_2_line_16 | NAYY 4x150 SE | 14 | 17 | 0.027634 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2578-1_0_2_line_17 | NAYY 4x150 SE | 14 | 18 | 0.022434 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2578-1_0_2_line_18 | NAYY 4x150 SE | 15 | 19 | 0.030581 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2578-1_0_2_line_19 | NAYY 4x150 SE | 16 | 20 | 0.012285 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2578-1_0_2_line_20 | NAYY 4x150 SE | 18 | 21 | 0.0038525 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2578-1_0_2_line_21 | NAYY 4x150 SE | 19 | 22 | 0.015102 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2578-1_0_2_line_22 | NAYY 4x150 SE | 21 | 23 | 0.018491 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2578-1_0_2_line_23 | NAYY 4x150 SE | 22 | 24 | 0.01089 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2578-1_0_2_line_24 | NAYY 4x150 SE | 24 | 25 | 0.0087549 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2578-1_0_2_line_25 | NAYY 4x150 SE | 25 | 26 | 0.019047 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2578-1_0_2_line_26 | NAYY 4x150 SE | 26 | 27 | 0.0022186 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2578-1_0_2_line_27 | NAYY 4x150 SE | 27 | 30 | 0.01738 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2578-1_0_2_line_28 | NAYY 4x150 SE | 27 | 28 | 0.016028 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2578-1_0_2_line_29 | NAYY 4x150 SE | 28 | 29 | 0.014155 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2578-1_0_2_line_30 | NAYY 4x150 SE | 30 | 31 | 0.0048733 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2578-1_0_2_line_31 | NAYY 4x150 SE | 31 | 32 | 0.014616 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2578-1_0_2_line_32 | NAYY 4x150 SE | 32 | 33 | 0.010065 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2578-1_0_2_trafo_30 | 0.25 MVA 20/0.4 kV | 34 | 3 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2630908.0559 | 1240054.4488 | 2630906.4872 | 1240052.1948 | 2630905.2018 | 1240050.7205 | 2630902.6242 | 1240049.095 | 2630897.0304 | 1240047.0094
1 | 2630908.0559 | 1240054.4488 | 2630924.0655 | 1240051.2634
2 | 2630924.0655 | 1240051.2634 | 2630926.3576 | 1240049.6409 | 2630928.5099 | 1240047.2617 | 2630929.7927 | 1240044.878 | 2630933.8787 | 1240034.0623
3 | 2630626.6481 | 1239659.3496 | 2630870.3685 | 1239979.5615
4 | 2630628.5033 | 1239641.3969 | 2630627.6018 | 1239646.1063 | 2630627.2042 | 1239649.9067 | 2630626.6481 | 1239659.3496
5 | 2630891.5004 | 1239995.3587 | 2630889.646 | 1239995.716 | 2630887.8857 | 1239995.4066 | 2630870.6237 | 1239989.2687 | 2630869.6073 | 1239988.4295 | 2630868.7894 | 1239987.2023 | 2630868.4553 | 1239986.0109 | 2630868.5069 | 1239984.8215 | 2630870.3685 | 1239979.5615
6 | 2630628.5033 | 1239641.3969 | 2630615.8036 | 1239638.9966 | 2630605.1021 | 1239637.6963 | 2630596.687 | 1239637.2966
7 | 2630891.5004 | 1239995.3587 | 2630892.3619 | 1239996.9309 | 2630894.6976 | 1240001.457 | 2630899.253 | 1240011.0311
8 | 2630899.253 | 1240011.0311 | 2630901.904 | 1240010.1127
9 | 2630915.6698 | 1240003.723 | 2630914.2639 | 1240005.0609 | 2630912.7459 | 1240006.1426 | 2630910.7297 | 1240007.0549 | 2630901.904 | 1240010.1127
10 | 2630942.3825 | 1240017.3817 | 2630939.8914 | 1240019.4589 | 2630939.0779 | 1240020.2996 | 2630933.8787 | 1240034.0623
11 | 2630915.6698 | 1240003.723 | 2630919.6612 | 1240005.4115 | 2630938.5623 | 1240013.3036 | 2630941.1523 | 1240015.4629 | 2630942.3825 | 1240017.3817
12 | 2630451.8999 | 1239628.604 | 2630448.3992 | 1239640.3046 | 2630443.2684 | 1239661.7449
13 | 2630435.7219 | 1239695.5079 | 2630436.6001 | 1239690.8984 | 2630439.9992 | 1239675.406 | 2630443.2684 | 1239661.7449
14 | 2630451.8999 | 1239628.604 | 2630456.0969 | 1239630.1043 | 2630463.6385 | 1239631.9845
15 | 2630451.8999 | 1239628.604 | 2630449.0995 | 1239627.6002 | 2630444.6977 | 1239625.7009
16 | 2630435.7219 | 1239695.5079 | 2630434.6028 | 1239701.4059 | 2630434.8033 | 1239703.5972 | 2630435.5031 | 1239708.704 | 2630436.2014 | 1239714.0999 | 2630436.199 | 1239719.0029 | 2630436.0573 | 1239722.9323
17 | 2630435.7219 | 1239695.5079 | 2630417.1218 | 1239699.3929 | 2630413.8212 | 1239700.3347
18 | 2630463.6385 | 1239631.9845 | 2630465.7038 | 1239632.4994 | 2630474.7984 | 1239634.5028 | 2630485.0986 | 1239635.901 | 2630493.8098 | 1239636.6745
19 | 2630433.4244 | 1239620.8196 | 2630435.2005 | 1239621.603 | 2630444.6977 | 1239625.7009
20 | 2630410.1166 | 1239701.3917 | 2630410.1166 | 1239701.3917 | 2630413.8212 | 1239700.3347
21 | 2630493.8098 | 1239636.6745 | 2630495.1971 | 1239636.7977 | 2630506.3025 | 1239637.4996 | 2630508.8814 | 1239637.6187
22 | 2630410.1166 | 1239701.3917 | 2630407.1919 | 1239705.4571 | 2630405.8703 | 1239711.0316 | 2630405.5388 | 1239718.7781
23 | 2630519.7598 | 1239638.109 | 2630519.2989 | 1239638.1 | 2630508.8814 | 1239637.6187
24 | 2630519.7598 | 1239638.109 | 2630528.513 | 1239638.2809
25 | 2630547.5552 | 1239638.5104 | 2630544.5996 | 1239638.5969 | 2630528.513 | 1239638.2809
26 | 2630549.7729 | 1239638.4456 | 2630547.5552 | 1239638.5104
27 | 2630549.7729 | 1239638.4456 | 2630567.1451 | 1239637.9276
28 | 2630549.7729 | 1239638.4456 | 2630549.1124 | 1239654.4596
29 | 2630548.529 | 1239668.6027 | 2630549.1124 | 1239654.4596
30 | 2630567.1451 | 1239637.9276 | 2630572.0162 | 1239637.7824
31 | 2630586.6273 | 1239637.3994 | 2630574.8986 | 1239637.6965 | 2630572.0162 | 1239637.7824
32 | 2630596.687 | 1239637.2966 | 2630594.6008 | 1239637.1975 | 2630586.6273 | 1239637.3994

## bus_geodata
| x | y | coords
0 | 2630897.0304 | 1240047.0094
1 | 2630908.0559 | 1240054.4488
2 | 2630924.0655 | 1240051.2634
3 | 2630626.6481 | 1239659.3496
4 | 2630870.3685 | 1239979.5615
5 | 2630628.5033 | 1239641.3969
6 | 2630899.253 | 1240011.0311
7 | 2630891.5004 | 1239995.3587
8 | 2630901.904 | 1240010.1127
9 | 2630933.8787 | 1240034.0623
10 | 2630915.6698 | 1240003.723
11 | 2630942.3825 | 1240017.3817
12 | 2630443.2684 | 1239661.7449
13 | 2630451.8999 | 1239628.604
14 | 2630435.7219 | 1239695.5079
15 | 2630463.6385 | 1239631.9845
16 | 2630444.6977 | 1239625.7009
17 | 2630436.0573 | 1239722.9323
18 | 2630413.8212 | 1239700.3347
19 | 2630493.8098 | 1239636.6745
20 | 2630433.4244 | 1239620.8196
21 | 2630410.1166 | 1239701.3917
22 | 2630508.8814 | 1239637.6187
23 | 2630405.5388 | 1239718.7781
24 | 2630519.7598 | 1239638.109
25 | 2630528.513 | 1239638.2809
26 | 2630547.5552 | 1239638.5104
27 | 2630549.7729 | 1239638.4456
28 | 2630549.1124 | 1239654.4596
29 | 2630548.529 | 1239668.6027
30 | 2630567.1451 | 1239637.9276
31 | 2630572.0162 | 1239637.7824
32 | 2630586.6273 | 1239637.3994
33 | 2630596.687 | 1239637.2966
34 | 2630626.6481 | 1239659.3496

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99234 | -0.053816 | 0.00060331 | 0.0001512
1 | 0.99235 | -0.053732 | 0 | 0
2 | 0.99237 | -0.053632 | 0 | 0
3 | 1 | 0 | -0.050041 | -0.012365
4 | 0.99292 | -0.049704 | 0.0075662 | 0.0018963
5 | 0.99905 | -0.006637 | 0 | 0
6 | 0.99258 | -0.052098 | 0 | 0
7 | 0.9927 | -0.051266 | 0 | 0
8 | 0.99256 | -0.052231 | 0.002754 | 0.00069021
9 | 0.99238 | -0.053507 | 0.0013293 | 0.00033314
10 | 0.99252 | -0.052533 | 0 | 0
11 | 0.99244 | -0.053131 | 0 | 0
12 | 0.99327 | -0.047211 | 0.0017742 | 0.00044466
13 | 0.99356 | -0.045196 | 0 | 0
14 | 0.99307 | -0.048624 | 0 | 0
15 | 0.99371 | -0.044139 | 0.0014758 | 0.00036987
16 | 0.99353 | -0.045411 | 0.00074944 | 0.00018783
17 | 0.993 | -0.049147 | 0.001866 | 0.00046765
18 | 0.993 | -0.049116 | 0.00078749 | 0.00019736
19 | 0.99415 | -0.04104 | 0.00049373 | 0.00012374
20 | 0.99349 | -0.045658 | 0.001984 | 0.00049724
21 | 0.993 | -0.04917 | 0.00076669 | 0.00019215
22 | 0.99438 | -0.039435 | 0.002458 | 0.00061602
23 | 0.99298 | -0.049284 | 0.00060854 | 0.00015251
24 | 0.99458 | -0.038008 | 0.0025841 | 0.00064765
25 | 0.99477 | -0.036633 | 0.0018009 | 0.00045135
26 | 0.99525 | -0.033297 | 0.0034166 | 0.00085629
27 | 0.99531 | -0.032833 | 0 | 0
28 | 0.99516 | -0.033911 | 0.002505 | 0.00062782
29 | 0.99508 | -0.034506 | 0.0041688 | 0.0010448
30 | 0.996 | -0.028026 | 0.0017805 | 0.00044623
31 | 0.9962 | -0.026593 | 0.002771 | 0.00069448
32 | 0.99687 | -0.021889 | 0.0018685 | 0.00046829
33 | 0.99736 | -0.018465 | 0.00286 | 0.00071678
34 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.00060331 | -0.0001512 | 0.00060332 | 0.00015103 | 7.006e-09 | -1.7455e-07 | 0.00090467 | 0.00090461 | 0.00090467 | 0.99234 | -0.053816 | 0.99235 | -0.053732 | 0.33506
1 | -0.00060332 | -0.00015103 | 0.00060333 | 0.00015082 | 8.3108e-09 | -2.071e-07 | 0.00090461 | 0.00090453 | 0.00090461 | 0.99235 | -0.053732 | 0.99237 | -0.053632 | 0.33504
2 | -0.00060333 | -0.00015082 | 0.00060334 | 0.00015056 | 1.0355e-08 | -2.581e-07 | 0.00090453 | 0.00090444 | 0.00090453 | 0.99237 | -0.053632 | 0.99238 | -0.053507 | 0.33501
3 | 0.012339 | 0.0030967 | -0.012255 | -0.0030694 | 8.4679e-05 | 2.7327e-05 | 0.018363 | 0.018365 | 0.018365 | 1 | 0 | 0.99292 | -0.049704 | 6.8017
4 | 0.036902 | 0.0092679 | -0.036868 | -0.0092551 | 3.4017e-05 | 1.2846e-05 | 0.054917 | 0.054917 | 0.054917 | 1 | 0 | 0.99905 | -0.006637 | 20.3398
5 | 0.0046886 | 0.0011732 | -0.0046875 | -0.0011732 | 1.0102e-06 | -3.557e-08 | 0.0070257 | 0.0070259 | 0.0070259 | 0.99292 | -0.049704 | 0.9927 | -0.051266 | 2.6022
6 | 0.036868 | 0.009255 | -0.036807 | -0.0092322 | 6.0466e-05 | 2.2836e-05 | 0.054917 | 0.054918 | 0.054918 | 0.99905 | -0.006637 | 0.99736 | -0.018465 | 20.3398
7 | -0.004687 | -0.0011732 | 0.0046875 | 0.0011732 | 5.3846e-07 | -1.8875e-08 | 0.0070259 | 0.0070259 | 0.0070259 | 0.99258 | -0.052098 | 0.9927 | -0.051266 | 2.6022
8 | 0.004687 | 0.0011732 | -0.0046869 | -0.0011732 | 8.6423e-08 | -3.024e-09 | 0.0070259 | 0.007026 | 0.007026 | 0.99258 | -0.052098 | 0.99256 | -0.052231 | 2.6022
9 | 0.0019329 | 0.000483 | -0.0019329 | -0.00048317 | 8.0448e-08 | -1.6755e-07 | 0.0028973 | 0.0028974 | 0.0028974 | 0.99256 | -0.052231 | 0.99252 | -0.052533 | 1.0731
10 | -0.0019326 | -0.00048371 | 0.0019327 | 0.0004835 | 1.002e-07 | -2.0858e-07 | 0.0028976 | 0.0028975 | 0.0028976 | 0.99238 | -0.053507 | 0.99244 | -0.053131 | 1.0732
11 | 0.0019329 | 0.00048317 | -0.0019327 | -0.0004835 | 1.5924e-07 | -3.3157e-07 | 0.0028974 | 0.0028975 | 0.0028975 | 0.99252 | -0.052533 | 0.99244 | -0.053131 | 1.0731
12 | -0.005804 | -0.0014534 | 0.0058056 | 0.0014536 | 1.616e-06 | 1.7798e-07 | 0.0086945 | 0.0086943 | 0.0086945 | 0.99327 | -0.047211 | 0.99356 | -0.045196 | 3.2202
13 | 0.0040298 | 0.0010087 | -0.004029 | -0.0010089 | 7.8677e-07 | -1.4515e-07 | 0.0060365 | 0.0060367 | 0.0060367 | 0.99327 | -0.047211 | 0.99307 | -0.048624 | 2.2358
14 | -0.0085392 | -0.0021384 | 0.0085405 | 0.0021387 | 1.248e-06 | 3.216e-07 | 0.012788 | 0.012788 | 0.012788 | 0.99356 | -0.045196 | 0.99371 | -0.044139 | 4.7364
15 | 0.0027336 | 0.00068487 | -0.0027335 | -0.00068494 | 8.1253e-08 | -6.936e-08 | 0.004094 | 0.004094 | 0.004094 | 0.99356 | -0.045196 | 0.99353 | -0.045411 | 1.5163
16 | 0.0018661 | 0.00046735 | -0.001866 | -0.00046765 | 1.3481e-07 | -3.0566e-07 | 0.002796 | 0.0027962 | 0.0027962 | 0.99307 | -0.048624 | 0.993 | -0.049147 | 1.0356
17 | 0.0021629 | 0.00054151 | -0.0021627 | -0.00054175 | 1.4702e-07 | -2.3369e-07 | 0.0032407 | 0.0032408 | 0.0032408 | 0.99307 | -0.048624 | 0.993 | -0.049116 | 1.2003
18 | -0.010016 | -0.0025086 | 0.010021 | 0.0025099 | 4.2925e-06 | 1.2546e-06 | 0.014998 | 0.014998 | 0.014998 | 0.99371 | -0.044139 | 0.99415 | -0.04104 | 5.5549
19 | 0.0019841 | 0.00049711 | -0.001984 | -0.00049724 | 6.769e-08 | -1.3305e-07 | 0.0029715 | 0.0029716 | 0.0029716 | 0.99353 | -0.045411 | 0.99349 | -0.045658 | 1.1006
20 | 0.0013753 | 0.00034438 | -0.0013752 | -0.00034443 | 1.0209e-08 | -4.591e-08 | 0.0020607 | 0.0020607 | 0.0020607 | 0.993 | -0.049116 | 0.993 | -0.04917 | 0.76323
21 | -0.010514 | -0.0026336 | 0.010517 | 0.0026343 | 2.3338e-06 | 7.0175e-07 | 0.015737 | 0.015737 | 0.015737 | 0.99415 | -0.04104 | 0.99438 | -0.039435 | 5.8285
22 | 0.00060855 | 0.00015228 | -0.00060854 | -0.00015251 | 9.5942e-09 | -2.3551e-07 | 0.00091183 | 0.00091192 | 0.00091192 | 0.993 | -0.04917 | 0.99298 | -0.049284 | 0.33775
23 | -0.012975 | -0.0032503 | 0.012977 | 0.0032512 | 2.5614e-06 | 8.4386e-07 | 0.019415 | 0.019415 | 0.019415 | 0.99438 | -0.039435 | 0.99458 | -0.038008 | 7.1908
24 | -0.015561 | -0.0038988 | 0.015564 | 0.0038999 | 2.9611e-06 | 1.0252e-06 | 0.023281 | 0.023281 | 0.023281 | 0.99458 | -0.038008 | 0.99477 | -0.036633 | 8.6227
25 | -0.017365 | -0.0043512 | 0.017373 | 0.004354 | 8.0189e-06 | 2.8368e-06 | 0.025975 | 0.025975 | 0.025975 | 0.99477 | -0.036633 | 0.99525 | -0.033297 | 9.6204
26 | -0.02079 | -0.0052103 | 0.020791 | 0.0052108 | 1.3376e-06 | 4.8563e-07 | 0.031083 | 0.031083 | 0.031083 | 0.99525 | -0.033297 | 0.99531 | -0.032833 | 11.5123
27 | -0.027466 | -0.0068835 | 0.027485 | 0.0068904 | 1.8286e-05 | 6.8071e-06 | 0.041063 | 0.041063 | 0.041063 | 0.99531 | -0.032833 | 0.996 | -0.028026 | 15.2084
28 | 0.0066751 | 0.0016727 | -0.0066741 | -0.0016726 | 9.9601e-07 | 1.7481e-07 | 0.0099794 | 0.0099794 | 0.0099794 | 0.99531 | -0.032833 | 0.99516 | -0.033911 | 3.6961
29 | 0.0041691 | 0.0010447 | -0.0041688 | -0.0010448 | 3.4325e-07 | -5.1877e-08 | 0.0062338 | 0.0062339 | 0.0062339 | 0.99516 | -0.033911 | 0.99508 | -0.034506 | 2.3088
30 | -0.029265 | -0.0073366 | 0.029271 | 0.0073388 | 5.8133e-06 | 2.1725e-06 | 0.043723 | 0.043723 | 0.043723 | 0.996 | -0.028026 | 0.9962 | -0.026593 | 16.1936
31 | -0.032042 | -0.0080332 | 0.032063 | 0.0080411 | 2.0892e-05 | 7.8451e-06 | 0.047862 | 0.047862 | 0.047862 | 0.9962 | -0.026593 | 0.99687 | -0.021889 | 17.7265
32 | -0.033931 | -0.0085094 | 0.033947 | 0.0085154 | 1.6112e-05 | 6.0657e-06 | 0.050651 | 0.050651 | 0.050651 | 0.99687 | -0.021889 | 0.99736 | -0.018465 | 18.7595

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -4.4415e-16 | -7.6913e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.564e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.053606 | 0.013258

## res_load
| p_mw | q_mvar
0 | 0.00060331 | 0.0001512
1 | 0.0035647 | 0.00089339
2 | 0.0075662 | 0.0018963
3 | 0.002754 | 0.00069021
4 | 0.0013293 | 0.00033314
5 | 0.0017742 | 0.00044466
6 | 0.0014758 | 0.00036987
7 | 0.00074944 | 0.00018783
8 | 0.001866 | 0.00046765
9 | 0.00078749 | 0.00019736
10 | 0.00049373 | 0.00012374
11 | 0.001984 | 0.00049724
12 | 0.00076669 | 0.00019215
13 | 0.002458 | 0.00061602
14 | 0.00060854 | 0.00015251
15 | 0.0025841 | 0.00064765
16 | 0.0018009 | 0.00045135
17 | 0.0034166 | 0.00085629
18 | 0.002505 | 0.00062782
19 | 0.0041688 | 0.0010448
20 | 0.0017805 | 0.00044623
21 | 0.002771 | 0.00069448
22 | 0.0018685 | 0.00046829
23 | 0.00286 | 0.00071678

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1