## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_332-8_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_332-8_0_3_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_332-8_0_3_node_4 | 0.4 | n |  | TRUE
3 | bus_LV_332-8_0_3_node_5 | 0.4 | n |  | TRUE
4 | bus_LV_332-8_0_3_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_332-8_0_3_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_332-8_0_3_node_61 | 0.4 | n |  | TRUE
7 | bus_LV_332-8_0_3_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_332-8_0_3_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_332-8_0_3_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_332-8_0_3_node_10 | 0.4 | n |  | TRUE
11 | bus_LV_332-8_0_3_node_11 | 0.4 | n |  | TRUE
12 | bus_LV_332-8_0_3_node_12 | 0.4 | n |  | TRUE
13 | bus_LV_332-8_0_3_node_60 | 0.4 | n |  | TRUE
14 | bus_LV_332-8_0_3_node_13 | 0.4 | n |  | TRUE
15 | bus_LV_332-8_0_3_node_14 | 0.4 | n |  | TRUE
16 | bus_LV_332-8_0_3_node_15 | 0.4 | n |  | TRUE
17 | bus_LV_332-8_0_3_node_16 | 0.4 | n |  | TRUE
18 | bus_LV_332-8_0_3_node_42 | 0.4 | n |  | TRUE
19 | bus_LV_332-8_0_3_node_37 | 0.4 | n |  | TRUE
20 | bus_LV_332-8_0_3_node_43 | 0.4 | n |  | TRUE
21 | bus_LV_332-8_0_3_node_38 | 0.4 | n |  | TRUE
22 | bus_LV_332-8_0_3_node_17 | 0.4 | n |  | TRUE
23 | bus_LV_332-8_0_3_node_18 | 0.4 | n |  | TRUE
24 | bus_LV_332-8_0_3_node_19 | 0.4 | n |  | TRUE
25 | bus_LV_332-8_0_3_node_20 | 0.4 | n |  | TRUE
26 | bus_LV_332-8_0_3_node_21 | 0.4 | n |  | TRUE
27 | bus_LV_332-8_0_3_node_36 | 0.4 | n |  | TRUE
28 | bus_LV_332-8_0_3_node_23 | 0.4 | n |  | TRUE
29 | bus_LV_332-8_0_3_node_53 | 0.4 | n |  | TRUE
30 | bus_LV_332-8_0_3_node_35 | 0.4 | n |  | TRUE
31 | bus_LV_332-8_0_3_node_22 | 0.4 | n |  | TRUE
32 | bus_LV_332-8_0_3_node_51 | 0.4 | n |  | TRUE
33 | bus_LV_332-8_0_3_node_24 | 0.4 | n |  | TRUE
34 | bus_LV_332-8_0_3_node_25 | 0.4 | n |  | TRUE
35 | bus_LV_332-8_0_3_node_26 | 0.4 | n |  | TRUE
36 | bus_LV_332-8_0_3_node_59 | 0.4 | n |  | TRUE
37 | bus_LV_332-8_0_3_node_27 | 0.4 | n |  | TRUE
38 | bus_LV_332-8_0_3_node_28 | 0.4 | n |  | TRUE
39 | bus_LV_332-8_0_3_node_29 | 0.4 | n |  | TRUE
40 | bus_LV_332-8_0_3_node_30 | 0.4 | n |  | TRUE
41 | bus_LV_332-8_0_3_node_34 | 0.4 | n |  | TRUE
42 | bus_LV_332-8_0_3_node_31 | 0.4 | n |  | TRUE
43 | bus_LV_332-8_0_3_node_58 | 0.4 | n |  | TRUE
44 | bus_LV_332-8_0_3_node_32 | 0.4 | n |  | TRUE
45 | bus_LV_332-8_0_3_node_33 | 0.4 | n |  | TRUE
46 | bus_LV_332-8_0_3_node_63 | 0.4 | n |  | TRUE
47 | bus_LV_332-8_0_3_node_48 | 0.4 | n |  | TRUE
48 | bus_LV_332-8_0_3_node_39 | 0.4 | n |  | TRUE
49 | bus_LV_332-8_0_3_node_40 | 0.4 | n |  | TRUE
50 | bus_LV_332-8_0_3_node_41 | 0.4 | n |  | TRUE
51 | bus_LV_332-8_0_3_node_62 | 0.4 | n |  | TRUE
52 | bus_LV_332-8_0_3_node_44 | 0.4 | n |  | TRUE
53 | bus_LV_332-8_0_3_node_45 | 0.4 | n |  | TRUE
54 | bus_LV_332-8_0_3_node_46 | 0.4 | n |  | TRUE
55 | bus_LV_332-8_0_3_node_47 | 0.4 | n |  | TRUE
56 | bus_LV_332-8_0_3_node_49 | 0.4 | n |  | TRUE
57 | bus_LV_332-8_0_3_node_55 | 0.4 | n |  | TRUE
58 | bus_LV_332-8_0_3_node_50 | 0.4 | n |  | TRUE
59 | bus_LV_332-8_0_3_node_56 | 0.4 | n |  | TRUE
60 | bus_LV_332-8_0_3_node_54 | 0.4 | n |  | TRUE
61 | bus_LV_332-8_0_3_node_52 | 0.4 | n |  | TRUE
62 | bus_LV_332-8_0_3_node_57 | 0.4 | n |  | TRUE
63 | bus_MV_476_0_node_136 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_332-8_0_3_load_0 | 0 | 0.0087241 | 0.0021865 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_332-8_0_3_load_5 | 3 | 0.004843 | 0.0012138 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_332-8_0_3_load_3 | 4 | 0.00084537 | 0.00021187 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_332-8_0_3_load_61 | 6 | 0.0040457 | 0.001014 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_332-8_0_3_load_7 | 8 | 0.0082717 | 0.0020731 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_332-8_0_3_load_10 | 10 | 0.0018283 | 0.00045821 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_332-8_0_3_load_11 | 11 | 0.0028675 | 0.00071867 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_332-8_0_3_load_12 | 12 | 0.0039143 | 0.00098102 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_332-8_0_3_load_60 | 13 | 0.0038149 | 0.00095609 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_332-8_0_3_load_13 | 14 | 0.0023294 | 0.00058381 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_332-8_0_3_load_42 | 18 | 0.001606 | 0.0004025 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_332-8_0_3_load_37 | 19 | 0.0063554 | 0.0015928 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_332-8_0_3_load_43 | 20 | 0.0013937 | 0.00034928 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_332-8_0_3_load_17 | 22 | 0.0029989 | 0.00075159 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_332-8_0_3_load_18 | 23 | 0.0023643 | 0.00059254 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_332-8_0_3_load_19 | 24 | 0.0021637 | 0.00054228 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_332-8_0_3_load_23 | 28 | 0.0023865 | 0.00059812 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_332-8_0_3_load_53 | 29 | 0.00684 | 0.0017143 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_332-8_0_3_load_35 | 30 | 0.0021092 | 0.00052862 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_332-8_0_3_load_22 | 31 | 0.007602 | 0.0019052 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_332-8_0_3_load_51 | 32 | 0.0077887 | 0.001952 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_332-8_0_3_load_25 | 34 | 0.0062896 | 0.0015763 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_332-8_0_3_load_26 | 35 | 0.021328 | 0.0053452 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_332-8_0_3_load_59 | 36 | 0.0078004 | 0.001955 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_332-8_0_3_load_27 | 37 | 0.0037855 | 0.00094872 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_332-8_0_3_load_30 | 40 | 0.0037294 | 0.00093466 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_332-8_0_3_load_34 | 41 | 0.002482 | 0.00062205 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_332-8_0_3_load_31 | 42 | 0.0024221 | 0.00060703 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_332-8_0_3_load_58 | 43 | 0.0024663 | 0.00061811 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_332-8_0_3_load_63 | 46 | 0.0019765 | 0.00049536 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_332-8_0_3_load_39 | 48 | 0.0098341 | 0.0024647 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_332-8_0_3_load_41 | 50 | 0.013152 | 0.0032962 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_332-8_0_3_load_62 | 51 | 0.0025565 | 0.00064073 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_332-8_0_3_load_44 | 52 | 0.0022286 | 0.00055854 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_332-8_0_3_load_45 | 53 | 0.0018188 | 0.00045583 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_332-8_0_3_load_47 | 55 | 0.0077067 | 0.0019315 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_332-8_0_3_load_55 | 57 | 0.0015478 | 0.00038793 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_332-8_0_3_load_50 | 58 | 0.0025132 | 0.00062988 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_332-8_0_3_load_56 | 59 | 0.0017518 | 0.00043903 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_332-8_0_3_load_54 | 60 | 0.0020311 | 0.00050904 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_332-8_0_3_load_52 | 61 | 0.0067616 | 0.0016946 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_332-8_0_3_load_57 | 62 | 0.0048448 | 0.0012142 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 33 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_332-8_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.021685 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_332-8_0_3_line_1 | NAYY 4x150 SE | 1 | 2 | 0.005065 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_332-8_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.038563 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_332-8_0_3_line_3 | NAYY 4x150 SE | 2 | 6 | 0.07434 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_332-8_0_3_line_4 | NAYY 4x150 SE | 2 | 7 | 0.002864 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_332-8_0_3_line_5 | NAYY 4x150 SE | 3 | 5 | 0.036394 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_332-8_0_3_line_6 | NAYY 4x150 SE | 4 | 5 | 0.024601 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_332-8_0_3_line_7 | NAYY 4x150 SE | 7 | 8 | 0.021335 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_332-8_0_3_line_8 | NAYY 4x150 SE | 8 | 9 | 0.036495 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_332-8_0_3_line_9 | NAYY 4x150 SE | 9 | 10 | 0.026929 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_332-8_0_3_line_10 | NAYY 4x150 SE | 9 | 11 | 0.011533 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_332-8_0_3_line_11 | NAYY 4x150 SE | 10 | 12 | 0.017315 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_332-8_0_3_line_12 | NAYY 4x150 SE | 11 | 13 | 0.015528 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_332-8_0_3_line_13 | NAYY 4x150 SE | 12 | 14 | 0.020622 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_332-8_0_3_line_14 | NAYY 4x150 SE | 14 | 15 | 0.0217 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_332-8_0_3_line_15 | NAYY 4x150 SE | 15 | 16 | 0.013973 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_332-8_0_3_line_16 | NAYY 4x150 SE | 16 | 17 | 0.023782 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_332-8_0_3_line_17 | NAYY 4x150 SE | 16 | 18 | 0.046087 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_332-8_0_3_line_18 | NAYY 4x150 SE | 17 | 19 | 0.019551 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_332-8_0_3_line_19 | NAYY 4x150 SE | 18 | 20 | 0.0094519 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_332-8_0_3_line_20 | NAYY 4x150 SE | 19 | 21 | 0.047909 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_332-8_0_3_line_21 | NAYY 4x150 SE | 20 | 34 | 0.025638 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_332-8_0_3_line_22 | NAYY 4x150 SE | 21 | 48 | 0.021313 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_332-8_0_3_line_23 | NAYY 4x150 SE | 21 | 49 | 0.027966 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_332-8_0_3_line_24 | NAYY 4x150 SE | 22 | 23 | 0.015772 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_332-8_0_3_line_25 | NAYY 4x150 SE | 22 | 24 | 0.0068954 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_332-8_0_3_line_26 | NAYY 4x150 SE | 23 | 25 | 0.01701 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_332-8_0_3_line_27 | NAYY 4x150 SE | 24 | 26 | 0.0085313 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_332-8_0_3_line_28 | NAYY 4x150 SE | 25 | 27 | 0.10852 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_332-8_0_3_line_29 | NAYY 4x150 SE | 26 | 28 | 0.023804 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_332-8_0_3_line_30 | NAYY 4x150 SE | 26 | 29 | 0.030957 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_332-8_0_3_line_31 | NAYY 4x150 SE | 27 | 30 | 0.0067835 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_332-8_0_3_line_32 | NAYY 4x150 SE | 28 | 31 | 0.00067811 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_332-8_0_3_line_33 | NAYY 4x150 SE | 29 | 32 | 0.013445 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_332-8_0_3_line_34 | NAYY 4x150 SE | 30 | 40 | 0.028965 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_332-8_0_3_line_35 | NAYY 4x150 SE | 31 | 33 | 0.025081 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_332-8_0_3_line_36 | NAYY 4x150 SE | 32 | 61 | 0.0036335 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_332-8_0_3_line_37 | NAYY 4x150 SE | 33 | 34 | 0.010203 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_332-8_0_3_line_38 | NAYY 4x150 SE | 33 | 35 | 0.046727 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_332-8_0_3_line_39 | NAYY 4x150 SE | 35 | 36 | 0.072681 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_332-8_0_3_line_40 | NAYY 4x150 SE | 37 | 38 | 0.015733 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_332-8_0_3_line_41 | NAYY 4x150 SE | 38 | 39 | 0.012274 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_332-8_0_3_line_42 | NAYY 4x150 SE | 38 | 40 | 0.015443 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_332-8_0_3_line_43 | NAYY 4x150 SE | 39 | 41 | 0.028009 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_332-8_0_3_line_44 | NAYY 4x150 SE | 39 | 42 | 0.039011 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_332-8_0_3_line_45 | NAYY 4x150 SE | 41 | 43 | 0.00075741 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_332-8_0_3_line_46 | NAYY 4x150 SE | 42 | 44 | 0.03696 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_332-8_0_3_line_47 | NAYY 4x150 SE | 43 | 47 | 0.024382 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_332-8_0_3_line_48 | NAYY 4x150 SE | 44 | 45 | 0.062319 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_332-8_0_3_line_49 | NAYY 4x150 SE | 45 | 46 | 0.041846 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_332-8_0_3_line_50 | NAYY 4x150 SE | 47 | 57 | 0.010873 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_332-8_0_3_line_51 | NAYY 4x150 SE | 47 | 54 | 0.018494 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_332-8_0_3_line_52 | NAYY 4x150 SE | 48 | 50 | 0.017729 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_332-8_0_3_line_53 | NAYY 4x150 SE | 49 | 51 | 0.028088 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_332-8_0_3_line_54 | NAYY 4x150 SE | 52 | 53 | 0.0079227 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_332-8_0_3_line_55 | NAYY 4x150 SE | 52 | 54 | 0.013957 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_332-8_0_3_line_56 | NAYY 4x150 SE | 54 | 55 | 0.018744 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_332-8_0_3_line_57 | NAYY 4x150 SE | 55 | 56 | 0.0036022 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_332-8_0_3_line_58 | NAYY 4x150 SE | 56 | 58 | 0.018764 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_332-8_0_3_line_59 | NAYY 4x150 SE | 57 | 59 | 0.00043269 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_332-8_0_3_line_60 | NAYY 4x150 SE | 58 | 60 | 0.0039184 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_332-8_0_3_line_61 | NAYY 4x150 SE | 59 | 62 | 0.01661 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_332-8_0_3_trafo_24 | 0.25 MVA 20/0.4 kV | 63 | 33 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2627137.9668 | 1223940.5217 | 2627125.3242 | 1223944.5221 | 2627117.8146 | 1223948.3399
1 | 2627137.9668 | 1223940.5217 | 2627142.9205 | 1223941.6449
2 | 2627137.9668 | 1223940.5217 | 2627132.4312 | 1223930.6573 | 2627117.8306 | 1223907.6476
3 | 2627158.548 | 1223881.6027 | 2627144.5083 | 1223886.0192 | 2627137.1196 | 1223893.4455 | 2627140.7506 | 1223903.6458 | 2627143.9523 | 1223918.1801 | 2627142.9205 | 1223941.6449
4 | 2627142.9205 | 1223941.6449 | 2627145.7463 | 1223942.158
5 | 2627101.2318 | 1223875.2938 | 2627114.5666 | 1223902.5038 | 2627117.8306 | 1223907.6476
6 | 2627101.2318 | 1223875.2938 | 2627095.7906 | 1223884.6635 | 2627095.7503 | 1223898.4296
7 | 2627145.7463 | 1223942.158 | 2627152.467 | 1223938.1974 | 2627165.5848 | 1223934.8677
8 | 2627200.9584 | 1223925.8888 | 2627165.5848 | 1223934.8677
9 | 2627200.9584 | 1223925.8888 | 2627212.4133 | 1223922.9727 | 2627227.191 | 1223919.8276
10 | 2627200.9584 | 1223925.8888 | 2627197.8795 | 1223914.7749
11 | 2627227.191 | 1223919.8276 | 2627244.1269 | 1223916.2233
12 | 2627197.405 | 1223900.3798 | 2627194.9387 | 1223904.1597 | 2627197.8795 | 1223914.7749
13 | 2627244.1269 | 1223916.2233 | 2627264.2972 | 1223911.9305
14 | 2627285.4202 | 1223906.9746 | 2627273.9349 | 1223909.8793 | 2627264.2972 | 1223911.9305
15 | 2627290.9987 | 1223894.1592 | 2627285.4202 | 1223906.9746
16 | 2627290.9987 | 1223894.1592 | 2627302.0098 | 1223897.1225 | 2627308.4075 | 1223899.153 | 2627312.1387 | 1223900.6598 | 2627313.5904 | 1223901.5559
17 | 2627290.9987 | 1223894.1592 | 2627291.0865 | 1223884.9319 | 2627288.9819 | 1223870.9696 | 2627283.5252 | 1223852.1891 | 2627282.4484 | 1223849.1945
18 | 2627313.5904 | 1223901.5559 | 2627321.9187 | 1223890.9656 | 2627325.8402 | 1223886.3221
19 | 2627282.4484 | 1223849.1945 | 2627279.2502 | 1223840.3001
20 | 2627356.7512 | 1223849.7786 | 2627347.017 | 1223862.675 | 2627333.7126 | 1223877.0002 | 2627325.8402 | 1223886.3221
21 | 2627270.467 | 1223816.2131 | 2627277.6029 | 1223835.7189 | 2627279.2502 | 1223840.3001
22 | 2627356.7512 | 1223849.7786 | 2627342.2778 | 1223834.134
23 | 2627356.7512 | 1223849.7786 | 2627361.5103 | 1223842.107 | 2627371.2296 | 1223825.8531
24 | 2627213.3798 | 1223747.1354 | 2627218.5155 | 1223752.2774 | 2627224.7676 | 1223758.0427
25 | 2627229.8368 | 1223762.7172 | 2627224.7676 | 1223758.0427
26 | 2627201.359 | 1223735.1001 | 2627213.3798 | 1223747.1354
27 | 2627236.1085 | 1223768.5007 | 2627229.8368 | 1223762.7172
28 | 2627201.359 | 1223735.1001 | 2627185.3 | 1223716.6493 | 2627176.5399 | 1223707.1816 | 2627182.6243 | 1223703.1625 | 2627197.6914 | 1223698.0281 | 2627244.2549 | 1223686.5894
29 | 2627236.1085 | 1223768.5007 | 2627248.4645 | 1223779.2079 | 2627253.0786 | 1223785.063
30 | 2627236.1085 | 1223768.5007 | 2627240.0326 | 1223756.0334 | 2627243.8319 | 1223750.9367 | 2627241.9753 | 1223744.0686 | 2627246.1346 | 1223742.5863
31 | 2627244.2549 | 1223686.5894 | 2627250.8653 | 1223685.0669
32 | 2627253.0786 | 1223785.063 | 2627253.4983 | 1223785.5956
33 | 2627258.7999 | 1223738.0728 | 2627246.1346 | 1223742.5863
34 | 2627250.8653 | 1223685.0669 | 2627279.0914 | 1223678.5657
35 | 2627266.9614 | 1223806.6308 | 2627266.0554 | 1223804.1363 | 2627258.6643 | 1223792.151 | 2627253.4983 | 1223785.5956
36 | 2627258.7999 | 1223738.0728 | 2627262.2225 | 1223736.8531
37 | 2627266.9614 | 1223806.6308 | 2627270.467 | 1223816.2131
38 | 2627266.9614 | 1223806.6308 | 2627222.8977 | 1223822.1815
39 | 2627177.2628 | 1223798.0942 | 2627181.3012 | 1223812.043 | 2627185.7155 | 1223825.0597 | 2627187.5417 | 1223831.9499 | 2627190.1458 | 1223832.8845 | 2627194.6227 | 1223832.1601 | 2627222.8977 | 1223822.1815
40 | 2627294.14 | 1223675.0996 | 2627294.7051 | 1223659.3764
41 | 2627294.14 | 1223675.0996 | 2627306.2074 | 1223672.6757
42 | 2627294.14 | 1223675.0996 | 2627279.0914 | 1223678.5657
43 | 2627306.2074 | 1223672.6757 | 2627310.3839 | 1223700.3718
44 | 2627306.2074 | 1223672.6757 | 2627343.9856 | 1223662.9472
45 | 2627310.3839 | 1223700.3718 | 2627310.4969 | 1223701.1207
46 | 2627379.9556 | 1223654.4697 | 2627356.3874 | 1223659.7535 | 2627343.9856 | 1223662.9472
47 | 2627315.3017 | 1223725.0149 | 2627311.3881 | 1223707.0308 | 2627310.4969 | 1223701.1207
48 | 2627379.9556 | 1223654.4697 | 2627381.8054 | 1223661.1488 | 2627389.6262 | 1223685.21 | 2627395.958 | 1223708.2416 | 2627397.796 | 1223714.1647
49 | 2627397.796 | 1223714.1647 | 2627385.8426 | 1223716.5556 | 2627372.258 | 1223719.1503 | 2627368.8095 | 1223713.8536 | 2627362.2629 | 1223714.4906 | 2627359.9974 | 1223712.479
50 | 2627315.3017 | 1223725.0149 | 2627304.7318 | 1223727.5647
51 | 2627315.3017 | 1223725.0149 | 2627319.1693 | 1223743.0989
52 | 2627329.8772 | 1223822.1502 | 2627332.5738 | 1223822.7518 | 2627337.9417 | 1223829.447 | 2627342.2778 | 1223834.134
53 | 2627371.2296 | 1223825.8531 | 2627351.4328 | 1223805.8727
54 | 2627332.7323 | 1223739.8066 | 2627340.4315 | 1223737.9377
55 | 2627319.1693 | 1223743.0989 | 2627332.7323 | 1223739.8066
56 | 2627319.1693 | 1223743.0989 | 2627322.6147 | 1223761.5232
57 | 2627323.2769 | 1223765.064 | 2627322.6147 | 1223761.5232
58 | 2627323.2769 | 1223765.064 | 2627341.1995 | 1223759.5081
59 | 2627304.3112 | 1223727.6661 | 2627304.7318 | 1223727.5647
60 | 2627344.9422 | 1223758.3479 | 2627341.1995 | 1223759.5081
61 | 2627288.1643 | 1223731.5612 | 2627304.3112 | 1223727.6661

## bus_geodata
| x | y | coords
0 | 2627117.8146 | 1223948.3399
1 | 2627137.9668 | 1223940.5217
2 | 2627142.9205 | 1223941.6449
3 | 2627117.8306 | 1223907.6476
4 | 2627095.7503 | 1223898.4296
5 | 2627101.2318 | 1223875.2938
6 | 2627158.548 | 1223881.6027
7 | 2627145.7463 | 1223942.158
8 | 2627165.5848 | 1223934.8677
9 | 2627200.9584 | 1223925.8888
10 | 2627227.191 | 1223919.8276
11 | 2627197.8795 | 1223914.7749
12 | 2627244.1269 | 1223916.2233
13 | 2627197.405 | 1223900.3798
14 | 2627264.2972 | 1223911.9305
15 | 2627285.4202 | 1223906.9746
16 | 2627290.9987 | 1223894.1592
17 | 2627313.5904 | 1223901.5559
18 | 2627282.4484 | 1223849.1945
19 | 2627325.8402 | 1223886.3221
20 | 2627279.2502 | 1223840.3001
21 | 2627356.7512 | 1223849.7786
22 | 2627224.7676 | 1223758.0427
23 | 2627213.3798 | 1223747.1354
24 | 2627229.8368 | 1223762.7172
25 | 2627201.359 | 1223735.1001
26 | 2627236.1085 | 1223768.5007
27 | 2627244.2549 | 1223686.5894
28 | 2627253.0786 | 1223785.063
29 | 2627246.1346 | 1223742.5863
30 | 2627250.8653 | 1223685.0669
31 | 2627253.4983 | 1223785.5956
32 | 2627258.7999 | 1223738.0728
33 | 2627266.9614 | 1223806.6308
34 | 2627270.467 | 1223816.2131
35 | 2627222.8977 | 1223822.1815
36 | 2627177.2628 | 1223798.0942
37 | 2627294.7051 | 1223659.3764
38 | 2627294.14 | 1223675.0996
39 | 2627306.2074 | 1223672.6757
40 | 2627279.0914 | 1223678.5657
41 | 2627310.3839 | 1223700.3718
42 | 2627343.9856 | 1223662.9472
43 | 2627310.4969 | 1223701.1207
44 | 2627379.9556 | 1223654.4697
45 | 2627397.796 | 1223714.1647
46 | 2627359.9974 | 1223712.479
47 | 2627315.3017 | 1223725.0149
48 | 2627342.2778 | 1223834.134
49 | 2627371.2296 | 1223825.8531
50 | 2627329.8772 | 1223822.1502
51 | 2627351.4328 | 1223805.8727
52 | 2627332.7323 | 1223739.8066
53 | 2627340.4315 | 1223737.9377
54 | 2627319.1693 | 1223743.0989
55 | 2627322.6147 | 1223761.5232
56 | 2627323.2769 | 1223765.064
57 | 2627304.7318 | 1223727.5647
58 | 2627341.1995 | 1223759.5081
59 | 2627304.3112 | 1223727.6661
60 | 2627344.9422 | 1223758.3479
61 | 2627262.2225 | 1223736.8531
62 | 2627288.1643 | 1223731.5612
63 | 2627236.1085 | 1223768.5007

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1