## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_338-6_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_338-6_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_338-6_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_338-6_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_338-6_0_3_node_27 | 0.4 | n |  | TRUE
5 | bus_LV_338-6_0_3_node_14 | 0.4 | n |  | TRUE
6 | bus_LV_338-6_0_3_node_9 | 0.4 | n |  | TRUE
7 | bus_LV_338-6_0_3_node_28 | 0.4 | n |  | TRUE
8 | bus_LV_338-6_0_3_node_15 | 0.4 | n |  | TRUE
9 | bus_LV_338-6_0_3_node_10 | 0.4 | n |  | TRUE
10 | bus_LV_338-6_0_3_node_4 | 0.4 | n |  | TRUE
11 | bus_LV_338-6_0_3_node_5 | 0.4 | n |  | TRUE
12 | bus_LV_338-6_0_3_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_338-6_0_3_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_338-6_0_3_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_338-6_0_3_node_20 | 0.4 | n |  | TRUE
16 | bus_LV_338-6_0_3_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_338-6_0_3_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_338-6_0_3_node_16 | 0.4 | n |  | TRUE
19 | bus_LV_338-6_0_3_node_33 | 0.4 | n |  | TRUE
20 | bus_LV_338-6_0_3_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_338-6_0_3_node_32 | 0.4 | n |  | TRUE
22 | bus_LV_338-6_0_3_node_31 | 0.4 | n |  | TRUE
23 | bus_LV_338-6_0_3_node_17 | 0.4 | n |  | TRUE
24 | bus_LV_338-6_0_3_node_18 | 0.4 | n |  | TRUE
25 | bus_LV_338-6_0_3_node_19 | 0.4 | n |  | TRUE
26 | bus_LV_338-6_0_3_node_30 | 0.4 | n |  | TRUE
27 | bus_LV_338-6_0_3_node_23 | 0.4 | n |  | TRUE
28 | bus_LV_338-6_0_3_node_24 | 0.4 | n |  | TRUE
29 | bus_LV_338-6_0_3_node_22 | 0.4 | n |  | TRUE
30 | bus_MV_129_2_node_203 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_338-6_0_3_load_0 | 0 | 0.031566 | 0.0079113 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_338-6_0_3_load_27 | 4 | 0.073048 | 0.018308 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_338-6_0_3_load_14 | 5 | 0.033153 | 0.0083088 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_338-6_0_3_load_9 | 6 | 0.0014911 | 0.00037371 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_338-6_0_3_load_28 | 7 | 0.01052 | 0.0026365 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_338-6_0_3_load_15 | 8 | 0.001845 | 0.00046239 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_338-6_0_3_load_4 | 10 | 0.0018016 | 0.00045151 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_338-6_0_3_load_5 | 11 | 0.0016954 | 0.00042491 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_338-6_0_3_load_6 | 12 | 0.0052401 | 0.0013133 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_338-6_0_3_load_7 | 13 | 0.0029073 | 0.00072864 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_338-6_0_3_load_8 | 14 | 0.0013416 | 0.00033624 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_338-6_0_3_load_20 | 15 | 0.0013932 | 0.00034916 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_338-6_0_3_load_11 | 16 | 0.0013506 | 0.00033848 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_338-6_0_3_load_33 | 19 | 0.0055031 | 0.0013792 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_338-6_0_3_load_32 | 21 | 0.00646 | 0.001619 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_338-6_0_3_load_17 | 23 | 0.0021609 | 0.00054156 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_338-6_0_3_load_18 | 24 | 0.0012699 | 0.00031827 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_338-6_0_3_load_19 | 25 | 0.0024001 | 0.00060151 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_338-6_0_3_load_30 | 26 | 0.010919 | 0.0027365 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_338-6_0_3_load_23 | 27 | 0.0014824 | 0.00037153 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_338-6_0_3_load_24 | 28 | 0.0012673 | 0.00031762 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_338-6_0_3_load_22 | 29 | 0.001207 | 0.0003025 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 5 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_338-6_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.017514 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_338-6_0_3_line_1 | NAYY 4x150 SE | 1 | 2 | 0.027038 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_338-6_0_3_line_2 | NAYY 4x150 SE | 2 | 3 | 0.12343 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
3 | LV_338-6_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.077886 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_338-6_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.019627 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
5 | LV_338-6_0_3_line_5 | NAYY 4x150 SE | 3 | 6 | 0.027675 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_338-6_0_3_line_6 | NAYY 4x150 SE | 4 | 7 | 0.055699 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_338-6_0_3_line_7 | NAYY 4x150 SE | 5 | 8 | 0.031772 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_338-6_0_3_line_8 | NAYY 4x150 SE | 6 | 9 | 0.011063 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_338-6_0_3_line_9 | NAYY 4x150 SE | 8 | 13 | 0.0018126 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_338-6_0_3_line_10 | NAYY 4x150 SE | 9 | 16 | 0.014156 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_338-6_0_3_line_11 | NAYY 4x150 SE | 9 | 17 | 0.039361 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_338-6_0_3_line_12 | NAYY 4x150 SE | 10 | 11 | 0.0041704 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_338-6_0_3_line_13 | NAYY 4x150 SE | 10 | 12 | 0.022529 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_338-6_0_3_line_14 | NAYY 4x150 SE | 11 | 13 | 0.022514 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_338-6_0_3_line_15 | NAYY 4x150 SE | 12 | 14 | 0.00707 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_338-6_0_3_line_16 | NAYY 4x150 SE | 14 | 15 | 0.021098 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_338-6_0_3_line_17 | NAYY 4x150 SE | 16 | 18 | 0.036965 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_338-6_0_3_line_18 | NAYY 4x150 SE | 17 | 19 | 0.011217 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_338-6_0_3_line_19 | NAYY 4x150 SE | 17 | 20 | 0.020745 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_338-6_0_3_line_20 | NAYY 4x150 SE | 18 | 23 | 0.015869 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_338-6_0_3_line_21 | NAYY 4x150 SE | 18 | 24 | 0.019391 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_338-6_0_3_line_22 | NAYY 4x150 SE | 18 | 25 | 0.042739 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_338-6_0_3_line_23 | NAYY 4x150 SE | 20 | 21 | 0.008658 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_338-6_0_3_line_24 | NAYY 4x150 SE | 20 | 22 | 0.034503 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_338-6_0_3_line_25 | NAYY 4x150 SE | 22 | 26 | 0.016198 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_338-6_0_3_line_26 | NAYY 4x150 SE | 23 | 27 | 0.028619 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_338-6_0_3_line_27 | NAYY 4x150 SE | 24 | 28 | 0.0032736 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_338-6_0_3_line_28 | NAYY 4x150 SE | 27 | 29 | 0.020165 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_338-6_0_3_trafo_14 | 0.25 MVA 20/0.4 kV | 30 | 5 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2628870.6725 | 1220473.4049 | 2628857.6521 | 1220461.6908
1 | 2628847.2679 | 1220482.7749 | 2628853.0744 | 1220483.7702 | 2628856.3089 | 1220483.23 | 2628858.9132 | 1220482.8202 | 2628861.9087 | 1220481.4894 | 2628866.3031 | 1220478.0086 | 2628870.6725 | 1220473.4049
2 | 2628847.2679 | 1220482.7749 | 2628853.0744 | 1220483.7702 | 2628856.3089 | 1220483.23 | 2628857.5305 | 1220491.0516 | 2628859.6967 | 1220494.9199 | 2628904.2772 | 1220535.3149 | 2628931.9455 | 1220566.5784
3 | 2628847.2679 | 1220482.7749 | 2628849.2285 | 1220491.5117 | 2628846.6544 | 1220498.2477 | 2628837.5904 | 1220515.0804 | 2628831.3059 | 1220523.4994 | 2628827.2305 | 1220526.9373 | 2628824.797 | 1220528.1151 | 2628817.1225 | 1220530.6239 | 2628814.0239 | 1220532.8547 | 2628806.2768 | 1220542.2393
4 | 2628931.9455 | 1220566.5784 | 2628928.3374 | 1220570.63 | 2628919.5916 | 1220581.8188
5 | 2628931.9455 | 1220566.5784 | 2628947.3892 | 1220589.544
6 | 2628806.2768 | 1220542.2393 | 2628797.6702 | 1220552.6651 | 2628793.6137 | 1220558.4712 | 2628791.1267 | 1220561.3386 | 2628770.3123 | 1220584.7159
7 | 2628919.5916 | 1220581.8188 | 2628900.0254 | 1220606.8507
8 | 2628953.5628 | 1220598.7244 | 2628947.3892 | 1220589.544
9 | 2628898.9091 | 1220608.2787 | 2628900.0254 | 1220606.8507
10 | 2628953.5628 | 1220598.7244 | 2628960.8989 | 1220610.8314
11 | 2628986.4095 | 1220588.3889 | 2628980.2529 | 1220582.9669 | 2628972.3933 | 1220589.1991 | 2628964.869 | 1220593.5651 | 2628953.5628 | 1220598.7244
12 | 2628882.4756 | 1220629.3027 | 2628885.044 | 1220626.0169
13 | 2628882.4756 | 1220629.3027 | 2628868.6012 | 1220647.0527
14 | 2628885.044 | 1220626.0169 | 2628898.9091 | 1220608.2787
15 | 2628864.2472 | 1220652.623 | 2628868.6012 | 1220647.0527
16 | 2628864.2472 | 1220652.623 | 2628851.254 | 1220669.2456
17 | 2628980.0548 | 1220642.4453 | 2628960.8989 | 1220610.8314
18 | 2628990.4402 | 1220598.8591 | 2628986.4095 | 1220588.3889
19 | 2628986.4095 | 1220588.3889 | 2628980.2529 | 1220582.9669 | 2628989.1267 | 1220574.1049
20 | 2628980.0548 | 1220642.4453 | 2628974.8966 | 1220645.4442 | 2628966.0898 | 1220649.9723
21 | 2628980.0548 | 1220642.4453 | 2628989.5188 | 1220659.3697
22 | 2628980.0548 | 1220642.4453 | 2628985.1968 | 1220639.6575 | 2629016.001 | 1220619.3604
23 | 2628996.425 | 1220569.4154 | 2628989.1267 | 1220574.1049
24 | 2628971.5571 | 1220545.8141 | 2628976.0639 | 1220548.8599 | 2628980.3996 | 1220552.7833 | 2628984.3969 | 1220559.1842 | 2628985.1547 | 1220562.4899 | 2628987.0568 | 1220567.6132 | 2628989.1267 | 1220574.1049
25 | 2628971.5571 | 1220545.8141 | 2628961.1104 | 1220550.4994 | 2628956.7914 | 1220552.4734
26 | 2628966.0898 | 1220649.9723 | 2628940.6377 | 1220663.0588
27 | 2628991.1166 | 1220662.2269 | 2628989.5188 | 1220659.3697
28 | 2628922.7046 | 1220672.2794 | 2628940.6377 | 1220663.0588

## bus_geodata
| x | y | coords
0 | 2628857.6521 | 1220461.6908
1 | 2628870.6725 | 1220473.4049
2 | 2628847.2679 | 1220482.7749
3 | 2628931.9455 | 1220566.5784
4 | 2628806.2768 | 1220542.2393
5 | 2628919.5916 | 1220581.8188
6 | 2628947.3892 | 1220589.544
7 | 2628770.3123 | 1220584.7159
8 | 2628900.0254 | 1220606.8507
9 | 2628953.5628 | 1220598.7244
10 | 2628882.4756 | 1220629.3027
11 | 2628885.044 | 1220626.0169
12 | 2628868.6012 | 1220647.0527
13 | 2628898.9091 | 1220608.2787
14 | 2628864.2472 | 1220652.623
15 | 2628851.254 | 1220669.2456
16 | 2628960.8989 | 1220610.8314
17 | 2628986.4095 | 1220588.3889
18 | 2628980.0548 | 1220642.4453
19 | 2628990.4402 | 1220598.8591
20 | 2628989.1267 | 1220574.1049
21 | 2628996.425 | 1220569.4154
22 | 2628971.5571 | 1220545.8141
23 | 2628966.0898 | 1220649.9723
24 | 2628989.5188 | 1220659.3697
25 | 2629016.001 | 1220619.3604
26 | 2628956.7914 | 1220552.4734
27 | 2628940.6377 | 1220663.0588
28 | 2628991.1166 | 1220662.2269
29 | 2628922.7046 | 1220672.2794
30 | 2628931.9455 | 1220566.5784

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98549 | -0.1012 | 0.031566 | 0.0079113
1 | 0.98629 | -0.095523 | 0 | 0
2 | 0.98752 | -0.086776 | 0 | 0
3 | 0.99786 | -0.014793 | 0 | 0
4 | 0.97803 | -0.15404 | 0.073048 | 0.018308
5 | 1 | 0 | -0.17016 | -0.042769
6 | 0.99645 | -0.024667 | 0.0014911 | 0.00037371
7 | 0.97718 | -0.16016 | 0.01052 | 0.0026365
8 | 0.99926 | -0.0051512 | 0.001845 | 0.00046239
9 | 0.99591 | -0.028456 | 0 | 0
10 | 0.9988 | -0.0084041 | 0.0018016 | 0.00045151
11 | 0.99886 | -0.007996 | 0.0016954 | 0.00042491
12 | 0.99854 | -0.010203 | 0.0052401 | 0.0013133
13 | 0.99923 | -0.0054119 | 0.0029073 | 0.00072864
14 | 0.99852 | -0.010397 | 0.0013416 | 0.00033624
15 | 0.99847 | -0.010691 | 0.0013932 | 0.00034916
16 | 0.99568 | -0.030045 | 0.0013506 | 0.00033848
17 | 0.99462 | -0.037534 | 0 | 0
18 | 0.99516 | -0.033694 | 0 | 0
19 | 0.99453 | -0.038157 | 0.0055031 | 0.0013792
20 | 0.9941 | -0.041175 | 0 | 0
21 | 0.99402 | -0.04174 | 0.00646 | 0.001619
22 | 0.99356 | -0.044983 | 0 | 0
23 | 0.99505 | -0.034471 | 0.0021609 | 0.00054156
24 | 0.99509 | -0.034191 | 0.0012699 | 0.00031827
25 | 0.99502 | -0.034729 | 0.0024001 | 0.00060151
26 | 0.99331 | -0.046771 | 0.010919 | 0.0027365
27 | 0.99494 | -0.035248 | 0.0014824 | 0.00037153
28 | 0.99509 | -0.034232 | 0.0012673 | 0.00031762
29 | 0.99491 | -0.035494 | 0.001207 | 0.0003025
30 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.031566 | -0.0079113 | 0.031591 | 0.0079206 | 2.4828e-05 | 9.3259e-06 | 0.047663 | 0.047663 | 0.047663 | 0.98549 | -0.1012 | 0.98629 | -0.095523 | 17.653
1 | -0.031591 | -0.0079206 | 0.03163 | 0.007935 | 3.8328e-05 | 1.4396e-05 | 0.047663 | 0.047663 | 0.047663 | 0.98629 | -0.095523 | 0.98752 | -0.086776 | 17.653
2 | -0.11599 | -0.029183 | 0.11717 | 0.029633 | 0.0011769 | 0.00044947 | 0.17482 | 0.17482 | 0.17482 | 0.98752 | -0.086776 | 0.99786 | -0.014793 | 32.374
3 | 0.084363 | 0.021248 | -0.083577 | -0.020947 | 0.00078582 | 0.00030125 | 0.12716 | 0.12716 | 0.12716 | 0.98752 | -0.086776 | 0.97803 | -0.15404 | 47.0953
4 | -0.1528 | -0.038575 | 0.15312 | 0.038697 | 0.00031821 | 0.00012188 | 0.22796 | 0.22796 | 0.22796 | 0.99786 | -0.014793 | 1 | 0 | 42.2148
5 | 0.035634 | 0.0089425 | -0.035585 | -0.0089241 | 4.8769e-05 | 1.8396e-05 | 0.053141 | 0.053141 | 0.053141 | 0.99786 | -0.014793 | 0.99645 | -0.024667 | 19.682
6 | 0.010529 | 0.0026393 | -0.01052 | -0.0026365 | 8.9188e-06 | 2.7319e-06 | 0.016019 | 0.016019 | 0.016019 | 0.97803 | -0.15404 | 0.97718 | -0.16016 | 5.9331
7 | 0.016243 | 0.004072 | -0.016231 | -0.0040679 | 1.1582e-05 | 4.0381e-06 | 0.02417 | 0.02417 | 0.02417 | 1 | 0 | 0.99926 | -0.0051512 | 8.952
8 | 0.034094 | 0.0085504 | -0.034076 | -0.0085436 | 1.7896e-05 | 6.739e-06 | 0.050915 | 0.050915 | 0.050915 | 0.99645 | -0.024667 | 0.99591 | -0.028456 | 18.8573
9 | 0.014386 | 0.0036055 | -0.014386 | -0.0036054 | 5.1908e-07 | 1.759e-07 | 0.021423 | 0.021423 | 0.021423 | 0.99926 | -0.0051512 | 0.99923 | -0.0054119 | 7.9345
10 | 0.011147 | 0.0027925 | -0.011144 | -0.0027917 | 2.4502e-06 | 7.5821e-07 | 0.016654 | 0.016655 | 0.016655 | 0.99591 | -0.028456 | 0.99568 | -0.030045 | 6.1684
11 | 0.022929 | 0.0057511 | -0.0229 | -0.0057405 | 2.883e-05 | 1.0577e-05 | 0.03426 | 0.03426 | 0.03426 | 0.99591 | -0.028456 | 0.99462 | -0.037534 | 12.6891
12 | -0.0097786 | -0.0024504 | 0.0097791 | 0.0024505 | 5.5229e-07 | 1.5783e-07 | 0.014568 | 0.014568 | 0.014568 | 0.9988 | -0.0084041 | 0.99886 | -0.007996 | 5.3956
13 | 0.007977 | 0.0019988 | -0.007975 | -0.0019984 | 1.9855e-06 | 4.6886e-07 | 0.011884 | 0.011884 | 0.011884 | 0.9988 | -0.0084041 | 0.99854 | -0.010203 | 4.4015
14 | -0.011475 | -0.0028754 | 0.011479 | 0.0028767 | 4.1049e-06 | 1.284e-06 | 0.017094 | 0.017094 | 0.017094 | 0.99886 | -0.007996 | 0.99923 | -0.0054119 | 6.331
15 | 0.0027349 | 0.00068508 | -0.0027348 | -0.00068515 | 7.3274e-08 | -6.4299e-08 | 0.0040754 | 0.0040754 | 0.0040754 | 0.99854 | -0.010203 | 0.99852 | -0.010397 | 1.5094
16 | 0.0013932 | 0.00034891 | -0.0013932 | -0.00034916 | 5.6749e-08 | -2.5413e-07 | 0.0020761 | 0.0020762 | 0.0020762 | 0.99852 | -0.010397 | 0.99847 | -0.010691 | 0.76897
17 | 0.0097939 | 0.0024533 | -0.0097889 | -0.0024518 | 4.9412e-06 | 1.4199e-06 | 0.014636 | 0.014636 | 0.014636 | 0.99568 | -0.030045 | 0.99516 | -0.033694 | 5.4209
18 | 0.0055036 | 0.0013793 | -0.0055031 | -0.0013792 | 4.7453e-07 | 3.6945e-08 | 0.0082338 | 0.0082338 | 0.0082338 | 0.99462 | -0.037534 | 0.99453 | -0.038157 | 3.0496
19 | 0.017396 | 0.0043613 | -0.017388 | -0.0043582 | 8.7687e-06 | 3.1035e-06 | 0.026027 | 0.026027 | 0.026027 | 0.99462 | -0.037534 | 0.9941 | -0.041175 | 9.6395
20 | 0.0048511 | 0.0012151 | -0.0048506 | -0.0012151 | 5.2099e-07 | -5.7813e-09 | 0.0072534 | 0.0072535 | 0.0072535 | 0.99516 | -0.033694 | 0.99505 | -0.034471 | 2.6865
21 | 0.0025374 | 0.00063566 | -0.0025372 | -0.00063585 | 1.7417e-07 | -1.8493e-07 | 0.0037939 | 0.003794 | 0.003794 | 0.99516 | -0.033694 | 0.99509 | -0.034191 | 1.4052
22 | 0.0024004 | 0.00060109 | -0.0024001 | -0.00060151 | 3.4355e-07 | -4.2308e-07 | 0.003589 | 0.0035892 | 0.0035892 | 0.99516 | -0.033694 | 0.99502 | -0.034729 | 1.3293
23 | 0.0064605 | 0.0016191 | -0.00646 | -0.001619 | 5.0523e-07 | 8.2078e-08 | 0.0096704 | 0.0096704 | 0.0096704 | 0.9941 | -0.041175 | 0.99402 | -0.04174 | 3.5816
24 | 0.010927 | 0.0027391 | -0.010921 | -0.0027373 | 5.7601e-06 | 1.7683e-06 | 0.016356 | 0.016357 | 0.016357 | 0.9941 | -0.041175 | 0.99356 | -0.044983 | 6.058
25 | 0.010921 | 0.0027373 | -0.010919 | -0.0027365 | 2.7042e-06 | 8.3034e-07 | 0.016357 | 0.016357 | 0.016357 | 0.99356 | -0.044983 | 0.99331 | -0.046771 | 6.058
26 | 0.0026898 | 0.00067353 | -0.0026895 | -0.00067379 | 2.8891e-07 | -2.606e-07 | 0.0040221 | 0.0040222 | 0.0040222 | 0.99505 | -0.034471 | 0.99494 | -0.035248 | 1.4897
27 | 0.0012673 | 0.00031758 | -0.0012673 | -0.00031762 | 7.3362e-09 | -3.9705e-08 | 0.0018951 | 0.0018951 | 0.0018951 | 0.99509 | -0.034191 | 0.99509 | -0.034232 | 0.70189
28 | 0.001207 | 0.00030226 | -0.001207 | -0.0003025 | 4.1003e-08 | -2.461e-07 | 0.0018051 | 0.0018052 | 0.0018052 | 0.99494 | -0.035248 | 0.99491 | -0.035494 | 0.6686

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.20332 | 0.051078

## res_load
| p_mw | q_mvar
0 | 0.031566 | 0.0079113
1 | 0.073048 | 0.018308
2 | 0.033153 | 0.0083088
3 | 0.0014911 | 0.00037371
4 | 0.01052 | 0.0026365
5 | 0.001845 | 0.00046239
6 | 0.0018016 | 0.00045151
7 | 0.0016954 | 0.00042491
8 | 0.0052401 | 0.0013133
9 | 0.0029073 | 0.00072864
10 | 0.0013416 | 0.00033624
11 | 0.0013932 | 0.00034916
12 | 0.0013506 | 0.00033848
13 | 0.0055031 | 0.0013792
14 | 0.00646 | 0.001619
15 | 0.0021609 | 0.00054156
16 | 0.0012699 | 0.00031827
17 | 0.0024001 | 0.00060151
18 | 0.010919 | 0.0027365
19 | 0.0014824 | 0.00037153
20 | 0.0012673 | 0.00031762
21 | 0.001207 | 0.0003025

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1