## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_4143-1_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_4143-1_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_4143-1_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_4143-1_0_4_node_50 | 0.4 | n |  | TRUE
4 | bus_LV_4143-1_0_4_node_68 | 0.4 | n |  | TRUE
5 | bus_LV_4143-1_0_4_node_46 | 0.4 | n |  | TRUE
6 | bus_LV_4143-1_0_4_node_3 | 0.4 | n |  | TRUE
7 | bus_LV_4143-1_0_4_node_70 | 0.4 | n |  | TRUE
8 | bus_LV_4143-1_0_4_node_69 | 0.4 | n |  | TRUE
9 | bus_LV_4143-1_0_4_node_4 | 0.4 | n |  | TRUE
10 | bus_LV_4143-1_0_4_node_30 | 0.4 | n |  | TRUE
11 | bus_LV_4143-1_0_4_node_28 | 0.4 | n |  | TRUE
12 | bus_LV_4143-1_0_4_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_4143-1_0_4_node_40 | 0.4 | n |  | TRUE
14 | bus_LV_4143-1_0_4_node_39 | 0.4 | n |  | TRUE
15 | bus_LV_4143-1_0_4_node_7 | 0.4 | n |  | TRUE
16 | bus_LV_4143-1_0_4_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_4143-1_0_4_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_4143-1_0_4_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_4143-1_0_4_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_4143-1_0_4_node_34 | 0.4 | n |  | TRUE
21 | bus_LV_4143-1_0_4_node_44 | 0.4 | n |  | TRUE
22 | bus_LV_4143-1_0_4_node_49 | 0.4 | n |  | TRUE
23 | bus_LV_4143-1_0_4_node_53 | 0.4 | n |  | TRUE
24 | bus_LV_4143-1_0_4_node_33 | 0.4 | n |  | TRUE
25 | bus_LV_4143-1_0_4_node_57 | 0.4 | n |  | TRUE
26 | bus_LV_4143-1_0_4_node_27 | 0.4 | n |  | TRUE
27 | bus_LV_4143-1_0_4_node_48 | 0.4 | n |  | TRUE
28 | bus_LV_4143-1_0_4_node_12 | 0.4 | n |  | TRUE
29 | bus_LV_4143-1_0_4_node_13 | 0.4 | n |  | TRUE
30 | bus_LV_4143-1_0_4_node_14 | 0.4 | n |  | TRUE
31 | bus_LV_4143-1_0_4_node_15 | 0.4 | n |  | TRUE
32 | bus_LV_4143-1_0_4_node_16 | 0.4 | n |  | TRUE
33 | bus_LV_4143-1_0_4_node_17 | 0.4 | n |  | TRUE
34 | bus_LV_4143-1_0_4_node_37 | 0.4 | n |  | TRUE
35 | bus_LV_4143-1_0_4_node_38 | 0.4 | n |  | TRUE
36 | bus_LV_4143-1_0_4_node_58 | 0.4 | n |  | TRUE
37 | bus_LV_4143-1_0_4_node_54 | 0.4 | n |  | TRUE
38 | bus_LV_4143-1_0_4_node_51 | 0.4 | n |  | TRUE
39 | bus_LV_4143-1_0_4_node_18 | 0.4 | n |  | TRUE
40 | bus_LV_4143-1_0_4_node_19 | 0.4 | n |  | TRUE
41 | bus_LV_4143-1_0_4_node_20 | 0.4 | n |  | TRUE
42 | bus_LV_4143-1_0_4_node_21 | 0.4 | n |  | TRUE
43 | bus_LV_4143-1_0_4_node_22 | 0.4 | n |  | TRUE
44 | bus_LV_4143-1_0_4_node_23 | 0.4 | n |  | TRUE
45 | bus_LV_4143-1_0_4_node_35 | 0.4 | n |  | TRUE
46 | bus_LV_4143-1_0_4_node_61 | 0.4 | n |  | TRUE
47 | bus_LV_4143-1_0_4_node_42 | 0.4 | n |  | TRUE
48 | bus_LV_4143-1_0_4_node_63 | 0.4 | n |  | TRUE
49 | bus_LV_4143-1_0_4_node_59 | 0.4 | n |  | TRUE
50 | bus_LV_4143-1_0_4_node_52 | 0.4 | n |  | TRUE
51 | bus_LV_4143-1_0_4_node_36 | 0.4 | n |  | TRUE
52 | bus_LV_4143-1_0_4_node_62 | 0.4 | n |  | TRUE
53 | bus_LV_4143-1_0_4_node_41 | 0.4 | n |  | TRUE
54 | bus_LV_4143-1_0_4_node_24 | 0.4 | n |  | TRUE
55 | bus_LV_4143-1_0_4_node_25 | 0.4 | n |  | TRUE
56 | bus_LV_4143-1_0_4_node_26 | 0.4 | n |  | TRUE
57 | bus_LV_4143-1_0_4_node_29 | 0.4 | n |  | TRUE
58 | bus_LV_4143-1_0_4_node_31 | 0.4 | n |  | TRUE
59 | bus_LV_4143-1_0_4_node_32 | 0.4 | n |  | TRUE
60 | bus_LV_4143-1_0_4_node_60 | 0.4 | n |  | TRUE
61 | bus_LV_4143-1_0_4_node_45 | 0.4 | n |  | TRUE
62 | bus_LV_4143-1_0_4_node_55 | 0.4 | n |  | TRUE
63 | bus_LV_4143-1_0_4_node_43 | 0.4 | n |  | TRUE
64 | bus_LV_4143-1_0_4_node_67 | 0.4 | n |  | TRUE
65 | bus_LV_4143-1_0_4_node_66 | 0.4 | n |  | TRUE
66 | bus_LV_4143-1_0_4_node_64 | 0.4 | n |  | TRUE
67 | bus_LV_4143-1_0_4_node_47 | 0.4 | n |  | TRUE
68 | bus_LV_4143-1_0_4_node_56 | 0.4 | n |  | TRUE
69 | bus_LV_4143-1_0_4_node_65 | 0.4 | n |  | TRUE
70 | bus_MV_482_0_node_55 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_4143-1_0_4_load_0 | 0 | 0.00054678 | 0.00013704 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_4143-1_0_4_load_1 | 1 | 0.0057607 | 0.0014438 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_4143-1_0_4_load_2 | 2 | 0.001086 | 0.00027219 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_4143-1_0_4_load_68 | 4 | 0.0072226 | 0.0018102 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_4143-1_0_4_load_3 | 6 | 0.0063661 | 0.0015955 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_4143-1_0_4_load_70 | 7 | 0.013054 | 0.0032716 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_4143-1_0_4_load_69 | 8 | 0.0095228 | 0.0023866 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_4143-1_0_4_load_4 | 9 | 0.00088547 | 0.00022192 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_4143-1_0_4_load_30 | 10 | 0.00066622 | 0.00016697 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_4143-1_0_4_load_28 | 11 | 0.00023466 | 5.8811e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_4143-1_0_4_load_6 | 12 | 0.0053936 | 0.0013518 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_4143-1_0_4_load_40 | 13 | 0.0019154 | 0.00048005 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_4143-1_0_4_load_39 | 14 | 0.0012713 | 0.00031862 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_4143-1_0_4_load_7 | 15 | 0.0014343 | 0.00035946 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_4143-1_0_4_load_9 | 17 | 0.00046162 | 0.00011569 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_4143-1_0_4_load_10 | 18 | 0.00088458 | 0.0002217 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_4143-1_0_4_load_49 | 22 | 0.00066778 | 0.00016736 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_4143-1_0_4_load_53 | 23 | 0.0019175 | 0.00048057 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_4143-1_0_4_load_33 | 24 | 0.0013607 | 0.00034102 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_4143-1_0_4_load_57 | 25 | 0.00020586 | 5.1592e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_4143-1_0_4_load_27 | 26 | 0.00053746 | 0.0001347 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_4143-1_0_4_load_48 | 27 | 0.00054018 | 0.00013538 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_4143-1_0_4_load_12 | 28 | 0.0037148 | 0.00093101 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_4143-1_0_4_load_13 | 29 | 0.00013279 | 3.328e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_4143-1_0_4_load_16 | 32 | 0.0012679 | 0.00031775 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_4143-1_0_4_load_17 | 33 | 0.0015842 | 0.00039704 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_4143-1_0_4_load_38 | 35 | 0.004525 | 0.0011341 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_4143-1_0_4_load_58 | 36 | 0.0015085 | 0.00037806 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_4143-1_0_4_load_54 | 37 | 0.0024122 | 0.00060454 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_4143-1_0_4_load_51 | 38 | 0.0037163 | 0.0009314 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_4143-1_0_4_load_18 | 39 | 0.039983 | 0.010021 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_4143-1_0_4_load_21 | 42 | 0.00076235 | 0.00019106 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_4143-1_0_4_load_35 | 45 | 0.012671 | 0.0031756 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_4143-1_0_4_load_61 | 46 | 0.0010344 | 0.00025925 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_4143-1_0_4_load_42 | 47 | 0.0008559 | 0.00021451 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_4143-1_0_4_load_63 | 48 | 0.0044361 | 0.0011118 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_4143-1_0_4_load_59 | 49 | 0.0083717 | 0.0020982 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_4143-1_0_4_load_52 | 50 | 0.0024541 | 0.00061506 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_4143-1_0_4_load_36 | 51 | 0.0037269 | 0.00093405 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_4143-1_0_4_load_62 | 52 | 0.0016177 | 0.00040543 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_4143-1_0_4_load_24 | 54 | 0.00049591 | 0.00012429 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_4143-1_0_4_load_25 | 55 | 0.00024695 | 6.1892e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_4143-1_0_4_load_26 | 56 | 0.0037183 | 0.00093188 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_4143-1_0_4_load_29 | 57 | 0.00029265 | 7.3344e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_4143-1_0_4_load_31 | 58 | 0.0009895 | 0.00024799 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_4143-1_0_4_load_32 | 59 | 0.00026536 | 6.6505e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_4143-1_0_4_load_60 | 60 | 0.00037018 | 9.2775e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_4143-1_0_4_load_45 | 61 | 0.0032564 | 0.00081612 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_4143-1_0_4_load_55 | 62 | 0.002842 | 0.00071227 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_4143-1_0_4_load_67 | 64 | 0.0019079 | 0.00047816 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_4143-1_0_4_load_66 | 65 | 0.0019163 | 0.00048027 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_4143-1_0_4_load_64 | 66 | 0.0026078 | 0.00065357 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_4143-1_0_4_load_47 | 67 | 0.0003551 | 8.8998e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_4143-1_0_4_load_56 | 68 | 0.0030496 | 0.0007643 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_4143-1_0_4_load_65 | 69 | 0.0017413 | 0.0004364 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 45 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_4143-1_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.19305 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_4143-1_0_4_line_1 | NAYY 4x150 SE | 1 | 2 | 0.051968 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_4143-1_0_4_line_2 | NAYY 4x150 SE | 2 | 3 | 0.0047855 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_4143-1_0_4_line_3 | NAYY 4x150 SE | 3 | 4 | 0.069564 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
4 | LV_4143-1_0_4_line_4 | NAYY 4x150 SE | 3 | 5 | 0.025246 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
5 | LV_4143-1_0_4_line_5 | NAYY 4x150 SE | 4 | 8 | 0.0074827 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_4143-1_0_4_line_6 | NAYY 4x150 SE | 5 | 67 | 0.032327 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
7 | LV_4143-1_0_4_line_7 | NAYY 4x150 SE | 6 | 7 | 0.51796 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_4143-1_0_4_line_8 | NAYY 4x150 SE | 7 | 8 | 0.043063 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_4143-1_0_4_line_9 | NAYY 4x150 SE | 9 | 10 | 0.41899 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_4143-1_0_4_line_10 | NAYY 4x150 SE | 10 | 11 | 0.0092795 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_4143-1_0_4_line_11 | NAYY 4x150 SE | 11 | 57 | 0.0077401 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_4143-1_0_4_line_12 | NAYY 4x150 SE | 12 | 13 | 0.067769 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_4143-1_0_4_line_13 | NAYY 4x150 SE | 13 | 14 | 0.013585 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_4143-1_0_4_line_14 | NAYY 4x150 SE | 14 | 53 | 0.023491 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_4143-1_0_4_line_15 | NAYY 4x150 SE | 15 | 16 | 0.016297 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_4143-1_0_4_line_16 | NAYY 4x150 SE | 15 | 17 | 0.028461 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_4143-1_0_4_line_17 | NAYY 4x150 SE | 16 | 18 | 0.037051 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_4143-1_0_4_line_18 | NAYY 4x150 SE | 16 | 19 | 0.059408 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_4143-1_0_4_line_19 | NAYY 4x150 SE | 18 | 20 | 0.02042 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_4143-1_0_4_line_20 | NAYY 4x150 SE | 19 | 21 | 0.036273 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
21 | LV_4143-1_0_4_line_21 | NAYY 4x150 SE | 19 | 22 | 0.01579 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
22 | LV_4143-1_0_4_line_22 | NAYY 4x150 SE | 20 | 23 | 0.022393 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_4143-1_0_4_line_23 | NAYY 4x150 SE | 20 | 24 | 0.02378 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_4143-1_0_4_line_24 | NAYY 4x150 SE | 21 | 25 | 0.013655 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
25 | LV_4143-1_0_4_line_25 | NAYY 4x150 SE | 21 | 26 | 0.025448 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_4143-1_0_4_line_26 | NAYY 4x150 SE | 22 | 27 | 0.04162 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
27 | LV_4143-1_0_4_line_27 | NAYY 4x150 SE | 23 | 60 | 0.0079171 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_4143-1_0_4_line_28 | NAYY 4x150 SE | 24 | 59 | 0.03088 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_4143-1_0_4_line_29 | NAYY 4x150 SE | 25 | 34 | 0.042509 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
30 | LV_4143-1_0_4_line_30 | NAYY 4x150 SE | 26 | 55 | 0.03216 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_4143-1_0_4_line_31 | NAYY 4x150 SE | 27 | 67 | 0.061911 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
32 | LV_4143-1_0_4_line_32 | NAYY 4x150 SE | 28 | 29 | 0.0062092 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_4143-1_0_4_line_33 | NAYY 4x150 SE | 28 | 30 | 0.017073 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_4143-1_0_4_line_34 | NAYY 4x150 SE | 29 | 31 | 0.037756 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_4143-1_0_4_line_35 | NAYY 4x150 SE | 30 | 32 | 0.028323 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_4143-1_0_4_line_36 | NAYY 4x150 SE | 30 | 33 | 0.034712 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_4143-1_0_4_line_37 | NAYY 4x150 SE | 31 | 34 | 0.018487 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
38 | LV_4143-1_0_4_line_38 | NAYY 4x150 SE | 31 | 35 | 0.021086 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
39 | LV_4143-1_0_4_line_39 | NAYY 4x150 SE | 32 | 36 | 0.015372 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_4143-1_0_4_line_40 | NAYY 4x150 SE | 34 | 37 | 0.019786 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_4143-1_0_4_line_41 | NAYY 4x150 SE | 35 | 38 | 0.011063 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
42 | LV_4143-1_0_4_line_42 | NAYY 4x150 SE | 37 | 62 | 0.00053718 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_4143-1_0_4_line_43 | NAYY 4x150 SE | 38 | 50 | 0.0076371 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
44 | LV_4143-1_0_4_line_44 | NAYY 4x150 SE | 39 | 40 | 0.055953 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
45 | LV_4143-1_0_4_line_45 | NAYY 4x150 SE | 39 | 41 | 0.0098295 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
46 | LV_4143-1_0_4_line_46 | NAYY 4x150 SE | 40 | 42 | 0.020623 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
47 | LV_4143-1_0_4_line_47 | NAYY 4x150 SE | 40 | 43 | 0.009406 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_4143-1_0_4_line_48 | NAYY 4x150 SE | 41 | 44 | 0.022531 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
49 | LV_4143-1_0_4_line_49 | NAYY 4x150 SE | 42 | 45 | 0.051515 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
50 | LV_4143-1_0_4_line_50 | NAYY 4x150 SE | 43 | 46 | 0.014549 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_4143-1_0_4_line_51 | NAYY 4x150 SE | 43 | 47 | 0.032434 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_4143-1_0_4_line_52 | NAYY 4x150 SE | 44 | 48 | 0.044613 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_4143-1_0_4_line_53 | NAYY 4x150 SE | 44 | 49 | 0.024811 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_4143-1_0_4_line_54 | NAYY 4x150 SE | 44 | 50 | 0.022989 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
55 | LV_4143-1_0_4_line_55 | NAYY 4x150 SE | 45 | 51 | 0.060797 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_4143-1_0_4_line_56 | NAYY 4x150 SE | 46 | 52 | 0.03405 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_4143-1_0_4_line_57 | NAYY 4x150 SE | 47 | 53 | 0.017137 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_4143-1_0_4_line_58 | NAYY 4x150 SE | 51 | 61 | 0.013395 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_4143-1_0_4_line_59 | NAYY 4x150 SE | 53 | 63 | 0.033262 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_4143-1_0_4_line_60 | NAYY 4x150 SE | 54 | 55 | 0.016182 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_4143-1_0_4_line_61 | NAYY 4x150 SE | 54 | 56 | 0.020181 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_4143-1_0_4_line_62 | NAYY 4x150 SE | 57 | 58 | 0.018324 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_4143-1_0_4_line_63 | NAYY 4x150 SE | 58 | 59 | 0.0083469 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_4143-1_0_4_line_64 | NAYY 4x150 SE | 62 | 68 | 0.030129 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_4143-1_0_4_line_65 | NAYY 4x150 SE | 63 | 64 | 0.031811 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_4143-1_0_4_line_66 | NAYY 4x150 SE | 63 | 65 | 0.015719 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_4143-1_0_4_line_67 | NAYY 4x150 SE | 65 | 66 | 0.028587 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_4143-1_0_4_line_68 | NAYY 4x150 SE | 66 | 69 | 0.0013836 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_4143-1_0_4_trafo_35 | 0.25 MVA 20/0.4 kV | 70 | 45 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2651624.1175 | 1233990.2511 | 2651768.5582 | 1233862.1701
1 | 2651624.1175 | 1233990.2511 | 2651620.0856 | 1233992.1549 | 2651603.2928 | 1233992.4871 | 2651572.5803 | 1233992.6986
2 | 2651569.6708 | 1233996.498 | 2651572.5803 | 1233992.6986 | 2651572.5803 | 1233992.6986
3 | 2651569.6708 | 1233996.498 | 2651603.417 | 1234057.3282
4 | 2651569.6708 | 1233996.498 | 2651558.1497 | 1233997.3542 | 2651545.41 | 1234002.5583
5 | 2651603.417 | 1234057.3282 | 2651607.047 | 1234063.8715
6 | 2651545.41 | 1234002.5583 | 2651519.8614 | 1233982.7522
7 | 2651635.775 | 1234095.2795 | 2651947.0069 | 1234509.3043
8 | 2651635.775 | 1234095.2795 | 2651617.363 | 1234078.142 | 2651613.1299 | 1234074.8364 | 2651607.047 | 1234063.8715
9 | 2651294.2127 | 1233932.5302 | 2650879.2619 | 1233990.5559
10 | 2651294.2127 | 1233932.5302 | 2651298.6299 | 1233924.3695
11 | 2651302.3144 | 1233917.5625 | 2651298.6299 | 1233924.3695
12 | 2651413.357 | 1234242.9248 | 2651436.6732 | 1234306.5564
13 | 2651413.357 | 1234242.9248 | 2651416.8627 | 1234236.6845 | 2651416.8872 | 1234233.8495 | 2651415.9028 | 1234230.3944
14 | 2651396.2424 | 1234217.5384 | 2651415.9028 | 1234230.3944
15 | 2651393.2404 | 1233879.3066 | 2651389.3577 | 1233895.1344
16 | 2651382.577 | 1233922.7757 | 2651389.3577 | 1233895.1344
17 | 2651393.2404 | 1233879.3066 | 2651387.2523 | 1233875.8416 | 2651373.864 | 1233869.3662 | 2651361.5382 | 1233860.3681
18 | 2651393.2404 | 1233879.3066 | 2651422.4992 | 1233885.319 | 2651419.9448 | 1233910.2017 | 2651424.3178 | 1233911.3625
19 | 2651344.4926 | 1233849.1996 | 2651351.4544 | 1233853.0066 | 2651361.5382 | 1233860.3681
20 | 2651415.5094 | 1233941.6391 | 2651419.9448 | 1233910.2017 | 2651424.3178 | 1233911.3625
21 | 2651424.3178 | 1233911.3625 | 2651437.4162 | 1233920.1802
22 | 2651344.4926 | 1233849.1996 | 2651324.7597 | 1233838.6142
23 | 2651344.4926 | 1233849.1996 | 2651332.291 | 1233869.6105
24 | 2651415.5094 | 1233941.6391 | 2651414.6259 | 1233949.2586 | 2651413.304 | 1233955.0954
25 | 2651415.5094 | 1233941.6391 | 2651438.0542 | 1233953.4425
26 | 2651470.9312 | 1233944.82 | 2651450.5686 | 1233929.0342 | 2651437.4162 | 1233920.1802
27 | 2651317.4963 | 1233835.4842 | 2651323.2588 | 1233837.809 | 2651324.7597 | 1233838.6142
28 | 2651315.0104 | 1233894.107 | 2651323.7139 | 1233878.0276 | 2651328.5239 | 1233875.9122 | 2651332.291 | 1233869.6105
29 | 2651403.1513 | 1233996.3673 | 2651408.8254 | 1233974.8693 | 2651413.304 | 1233955.0954
30 | 2651466.5458 | 1233968.3594 | 2651438.0542 | 1233953.4425
31 | 2651519.8614 | 1233982.7522 | 2651470.9312 | 1233944.82
32 | 2651361.9768 | 1234007.2471 | 2651357.7439 | 1234006.437 | 2651355.9253 | 1234006.9851
33 | 2651349.5473 | 1234022.0318 | 2651350.3358 | 1234017.5135 | 2651352.63 | 1234010.4399 | 2651354.4804 | 1234007.4206 | 2651355.9253 | 1234006.9851
34 | 2651399.0596 | 1234014.3435 | 2651361.9768 | 1234007.2471
35 | 2651349.5473 | 1234022.0318 | 2651344.6898 | 1234049.9356
36 | 2651349.5473 | 1234022.0318 | 2651315.0523 | 1234018.1603
37 | 2651399.0596 | 1234014.3435 | 2651399.2775 | 1234011.021 | 2651403.1513 | 1233996.3673
38 | 2651399.0596 | 1234014.3435 | 2651398.111 | 1234028.6222 | 2651398.4377 | 1234035.3906
39 | 2651344.6898 | 1234049.9356 | 2651342.0534 | 1234065.08
40 | 2651403.1513 | 1233996.3673 | 2651421.7443 | 1234003.1347
41 | 2651398.9712 | 1234046.4411 | 2651398.9712 | 1234046.4411 | 2651398.4377 | 1234035.3906
42 | 2651422.2491 | 1234003.3184 | 2651421.7443 | 1234003.1347
43 | 2651398.9712 | 1234046.4411 | 2651400.7304 | 1234053.8728
44 | 2651417.8481 | 1234163.0346 | 2651418.9891 | 1234155.3951 | 2651419.5512 | 1234145.5492 | 2651417.7351 | 1234127.0995 | 2651414.8037 | 1234113.332 | 2651413.4801 | 1234107.7347
45 | 2651411.2182 | 1234098.169 | 2651413.4801 | 1234107.7347
46 | 2651417.8481 | 1234163.0346 | 2651427.6664 | 1234161.2295 | 2651436.3564 | 1234155.0896
47 | 2651416.4808 | 1234172.3399 | 2651417.8481 | 1234163.0346
48 | 2651411.2182 | 1234098.169 | 2651406.0258 | 1234076.2434
49 | 2651436.3564 | 1234155.0896 | 2651462.7596 | 1234110.855
50 | 2651416.4808 | 1234172.3399 | 2651421.9684 | 1234185.8142
51 | 2651416.4808 | 1234172.3399 | 2651404.1855 | 1234202.3528
52 | 2651406.0258 | 1234076.2434 | 2651391.5607 | 1234086.6806 | 2651377.1321 | 1234109.2366
53 | 2651406.0258 | 1234076.2434 | 2651387.3639 | 1234079.1618 | 2651381.4441 | 1234079.3458
54 | 2651406.0258 | 1234076.2434 | 2651400.7304 | 1234053.8728
55 | 2651502.9357 | 1234065.6952 | 2651470.4372 | 1234097.9923 | 2651462.7596 | 1234110.855
56 | 2651441.6574 | 1234213.4173 | 2651423.715 | 1234190.1027 | 2651421.9684 | 1234185.8142
57 | 2651396.2424 | 1234217.5384 | 2651404.1855 | 1234202.3528
58 | 2651502.9357 | 1234065.6952 | 2651504.7967 | 1234063.8457 | 2651512.1845 | 1234056.0072
59 | 2651368.5563 | 1234205.7916 | 2651394.7262 | 1234220.4382 | 2651396.2424 | 1234217.5384
60 | 2651466.5458 | 1233968.3594 | 2651475.6895 | 1233973.1466 | 2651480.2385 | 1233976.8417
61 | 2651495.9025 | 1233989.5654 | 2651480.2385 | 1233976.8417
62 | 2651302.3144 | 1233917.5625 | 2651311.0372 | 1233901.4475
63 | 2651315.0104 | 1233894.107 | 2651311.0372 | 1233901.4475
64 | 2651448.6368 | 1234017.5449 | 2651438.7199 | 1234010.584 | 2651425.7744 | 1234004.6016 | 2651422.2491 | 1234003.3184
65 | 2651340.7365 | 1234190.2191 | 2651368.5563 | 1234205.7916
66 | 2651368.5563 | 1234205.7916 | 2651375.6722 | 1234191.776
67 | 2651388.6139 | 1234166.2859 | 2651375.6722 | 1234191.776
68 | 2651388.6139 | 1234166.2859 | 2651389.2403 | 1234165.0522

## bus_geodata
| x | y | coords
0 | 2651768.5582 | 1233862.1701
1 | 2651624.1175 | 1233990.2511
2 | 2651572.5803 | 1233992.6986
3 | 2651569.6708 | 1233996.498
4 | 2651603.4171 | 1234057.3282
5 | 2651545.41 | 1234002.5583
6 | 2651947.0069 | 1234509.3043
7 | 2651635.775 | 1234095.2795
8 | 2651607.047 | 1234063.8715
9 | 2650879.2619 | 1233990.5559
10 | 2651294.2127 | 1233932.5302
11 | 2651298.6299 | 1233924.3695
12 | 2651436.6732 | 1234306.5564
13 | 2651413.357 | 1234242.9248
14 | 2651415.9028 | 1234230.3944
15 | 2651389.3577 | 1233895.1344
16 | 2651393.2404 | 1233879.3066
17 | 2651382.577 | 1233922.7757
18 | 2651361.5382 | 1233860.3681
19 | 2651424.3178 | 1233911.3625
20 | 2651344.4926 | 1233849.1996
21 | 2651415.5094 | 1233941.6391
22 | 2651437.4162 | 1233920.1802
23 | 2651324.7597 | 1233838.6142
24 | 2651332.291 | 1233869.6105
25 | 2651413.304 | 1233955.0954
26 | 2651438.0542 | 1233953.4425
27 | 2651470.9312 | 1233944.82
28 | 2651355.9253 | 1234006.9851
29 | 2651361.9768 | 1234007.2471
30 | 2651349.5473 | 1234022.0318
31 | 2651399.0596 | 1234014.3435
32 | 2651344.6898 | 1234049.9355
33 | 2651315.0523 | 1234018.1603
34 | 2651403.1513 | 1233996.3673
35 | 2651398.4377 | 1234035.3906
36 | 2651342.0534 | 1234065.08
37 | 2651421.7443 | 1234003.1347
38 | 2651398.9712 | 1234046.4411
39 | 2651413.4801 | 1234107.7347
40 | 2651417.8481 | 1234163.0346
41 | 2651411.2182 | 1234098.169
42 | 2651436.3564 | 1234155.0896
43 | 2651416.4808 | 1234172.3399
44 | 2651406.0258 | 1234076.2434
45 | 2651462.7596 | 1234110.855
46 | 2651421.9684 | 1234185.8142
47 | 2651404.1855 | 1234202.3528
48 | 2651377.1321 | 1234109.2366
49 | 2651381.4441 | 1234079.3458
50 | 2651400.7304 | 1234053.8728
51 | 2651502.9357 | 1234065.6952
52 | 2651441.6574 | 1234213.4173
53 | 2651396.2424 | 1234217.5384
54 | 2651480.2385 | 1233976.8417
55 | 2651466.5458 | 1233968.3594
56 | 2651495.9025 | 1233989.5654
57 | 2651302.3144 | 1233917.5625
58 | 2651311.0372 | 1233901.4475
59 | 2651315.0104 | 1233894.107
60 | 2651317.4963 | 1233835.4842
61 | 2651512.1845 | 1234056.0072
62 | 2651422.2491 | 1234003.3184
63 | 2651368.5563 | 1234205.7916
64 | 2651340.7365 | 1234190.2191
65 | 2651375.6722 | 1234191.776
66 | 2651388.6139 | 1234166.2859
67 | 2651519.8614 | 1233982.7522
68 | 2651448.6368 | 1234017.5449
69 | 2651389.2403 | 1234165.0522
70 | 2651417.8481 | 1234163.0346

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1