## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_4313-10_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_4313-10_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_4313-10_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_4313-10_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_4313-10_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_4313-10_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_4313-10_0_3_node_13 | 0.4 | n |  | TRUE
7 | bus_LV_4313-10_0_3_node_11 | 0.4 | n |  | TRUE
8 | bus_LV_4313-10_0_3_node_33 | 0.4 | n |  | TRUE
9 | bus_LV_4313-10_0_3_node_43 | 0.4 | n |  | TRUE
10 | bus_LV_4313-10_0_3_node_12 | 0.4 | n |  | TRUE
11 | bus_LV_4313-10_0_3_node_24 | 0.4 | n |  | TRUE
12 | bus_LV_4313-10_0_3_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_4313-10_0_3_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_4313-10_0_3_node_6 | 0.4 | n |  | TRUE
15 | bus_LV_4313-10_0_3_node_34 | 0.4 | n |  | TRUE
16 | bus_LV_4313-10_0_3_node_41 | 0.4 | n |  | TRUE
17 | bus_LV_4313-10_0_3_node_7 | 0.4 | n |  | TRUE
18 | bus_LV_4313-10_0_3_node_9 | 0.4 | n |  | TRUE
19 | bus_LV_4313-10_0_3_node_20 | 0.4 | n |  | TRUE
20 | bus_LV_4313-10_0_3_node_21 | 0.4 | n |  | TRUE
21 | bus_LV_4313-10_0_3_node_22 | 0.4 | n |  | TRUE
22 | bus_LV_4313-10_0_3_node_17 | 0.4 | n |  | TRUE
23 | bus_LV_4313-10_0_3_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_4313-10_0_3_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_4313-10_0_3_node_23 | 0.4 | n |  | TRUE
26 | bus_LV_4313-10_0_3_node_18 | 0.4 | n |  | TRUE
27 | bus_LV_4313-10_0_3_node_19 | 0.4 | n |  | TRUE
28 | bus_LV_4313-10_0_3_node_26 | 0.4 | n |  | TRUE
29 | bus_LV_4313-10_0_3_node_28 | 0.4 | n |  | TRUE
30 | bus_LV_4313-10_0_3_node_25 | 0.4 | n |  | TRUE
31 | bus_LV_4313-10_0_3_node_27 | 0.4 | n |  | TRUE
32 | bus_LV_4313-10_0_3_node_30 | 0.4 | n |  | TRUE
33 | bus_LV_4313-10_0_3_node_29 | 0.4 | n |  | TRUE
34 | bus_LV_4313-10_0_3_node_47 | 0.4 | n |  | TRUE
35 | bus_LV_4313-10_0_3_node_70 | 0.4 | n |  | TRUE
36 | bus_LV_4313-10_0_3_node_31 | 0.4 | n |  | TRUE
37 | bus_LV_4313-10_0_3_node_55 | 0.4 | n |  | TRUE
38 | bus_LV_4313-10_0_3_node_46 | 0.4 | n |  | TRUE
39 | bus_LV_4313-10_0_3_node_36 | 0.4 | n |  | TRUE
40 | bus_LV_4313-10_0_3_node_32 | 0.4 | n |  | TRUE
41 | bus_LV_4313-10_0_3_node_35 | 0.4 | n |  | TRUE
42 | bus_LV_4313-10_0_3_node_44 | 0.4 | n |  | TRUE
43 | bus_LV_4313-10_0_3_node_45 | 0.4 | n |  | TRUE
44 | bus_LV_4313-10_0_3_node_37 | 0.4 | n |  | TRUE
45 | bus_LV_4313-10_0_3_node_38 | 0.4 | n |  | TRUE
46 | bus_LV_4313-10_0_3_node_39 | 0.4 | n |  | TRUE
47 | bus_LV_4313-10_0_3_node_42 | 0.4 | n |  | TRUE
48 | bus_LV_4313-10_0_3_node_54 | 0.4 | n |  | TRUE
49 | bus_LV_4313-10_0_3_node_53 | 0.4 | n |  | TRUE
50 | bus_LV_4313-10_0_3_node_58 | 0.4 | n |  | TRUE
51 | bus_LV_4313-10_0_3_node_50 | 0.4 | n |  | TRUE
52 | bus_LV_4313-10_0_3_node_56 | 0.4 | n |  | TRUE
53 | bus_LV_4313-10_0_3_node_48 | 0.4 | n |  | TRUE
54 | bus_LV_4313-10_0_3_node_49 | 0.4 | n |  | TRUE
55 | bus_LV_4313-10_0_3_node_51 | 0.4 | n |  | TRUE
56 | bus_LV_4313-10_0_3_node_52 | 0.4 | n |  | TRUE
57 | bus_LV_4313-10_0_3_node_57 | 0.4 | n |  | TRUE
58 | bus_LV_4313-10_0_3_node_60 | 0.4 | n |  | TRUE
59 | bus_LV_4313-10_0_3_node_67 | 0.4 | n |  | TRUE
60 | bus_LV_4313-10_0_3_node_59 | 0.4 | n |  | TRUE
61 | bus_LV_4313-10_0_3_node_68 | 0.4 | n |  | TRUE
62 | bus_LV_4313-10_0_3_node_62 | 0.4 | n |  | TRUE
63 | bus_LV_4313-10_0_3_node_63 | 0.4 | n |  | TRUE
64 | bus_LV_4313-10_0_3_node_64 | 0.4 | n |  | TRUE
65 | bus_LV_4313-10_0_3_node_65 | 0.4 | n |  | TRUE
66 | bus_LV_4313-10_0_3_node_66 | 0.4 | n |  | TRUE
67 | bus_LV_4313-10_0_3_node_69 | 0.4 | n |  | TRUE
68 | bus_LV_4313-10_0_3_node_74 | 0.4 | n |  | TRUE
69 | bus_LV_4313-10_0_3_node_72 | 0.4 | n |  | TRUE
70 | bus_MV_486_0_node_28 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_4313-10_0_3_load_0 | 0 | 0.0053312 | 0.0013361 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_4313-10_0_3_load_1 | 1 | 0.00025944 | 6.5023e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_4313-10_0_3_load_5 | 5 | 0.00059492 | 0.0001491 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_4313-10_0_3_load_13 | 6 | 0.0050531 | 0.0012664 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_4313-10_0_3_load_33 | 8 | 0.004348 | 0.0010897 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_4313-10_0_3_load_43 | 9 | 0.00043903 | 0.00011003 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_4313-10_0_3_load_24 | 11 | 0.0030357 | 0.00076083 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_4313-10_0_3_load_10 | 13 | 0.0016103 | 0.00040359 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_4313-10_0_3_load_6 | 14 | 0.0022066 | 0.00055303 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_4313-10_0_3_load_41 | 16 | 0.0011427 | 0.00028639 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_4313-10_0_3_load_7 | 17 | 0.0034758 | 0.00087112 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_4313-10_0_3_load_9 | 18 | 0.00076871 | 0.00019266 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_4313-10_0_3_load_20 | 19 | 0.0013272 | 0.00033263 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_4313-10_0_3_load_22 | 21 | 0.0021727 | 0.00054453 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_4313-10_0_3_load_17 | 22 | 0.0033465 | 0.00083871 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_4313-10_0_3_load_16 | 23 | 0.0028243 | 0.00070785 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_4313-10_0_3_load_23 | 25 | 0.0014421 | 0.00036143 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_4313-10_0_3_load_18 | 26 | 0.0021042 | 0.00052736 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_4313-10_0_3_load_19 | 27 | 0.0021352 | 0.00053513 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_4313-10_0_3_load_25 | 30 | 0.00097686 | 0.00024482 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_4313-10_0_3_load_30 | 32 | 0.0029929 | 0.0007501 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_4313-10_0_3_load_47 | 34 | 0.0079244 | 0.001986 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_4313-10_0_3_load_70 | 35 | 0.0042655 | 0.001069 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_4313-10_0_3_load_31 | 36 | 0.0022286 | 0.00055855 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_4313-10_0_3_load_55 | 37 | 0.0048767 | 0.0012222 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_4313-10_0_3_load_46 | 38 | 0.004213 | 0.0010559 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_4313-10_0_3_load_36 | 39 | 0.0061792 | 0.0015487 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_4313-10_0_3_load_32 | 40 | 0.0018907 | 0.00047385 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_4313-10_0_3_load_35 | 41 | 0.033209 | 0.008323 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_4313-10_0_3_load_44 | 42 | 0.00042717 | 0.00010706 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_4313-10_0_3_load_45 | 43 | 0.00061083 | 0.00015309 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_4313-10_0_3_load_37 | 44 | 0.0008407 | 0.0002107 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_4313-10_0_3_load_38 | 45 | 0.00018524 | 4.6425e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_4313-10_0_3_load_39 | 46 | 0.00030911 | 7.7469e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_4313-10_0_3_load_54 | 48 | 0.010953 | 0.002745 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_4313-10_0_3_load_53 | 49 | 0.005622 | 0.001409 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_4313-10_0_3_load_58 | 50 | 0.015027 | 0.0037661 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_4313-10_0_3_load_56 | 52 | 0.0065114 | 0.0016319 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_4313-10_0_3_load_48 | 53 | 0.0094698 | 0.0023733 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_4313-10_0_3_load_49 | 54 | 0.0032772 | 0.00082133 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_4313-10_0_3_load_51 | 55 | 0.012461 | 0.003123 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_4313-10_0_3_load_57 | 57 | 0.0027233 | 0.00068252 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_4313-10_0_3_load_60 | 58 | 0.0046144 | 0.0011565 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_4313-10_0_3_load_67 | 59 | 0.002044 | 0.00051227 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_4313-10_0_3_load_59 | 60 | 0.0046585 | 0.0011675 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_4313-10_0_3_load_68 | 61 | 0.017027 | 0.0042673 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_4313-10_0_3_load_62 | 62 | 0.00217 | 0.00054384 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_4313-10_0_3_load_63 | 63 | 0.0019922 | 0.00049928 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_4313-10_0_3_load_64 | 64 | 0.002464 | 0.00061754 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_4313-10_0_3_load_65 | 65 | 0.0011762 | 0.00029478 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_4313-10_0_3_load_72 | 69 | 0.0017877 | 0.00044804 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 42 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_4313-10_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.021085 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_4313-10_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.055472 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_4313-10_0_3_line_2 | NAYY 4x150 SE | 2 | 3 | 0.018691 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_4313-10_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.022606 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_4313-10_0_3_line_4 | NAYY 4x150 SE | 2 | 5 | 0.028335 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_4313-10_0_3_line_5 | NAYY 4x150 SE | 3 | 6 | 0.013912 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_4313-10_0_3_line_6 | NAYY 4x150 SE | 4 | 7 | 0.006922 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_4313-10_0_3_line_7 | NAYY 4x150 SE | 4 | 8 | 0.0034186 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_4313-10_0_3_line_8 | NAYY 4x150 SE | 5 | 9 | 0.0096632 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_4313-10_0_3_line_9 | NAYY 4x150 SE | 7 | 10 | 0.010691 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_4313-10_0_3_line_10 | NAYY 4x150 SE | 8 | 15 | 0.036251 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_4313-10_0_3_line_11 | NAYY 4x150 SE | 9 | 16 | 0.0082101 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_4313-10_0_3_line_12 | NAYY 4x150 SE | 10 | 11 | 0.075974 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_4313-10_0_3_line_13 | NAYY 4x150 SE | 10 | 12 | 0.039676 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_4313-10_0_3_line_14 | NAYY 4x150 SE | 12 | 13 | 0.0092256 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_4313-10_0_3_line_15 | NAYY 4x150 SE | 12 | 14 | 0.017431 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_4313-10_0_3_line_16 | NAYY 4x150 SE | 13 | 20 | 0.015408 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_4313-10_0_3_line_17 | NAYY 4x150 SE | 15 | 41 | 0.048093 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_4313-10_0_3_line_18 | NAYY 4x150 SE | 15 | 39 | 0.045048 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_4313-10_0_3_line_19 | NAYY 4x150 SE | 16 | 46 | 0.0012833 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_4313-10_0_3_line_20 | NAYY 4x150 SE | 17 | 18 | 0.021686 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_4313-10_0_3_line_21 | NAYY 4x150 SE | 18 | 19 | 0.0012455 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_4313-10_0_3_line_22 | NAYY 4x150 SE | 19 | 20 | 0.029568 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_4313-10_0_3_line_23 | NAYY 4x150 SE | 20 | 21 | 0.023017 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_4313-10_0_3_line_24 | NAYY 4x150 SE | 21 | 24 | 0.046371 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_4313-10_0_3_line_25 | NAYY 4x150 SE | 22 | 23 | 0.023571 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_4313-10_0_3_line_26 | NAYY 4x150 SE | 23 | 26 | 0.026379 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_4313-10_0_3_line_27 | NAYY 4x150 SE | 24 | 25 | 0.13077 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_4313-10_0_3_line_28 | NAYY 4x150 SE | 26 | 27 | 0.023021 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_4313-10_0_3_line_29 | NAYY 4x150 SE | 27 | 28 | 0.010684 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_4313-10_0_3_line_30 | NAYY 4x150 SE | 28 | 29 | 0.006493 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_4313-10_0_3_line_31 | NAYY 4x150 SE | 28 | 30 | 0.018982 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_4313-10_0_3_line_32 | NAYY 4x150 SE | 29 | 33 | 0.009804 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_4313-10_0_3_line_33 | NAYY 4x150 SE | 29 | 34 | 0.043187 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_4313-10_0_3_line_34 | NAYY 4x150 SE | 30 | 31 | 0.016848 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_4313-10_0_3_line_35 | NAYY 4x150 SE | 31 | 32 | 0.01326 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_4313-10_0_3_line_36 | NAYY 4x150 SE | 32 | 36 | 0.025622 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_4313-10_0_3_line_37 | NAYY 4x150 SE | 33 | 35 | 0.018038 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_4313-10_0_3_line_38 | NAYY 4x150 SE | 34 | 37 | 0.0052118 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_4313-10_0_3_line_39 | NAYY 4x150 SE | 36 | 40 | 0.02505 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_4313-10_0_3_line_40 | NAYY 4x150 SE | 37 | 52 | 0.0012804 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_4313-10_0_3_line_41 | NAYY 4x150 SE | 38 | 39 | 0.012629 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_4313-10_0_3_line_42 | NAYY 4x150 SE | 41 | 42 | 0.029221 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_4313-10_0_3_line_43 | NAYY 4x150 SE | 42 | 43 | 0.010603 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
44 | LV_4313-10_0_3_line_44 | NAYY 4x150 SE | 43 | 50 | 0.0066302 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
45 | LV_4313-10_0_3_line_45 | NAYY 4x150 SE | 44 | 45 | 0.012848 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_4313-10_0_3_line_46 | NAYY 4x150 SE | 44 | 46 | 0.017703 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_4313-10_0_3_line_47 | NAYY 4x150 SE | 47 | 48 | 0.011838 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
48 | LV_4313-10_0_3_line_48 | NAYY 4x150 SE | 47 | 49 | 0.0020424 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
49 | LV_4313-10_0_3_line_49 | NAYY 4x150 SE | 48 | 50 | 0.012447 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
50 | LV_4313-10_0_3_line_50 | NAYY 4x150 SE | 49 | 51 | 0.012254 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
51 | LV_4313-10_0_3_line_51 | NAYY 4x150 SE | 51 | 56 | 0.007611 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_4313-10_0_3_line_52 | NAYY 4x150 SE | 51 | 53 | 0.041646 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_4313-10_0_3_line_53 | NAYY 4x150 SE | 52 | 57 | 0.0046302 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_4313-10_0_3_line_54 | NAYY 4x150 SE | 53 | 54 | 0.02665 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_4313-10_0_3_line_55 | NAYY 4x150 SE | 54 | 55 | 0.016162 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_4313-10_0_3_line_56 | NAYY 4x150 SE | 55 | 57 | 0.0090426 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_4313-10_0_3_line_57 | NAYY 4x150 SE | 56 | 58 | 0.0010691 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_4313-10_0_3_line_58 | NAYY 4x150 SE | 56 | 59 | 0.068997 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_4313-10_0_3_line_59 | NAYY 4x150 SE | 58 | 60 | 0.045116 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_4313-10_0_3_line_60 | NAYY 4x150 SE | 59 | 61 | 0.045724 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_4313-10_0_3_line_61 | NAYY 4x150 SE | 61 | 67 | 0.094917 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_4313-10_0_3_line_62 | NAYY 4x150 SE | 62 | 63 | 0.0013189 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_4313-10_0_3_line_63 | NAYY 4x150 SE | 62 | 64 | 0.021756 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_4313-10_0_3_line_64 | NAYY 4x150 SE | 63 | 65 | 0.019489 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_4313-10_0_3_line_65 | NAYY 4x150 SE | 64 | 66 | 0.013749 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_4313-10_0_3_line_66 | NAYY 4x150 SE | 66 | 67 | 0.039286 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_4313-10_0_3_line_67 | NAYY 4x150 SE | 66 | 68 | 0.02029 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_4313-10_0_3_line_68 | NAYY 4x150 SE | 68 | 69 | 0.01233 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_4313-10_0_3_trafo_44 | 0.25 MVA 20/0.4 kV | 70 | 42 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2658798.5625 | 1270965.7257 | 2658800.9652 | 1270961.6049 | 2658809.1266 | 1270947.4786
1 | 2658773.0595 | 1271014.8677 | 2658776.221 | 1271006.3593 | 2658778.7235 | 1271001.3249 | 2658784.0433 | 1270990.6252 | 2658787.7247 | 1270984.3126 | 2658798.5625 | 1270965.7257
2 | 2658755.611 | 1271008.3781 | 2658759.7344 | 1271010.5541 | 2658766.8507 | 1271013.605 | 2658773.0595 | 1271014.8677
3 | 2658769.8055 | 1271037.1967 | 2658770.6072 | 1271026.9413 | 2658773.0595 | 1271014.8677
4 | 2658773.0595 | 1271014.8677 | 2658791.3545 | 1271016.4175 | 2658801.2977 | 1271017.2035
5 | 2658755.611 | 1271008.3781 | 2658750.6609 | 1271004.6149 | 2658746.1577 | 1271000.5337 | 2658745.1506 | 1270999.2699
6 | 2658769.8055 | 1271037.1967 | 2658764.8707 | 1271037.1921 | 2658762.8622 | 1271037.1832
7 | 2658769.8055 | 1271037.1967 | 2658769.8427 | 1271040.6151
8 | 2658801.2977 | 1271017.2035 | 2658810.9309 | 1271017.9649
9 | 2658762.8622 | 1271037.1832 | 2658760.6281 | 1271037.1721 | 2658752.4581 | 1271039.4704
10 | 2658775.2692 | 1271076.2807 | 2658771.4734 | 1271061.5985 | 2658769.947 | 1271050.1969 | 2658769.8427 | 1271040.6151
11 | 2658810.9309 | 1271017.9649 | 2658813.5667 | 1271018.1732 | 2658819.1311 | 1271018.3123
12 | 2658752.4581 | 1271039.4704 | 2658753.1412 | 1271044.1474 | 2658754.0007 | 1271059.8345 | 2658750.8983 | 1271071.4792 | 2658739.9159 | 1271113.5553
13 | 2658718.3376 | 1271036.9293 | 2658727.3842 | 1271035.7516 | 2658734.1025 | 1271034.1839 | 2658739.4072 | 1271032.5576 | 2658744.0752 | 1271029.8909 | 2658752.4581 | 1271039.4704
14 | 2658718.3376 | 1271036.9293 | 2658710.3839 | 1271036.3943 | 2658709.158 | 1271036.1307
15 | 2658718.3376 | 1271036.9293 | 2658718.1614 | 1271041.0307 | 2658712.5702 | 1271053.1262
16 | 2658694.6451 | 1271031.2229 | 2658702.1415 | 1271034.6222 | 2658709.158 | 1271036.1307
17 | 2658775.2692 | 1271076.2807 | 2658783.5095 | 1271074.4724 | 2658790.2217 | 1271074.2724 | 2658796.7093 | 1271076.2384 | 2658806.038 | 1271081.4686 | 2658817.0233 | 1271092.3579
18 | 2658775.2692 | 1271076.2807 | 2658777.5386 | 1271087.8565 | 2658778.7985 | 1271099.5891 | 2658777.9579 | 1271116.0154 | 2658777.1363 | 1271120.9517
19 | 2658820.414 | 1271018.3443 | 2658819.1311 | 1271018.3123
20 | 2658689.941 | 1271071.2011 | 2658681.0015 | 1271065.013 | 2658676.4241 | 1271055.2158
21 | 2658675.8969 | 1271054.0874 | 2658676.4241 | 1271055.2158
22 | 2658694.6451 | 1271031.2229 | 2658682.643 | 1271045.9371 | 2658675.8969 | 1271054.0874
23 | 2658694.6451 | 1271031.2229 | 2658687.269 | 1271027.0576 | 2658676.5453 | 1271017.2302
24 | 2658638.7063 | 1270992.5604 | 2658649.5701 | 1270994.7365 | 2658659.9244 | 1271001.2554 | 2658671.2485 | 1271012.3762 | 2658676.5453 | 1271017.2302
25 | 2658770.7544 | 1271119.2456 | 2658767.7026 | 1271136.6179 | 2658766.5876 | 1271142.4448
26 | 2658761.6297 | 1271168.3537 | 2658766.5876 | 1271142.4448
27 | 2658638.7063 | 1270992.5604 | 2658527.995 | 1271062.1544
28 | 2658757.3028 | 1271190.9648 | 2658761.6297 | 1271168.3537
29 | 2658755.8628 | 1271201.5495 | 2658757.0773 | 1271192.1433 | 2658757.3028 | 1271190.9648
30 | 2658755.8628 | 1271201.5495 | 2658762.2328 | 1271200.2007
31 | 2658755.8628 | 1271201.5495 | 2658736.9487 | 1271203.1522
32 | 2658760.3467 | 1271209.8226 | 2658762.2328 | 1271200.2007
33 | 2658762.2328 | 1271200.2007 | 2658773.0487 | 1271198.0845 | 2658781.0051 | 1271195.3059 | 2658792.5745 | 1271190.7954 | 2658802.7647 | 1271185.8639
34 | 2658720.1609 | 1271204.5747 | 2658736.9487 | 1271203.1522
35 | 2658720.1609 | 1271204.5747 | 2658722.5716 | 1271191.5361
36 | 2658727.2299 | 1271166.3414 | 2658722.5716 | 1271191.5361
37 | 2658760.3467 | 1271209.8226 | 2658756.9487 | 1271227.5373
38 | 2658807.456 | 1271183.5935 | 2658802.7647 | 1271185.8639
39 | 2658731.7842 | 1271141.7091 | 2658727.2299 | 1271166.3414
40 | 2658807.456 | 1271183.5935 | 2658808.6085 | 1271183.0357
41 | 2658775.0087 | 1271133.4 | 2658775.4376 | 1271131.1574 | 2658777.1363 | 1271120.9517
42 | 2658817.0233 | 1271092.3579 | 2658817.2787 | 1271092.6111 | 2658827.9653 | 1271101.9802 | 2658838.1187 | 1271108.9977 | 2658840.1464 | 1271110.0973
43 | 2658849.4669 | 1271115.1514 | 2658840.1464 | 1271110.0973
44 | 2658849.4669 | 1271115.1514 | 2658855.2954 | 1271118.3119
45 | 2658838.1116 | 1271018.7866 | 2658850.9553 | 1271019.1076
46 | 2658838.1116 | 1271018.7866 | 2658820.414 | 1271018.3443
47 | 2658877.2827 | 1271128.5026 | 2658866.2368 | 1271124.2449
48 | 2658877.2827 | 1271128.5026 | 2658879.1851 | 1271129.246
49 | 2658866.2368 | 1271124.2449 | 2658855.2954 | 1271118.3119
50 | 2658890.5985 | 1271133.706 | 2658879.1851 | 1271129.246
51 | 2658890.5985 | 1271133.706 | 2658897.8802 | 1271135.9914
52 | 2658890.5985 | 1271133.706 | 2658889.0751 | 1271138.6167 | 2658886.6598 | 1271143.1961 | 2658879.1926 | 1271148.9594 | 2658859.4702 | 1271158.4669
53 | 2658812.7763 | 1271181.0187 | 2658808.6085 | 1271183.0357
54 | 2658859.4702 | 1271158.4669 | 2658835.4641 | 1271170.0395
55 | 2658820.9158 | 1271177.0796 | 2658835.1695 | 1271170.1815 | 2658835.4641 | 1271170.0395
56 | 2658812.7763 | 1271181.0187 | 2658820.9158 | 1271177.0796
57 | 2658897.8802 | 1271135.9914 | 2658898.9004 | 1271136.3108
58 | 2658897.8802 | 1271135.9914 | 2658895.8828 | 1271145.4342 | 2658883.8747 | 1271203.5524
59 | 2658941.9557 | 1271149.7908 | 2658898.9004 | 1271136.3108
60 | 2658883.8747 | 1271203.5524 | 2658874.6229 | 1271248.3306
61 | 2658928.5001 | 1271287.9566 | 2658923.0881 | 1271287.5356 | 2658895.0633 | 1271284.8987 | 2658867.7761 | 1271281.4686 | 2658874.6229 | 1271248.3306
62 | 2658974.0546 | 1271247.1028 | 2658974.3378 | 1271245.8146
63 | 2658974.0546 | 1271247.1028 | 2658970.7954 | 1271261.9254 | 2658969.4879 | 1271268.3738
64 | 2658978.523 | 1271226.7806 | 2658974.3378 | 1271245.8146
65 | 2658966.7374 | 1271281.8445 | 2658968.4059 | 1271273.7105 | 2658969.4879 | 1271268.3738
66 | 2658928.5001 | 1271287.9566 | 2658935.3479 | 1271283.9441 | 2658952.9563 | 1271282.5965 | 2658966.7374 | 1271281.8445
67 | 2658986.9738 | 1271284.0037 | 2658966.7374 | 1271281.8445
68 | 2658986.9738 | 1271284.0037 | 2658990.6994 | 1271277.0245 | 2658993.5153 | 1271273.6195

## bus_geodata
| x | y | coords
0 | 2658798.5625 | 1270965.7257
1 | 2658809.1266 | 1270947.4786
2 | 2658773.0595 | 1271014.8677
3 | 2658755.611 | 1271008.3781
4 | 2658769.8055 | 1271037.1967
5 | 2658801.2977 | 1271017.2035
6 | 2658745.1506 | 1270999.2699
7 | 2658762.8622 | 1271037.1832
8 | 2658769.8427 | 1271040.6151
9 | 2658810.9309 | 1271017.9649
10 | 2658752.4581 | 1271039.4704
11 | 2658739.9159 | 1271113.5553
12 | 2658718.3376 | 1271036.9293
13 | 2658709.158 | 1271036.1307
14 | 2658712.5702 | 1271053.1262
15 | 2658775.2692 | 1271076.2807
16 | 2658819.1311 | 1271018.3123
17 | 2658689.941 | 1271071.2011
18 | 2658676.4241 | 1271055.2158
19 | 2658675.8969 | 1271054.0874
20 | 2658694.6451 | 1271031.2229
21 | 2658676.5453 | 1271017.2302
22 | 2658770.7544 | 1271119.2456
23 | 2658766.5876 | 1271142.4448
24 | 2658638.7063 | 1270992.5604
25 | 2658527.9949 | 1271062.1544
26 | 2658761.6297 | 1271168.3537
27 | 2658757.3028 | 1271190.9648
28 | 2658755.8628 | 1271201.5495
29 | 2658762.2328 | 1271200.2007
30 | 2658736.9487 | 1271203.1522
31 | 2658720.1609 | 1271204.5747
32 | 2658722.5716 | 1271191.5361
33 | 2658760.3467 | 1271209.8226
34 | 2658802.7647 | 1271185.8639
35 | 2658756.9487 | 1271227.5373
36 | 2658727.2299 | 1271166.3414
37 | 2658807.456 | 1271183.5935
38 | 2658775.0087 | 1271133.4
39 | 2658777.1363 | 1271120.9517
40 | 2658731.7842 | 1271141.7091
41 | 2658817.0233 | 1271092.3579
42 | 2658840.1464 | 1271110.0973
43 | 2658849.4669 | 1271115.1514
44 | 2658838.1116 | 1271018.7866
45 | 2658850.9553 | 1271019.1076
46 | 2658820.414 | 1271018.3443
47 | 2658877.2827 | 1271128.5026
48 | 2658866.2368 | 1271124.2449
49 | 2658879.1851 | 1271129.246
50 | 2658855.2954 | 1271118.3119
51 | 2658890.5985 | 1271133.706
52 | 2658808.6085 | 1271183.0357
53 | 2658859.4702 | 1271158.4669
54 | 2658835.4641 | 1271170.0395
55 | 2658820.9158 | 1271177.0796
56 | 2658897.8802 | 1271135.9914
57 | 2658812.7763 | 1271181.0187
58 | 2658898.9004 | 1271136.3108
59 | 2658883.8747 | 1271203.5524
60 | 2658941.9557 | 1271149.7908
61 | 2658874.6229 | 1271248.3306
62 | 2658974.0546 | 1271247.1028
63 | 2658974.3378 | 1271245.8146
64 | 2658969.4879 | 1271268.3738
65 | 2658978.523 | 1271226.7806
66 | 2658966.7374 | 1271281.8445
67 | 2658928.5001 | 1271287.9566
68 | 2658986.9738 | 1271284.0037
69 | 2658993.5153 | 1271273.6195
70 | 2658877.2827 | 1271128.5026

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1