## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_4701-1_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_4701-1_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_4701-1_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_4701-1_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_4701-1_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_4701-1_0_2_node_130 | 0.4 | n |  | TRUE
6 | bus_LV_4701-1_0_2_node_124 | 0.4 | n |  | TRUE
7 | bus_LV_4701-1_0_2_node_128 | 0.4 | n |  | TRUE
8 | bus_LV_4701-1_0_2_node_104 | 0.4 | n |  | TRUE
9 | bus_LV_4701-1_0_2_node_126 | 0.4 | n |  | TRUE
10 | bus_LV_4701-1_0_2_node_129 | 0.4 | n |  | TRUE
11 | bus_LV_4701-1_0_2_node_95 | 0.4 | n |  | TRUE
12 | bus_LV_4701-1_0_2_node_131 | 0.4 | n |  | TRUE
13 | bus_LV_4701-1_0_2_node_132 | 0.4 | n |  | TRUE
14 | bus_LV_4701-1_0_2_node_134 | 0.4 | n |  | TRUE
15 | bus_LV_4701-1_0_2_node_133 | 0.4 | n |  | TRUE
16 | bus_LV_4701-1_0_2_node_135 | 0.4 | n |  | TRUE
17 | bus_LV_4701-1_0_2_node_136 | 0.4 | n |  | TRUE
18 | bus_LV_4701-1_0_2_node_137 | 0.4 | n |  | TRUE
19 | bus_LV_4701-1_0_2_node_89 | 0.4 | n |  | TRUE
20 | bus_LV_4701-1_0_2_node_139 | 0.4 | n |  | TRUE
21 | bus_LV_4701-1_0_2_node_141 | 0.4 | n |  | TRUE
22 | bus_LV_4701-1_0_2_node_116 | 0.4 | n |  | TRUE
23 | bus_LV_4701-1_0_2_node_138 | 0.4 | n |  | TRUE
24 | bus_LV_4701-1_0_2_node_140 | 0.4 | n |  | TRUE
25 | bus_LV_4701-1_0_2_node_101 | 0.4 | n |  | TRUE
26 | bus_LV_4701-1_0_2_node_143 | 0.4 | n |  | TRUE
27 | bus_LV_4701-1_0_2_node_94 | 0.4 | n |  | TRUE
28 | bus_LV_4701-1_0_2_node_250 | 0.4 | n |  | TRUE
29 | bus_LV_4701-1_0_2_node_249 | 0.4 | n |  | TRUE
30 | bus_LV_4701-1_0_2_node_251 | 0.4 | n |  | TRUE
31 | bus_LV_4701-1_0_2_node_253 | 0.4 | n |  | TRUE
32 | bus_LV_4701-1_0_2_node_125 | 0.4 | n |  | TRUE
33 | bus_LV_4701-1_0_2_node_65 | 0.4 | n |  | TRUE
34 | bus_LV_4701-1_0_2_node_90 | 0.4 | n |  | TRUE
35 | bus_LV_4701-1_0_2_node_80 | 0.4 | n |  | TRUE
36 | bus_LV_4701-1_0_2_node_81 | 0.4 | n |  | TRUE
37 | bus_LV_4701-1_0_2_node_82 | 0.4 | n |  | TRUE
38 | bus_LV_4701-1_0_2_node_84 | 0.4 | n |  | TRUE
39 | bus_LV_4701-1_0_2_node_85 | 0.4 | n |  | TRUE
40 | bus_LV_4701-1_0_2_node_102 | 0.4 | n |  | TRUE
41 | bus_LV_4701-1_0_2_node_109 | 0.4 | n |  | TRUE
42 | bus_LV_4701-1_0_2_node_86 | 0.4 | n |  | TRUE
43 | bus_LV_4701-1_0_2_node_87 | 0.4 | n |  | TRUE
44 | bus_LV_4701-1_0_2_node_88 | 0.4 | n |  | TRUE
45 | bus_LV_4701-1_0_2_node_91 | 0.4 | n |  | TRUE
46 | bus_LV_4701-1_0_2_node_92 | 0.4 | n |  | TRUE
47 | bus_LV_4701-1_0_2_node_93 | 0.4 | n |  | TRUE
48 | bus_LV_4701-1_0_2_node_127 | 0.4 | n |  | TRUE
49 | bus_LV_4701-1_0_2_node_96 | 0.4 | n |  | TRUE
50 | bus_LV_4701-1_0_2_node_97 | 0.4 | n |  | TRUE
51 | bus_LV_4701-1_0_2_node_98 | 0.4 | n |  | TRUE
52 | bus_LV_4701-1_0_2_node_99 | 0.4 | n |  | TRUE
53 | bus_LV_4701-1_0_2_node_100 | 0.4 | n |  | TRUE
54 | bus_LV_4701-1_0_2_node_119 | 0.4 | n |  | TRUE
55 | bus_LV_4701-1_0_2_node_117 | 0.4 | n |  | TRUE
56 | bus_LV_4701-1_0_2_node_103 | 0.4 | n |  | TRUE
57 | bus_LV_4701-1_0_2_node_120 | 0.4 | n |  | TRUE
58 | bus_LV_4701-1_0_2_node_105 | 0.4 | n |  | TRUE
59 | bus_LV_4701-1_0_2_node_106 | 0.4 | n |  | TRUE
60 | bus_LV_4701-1_0_2_node_107 | 0.4 | n |  | TRUE
61 | bus_LV_4701-1_0_2_node_108 | 0.4 | n |  | TRUE
62 | bus_LV_4701-1_0_2_node_111 | 0.4 | n |  | TRUE
63 | bus_LV_4701-1_0_2_node_112 | 0.4 | n |  | TRUE
64 | bus_LV_4701-1_0_2_node_110 | 0.4 | n |  | TRUE
65 | bus_LV_4701-1_0_2_node_118 | 0.4 | n |  | TRUE
66 | bus_LV_4701-1_0_2_node_122 | 0.4 | n |  | TRUE
67 | bus_LV_4701-1_0_2_node_113 | 0.4 | n |  | TRUE
68 | bus_LV_4701-1_0_2_node_114 | 0.4 | n |  | TRUE
69 | bus_LV_4701-1_0_2_node_115 | 0.4 | n |  | TRUE
70 | bus_LV_4701-1_0_2_node_121 | 0.4 | n |  | TRUE
71 | bus_LV_4701-1_0_2_node_123 | 0.4 | n |  | TRUE
72 | bus_MV_441_0_node_262 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_4701-1_0_2_load_0 | 0 | 0.0022687 | 0.00056858 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_4701-1_0_2_load_1 | 1 | 0.0042913 | 0.0010755 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_4701-1_0_2_load_3 | 3 | 0.0024549 | 0.00061527 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_4701-1_0_2_load_130 | 5 | 0.0012866 | 0.00032245 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_4701-1_0_2_load_124 | 6 | 0.0043089 | 0.0010799 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_4701-1_0_2_load_128 | 7 | 0.00027521 | 6.8974e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_4701-1_0_2_load_126 | 9 | 0.00072097 | 0.00018069 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_4701-1_0_2_load_129 | 10 | 0.0013842 | 0.00034692 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_4701-1_0_2_load_95 | 11 | 0.0024057 | 0.00060292 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_4701-1_0_2_load_131 | 12 | 0.00038477 | 9.6433e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_4701-1_0_2_load_132 | 13 | 0.00041267 | 0.00010343 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_4701-1_0_2_load_136 | 17 | 0.00026231 | 6.5742e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_4701-1_0_2_load_137 | 18 | 0.0001803 | 4.5188e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_4701-1_0_2_load_89 | 19 | 0.00020887 | 5.2348e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_4701-1_0_2_load_139 | 20 | 0.00077462 | 0.00019414 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_4701-1_0_2_load_138 | 23 | 0.00030594 | 7.6676e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_4701-1_0_2_load_140 | 24 | 0.0001841 | 4.6139e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_4701-1_0_2_load_143 | 26 | 0.0018203 | 0.0004562 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_4701-1_0_2_load_250 | 28 | 0.00023239 | 5.8242e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_4701-1_0_2_load_249 | 29 | 0.0026601 | 0.00066669 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_4701-1_0_2_load_251 | 30 | 0.0021247 | 0.00053251 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_4701-1_0_2_load_253 | 31 | 0.004517 | 0.0011321 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_4701-1_0_2_load_90 | 34 | 0.00064371 | 0.00016133 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_4701-1_0_2_load_80 | 35 | 0.0047743 | 0.0011966 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_4701-1_0_2_load_81 | 36 | 0.002758 | 0.00069123 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_4701-1_0_2_load_85 | 39 | 0.0046899 | 0.0011754 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_4701-1_0_2_load_102 | 40 | 0.002008 | 0.00050326 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_4701-1_0_2_load_109 | 41 | 0.0016564 | 0.00041513 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_4701-1_0_2_load_86 | 42 | 0.00027669 | 6.9346e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_4701-1_0_2_load_87 | 43 | 0.00057912 | 0.00014514 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_4701-1_0_2_load_88 | 44 | 0.00041287 | 0.00010348 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_4701-1_0_2_load_91 | 45 | 0.00085094 | 0.00021326 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_4701-1_0_2_load_92 | 46 | 0.00059708 | 0.00014964 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_4701-1_0_2_load_127 | 48 | 0.00041541 | 0.00010411 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_4701-1_0_2_load_96 | 49 | 0.0017529 | 0.00043931 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_4701-1_0_2_load_97 | 50 | 0.00053378 | 0.00013378 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_4701-1_0_2_load_98 | 51 | 0.00046008 | 0.00011531 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_4701-1_0_2_load_99 | 52 | 0.00069701 | 0.00017469 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_4701-1_0_2_load_100 | 53 | 0.00041128 | 0.00010308 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_4701-1_0_2_load_119 | 54 | 0.00024842 | 6.226e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_4701-1_0_2_load_117 | 55 | 0.00013049 | 3.2703e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_4701-1_0_2_load_103 | 56 | 0.0005957 | 0.0001493 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_4701-1_0_2_load_120 | 57 | 0.0024204 | 0.0006066 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_4701-1_0_2_load_105 | 58 | 0.00090194 | 0.00022605 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_4701-1_0_2_load_106 | 59 | 0.0017981 | 0.00045065 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_4701-1_0_2_load_107 | 60 | 0.00172 | 0.00043108 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_4701-1_0_2_load_111 | 62 | 0.0017648 | 0.00044229 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_4701-1_0_2_load_112 | 63 | 0.0020903 | 0.00052387 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_4701-1_0_2_load_110 | 64 | 0.0017405 | 0.0004362 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_4701-1_0_2_load_118 | 65 | 0.0015515 | 0.00038883 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_4701-1_0_2_load_122 | 66 | 0.0020872 | 0.00052311 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_4701-1_0_2_load_113 | 67 | 0.00018589 | 4.6588e-05 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_4701-1_0_2_load_114 | 68 | 0.00033 | 8.2705e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_4701-1_0_2_load_115 | 69 | 0.00018595 | 4.6603e-05 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_4701-1_0_2_load_121 | 70 | 0.0020278 | 0.00050822 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_4701-1_0_2_load_123 | 71 | 0.0016016 | 0.00040141 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 38 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_4701-1_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.077289 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_4701-1_0_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.013301 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_4701-1_0_2_line_2 | NAYY 4x150 SE | 1 | 3 | 0.0018346 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_4701-1_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.12723 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_4701-1_0_2_line_4 | NAYY 4x150 SE | 3 | 5 | 0.024893 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_4701-1_0_2_line_5 | NAYY 4x150 SE | 4 | 6 | 0.040407 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_4701-1_0_2_line_6 | NAYY 4x150 SE | 5 | 10 | 0.019032 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_4701-1_0_2_line_7 | NAYY 4x150 SE | 6 | 71 | 0.019508 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_4701-1_0_2_line_8 | NAYY 4x150 SE | 7 | 8 | 0.01652 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_4701-1_0_2_line_9 | NAYY 4x150 SE | 7 | 9 | 0.012684 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_4701-1_0_2_line_10 | NAYY 4x150 SE | 8 | 57 | 0.0066246 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_4701-1_0_2_line_11 | NAYY 4x150 SE | 8 | 56 | 0.025915 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_4701-1_0_2_line_12 | NAYY 4x150 SE | 9 | 48 | 0.041825 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_4701-1_0_2_line_13 | NAYY 4x150 SE | 10 | 11 | 0.011077 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_4701-1_0_2_line_14 | NAYY 4x150 SE | 11 | 47 | 0.012814 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_4701-1_0_2_line_15 | NAYY 4x150 SE | 12 | 13 | 0.027074 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_4701-1_0_2_line_16 | NAYY 4x150 SE | 13 | 14 | 0.01278 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_4701-1_0_2_line_17 | NAYY 4x150 SE | 14 | 18 | 0.013043 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_4701-1_0_2_line_18 | NAYY 4x150 SE | 15 | 16 | 0.027693 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_4701-1_0_2_line_19 | NAYY 4x150 SE | 15 | 17 | 0.046224 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_4701-1_0_2_line_20 | NAYY 4x150 SE | 16 | 19 | 0.024587 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_4701-1_0_2_line_21 | NAYY 4x150 SE | 16 | 20 | 0.022865 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_4701-1_0_2_line_22 | NAYY 4x150 SE | 17 | 21 | 0.035158 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_4701-1_0_2_line_23 | NAYY 4x150 SE | 18 | 22 | 0.012577 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_4701-1_0_2_line_24 | NAYY 4x150 SE | 19 | 43 | 0.01182 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_4701-1_0_2_line_25 | NAYY 4x150 SE | 21 | 23 | 0.036816 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_4701-1_0_2_line_26 | NAYY 4x150 SE | 22 | 23 | 0.10955 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_4701-1_0_2_line_27 | NAYY 4x150 SE | 22 | 68 | 0.0047034 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_4701-1_0_2_line_28 | NAYY 4x150 SE | 24 | 25 | 0.056981 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_4701-1_0_2_line_29 | NAYY 4x150 SE | 25 | 29 | 0.52523 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_4701-1_0_2_line_30 | NAYY 4x150 SE | 25 | 33 | 0.059112 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_4701-1_0_2_line_31 | NAYY 4x150 SE | 26 | 27 | 0.077422 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_4701-1_0_2_line_32 | NAYY 4x150 SE | 27 | 48 | 0.11657 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_4701-1_0_2_line_33 | NAYY 4x150 SE | 27 | 46 | 0.073878 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_4701-1_0_2_line_34 | NAYY 4x150 SE | 28 | 29 | 0.0073991 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_4701-1_0_2_line_35 | NAYY 4x150 SE | 28 | 30 | 0.015608 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_4701-1_0_2_line_36 | NAYY 4x150 SE | 31 | 32 | 0.21497 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_4701-1_0_2_line_37 | NAYY 4x150 SE | 32 | 71 | 0.1604 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_4701-1_0_2_line_38 | NAYY 4x150 SE | 33 | 34 | 0.056988 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_4701-1_0_2_line_39 | NAYY 4x150 SE | 34 | 44 | 0.0082857 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_4701-1_0_2_line_40 | NAYY 4x150 SE | 35 | 36 | 0.038618 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_4701-1_0_2_line_41 | NAYY 4x150 SE | 35 | 37 | 0.02271 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_4701-1_0_2_line_42 | NAYY 4x150 SE | 37 | 38 | 0.008009 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_4701-1_0_2_line_43 | NAYY 4x150 SE | 37 | 39 | 0.017652 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_4701-1_0_2_line_44 | NAYY 4x150 SE | 38 | 40 | 0.059462 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_4701-1_0_2_line_45 | NAYY 4x150 SE | 39 | 41 | 0.022566 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_4701-1_0_2_line_46 | NAYY 4x150 SE | 40 | 56 | 0.0018902 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_4701-1_0_2_line_47 | NAYY 4x150 SE | 41 | 64 | 0.01854 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_4701-1_0_2_line_48 | NAYY 4x150 SE | 42 | 43 | 0.010278 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_4701-1_0_2_line_49 | NAYY 4x150 SE | 42 | 44 | 0.019322 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_4701-1_0_2_line_50 | NAYY 4x150 SE | 45 | 46 | 0.004355 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_4701-1_0_2_line_51 | NAYY 4x150 SE | 45 | 47 | 0.0095984 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_4701-1_0_2_line_52 | NAYY 4x150 SE | 49 | 50 | 0.0016047 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_4701-1_0_2_line_53 | NAYY 4x150 SE | 49 | 51 | 0.00016621 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_4701-1_0_2_line_54 | NAYY 4x150 SE | 50 | 52 | 0.017438 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_4701-1_0_2_line_55 | NAYY 4x150 SE | 51 | 53 | 0.017383 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_4701-1_0_2_line_56 | NAYY 4x150 SE | 52 | 54 | 0.012228 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_4701-1_0_2_line_57 | NAYY 4x150 SE | 53 | 55 | 0.001684 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_4701-1_0_2_line_58 | NAYY 4x150 SE | 54 | 57 | 0.0078921 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_4701-1_0_2_line_59 | NAYY 4x150 SE | 55 | 69 | 0.025214 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_4701-1_0_2_line_60 | NAYY 4x150 SE | 58 | 59 | 0.0094681 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_4701-1_0_2_line_61 | NAYY 4x150 SE | 58 | 60 | 0.0039497 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_4701-1_0_2_line_62 | NAYY 4x150 SE | 59 | 61 | 0.012085 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_4701-1_0_2_line_63 | NAYY 4x150 SE | 61 | 62 | 0.016654 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_4701-1_0_2_line_64 | NAYY 4x150 SE | 61 | 63 | 0.020162 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_4701-1_0_2_line_65 | NAYY 4x150 SE | 62 | 65 | 0.01382 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_4701-1_0_2_line_66 | NAYY 4x150 SE | 63 | 66 | 3.3372e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_4701-1_0_2_line_67 | NAYY 4x150 SE | 64 | 65 | 0.0057439 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_4701-1_0_2_line_68 | NAYY 4x150 SE | 66 | 70 | 0.00091264 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_4701-1_0_2_line_69 | NAYY 4x150 SE | 67 | 68 | 0.007653 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_4701-1_0_2_line_70 | NAYY 4x150 SE | 67 | 69 | 0.010828 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_4701-1_0_2_trafo_84 | 0.25 MVA 20/0.4 kV | 72 | 38 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2724221.249 | 1277202.8344 | 2724218.8013 | 1277198.3172 | 2724210.4651 | 1277181.5147 | 2724201.9928 | 1277157.2577 | 2724194.2507 | 1277130.6607
1 | 2724227.5859 | 1277214.5287 | 2724221.249 | 1277202.8344
2 | 2724193.7379 | 1277128.8993 | 2724194.2507 | 1277130.6607
3 | 2724149.2788 | 1277312.9296 | 2724194.1471 | 1277258.4665 | 2724208.6984 | 1277241.1008 | 2724216.9151 | 1277232.5323 | 2724222.0358 | 1277229.2592 | 2724226.5455 | 1277221.8026 | 2724227.5859 | 1277214.5287
4 | 2724186.7807 | 1277104.9987 | 2724193.7379 | 1277128.8993
5 | 2724149.2788 | 1277312.9296 | 2724129.1227 | 1277337.3065 | 2724124.1563 | 1277344.5421
6 | 2724181.4614 | 1277086.7251 | 2724186.7807 | 1277104.9987
7 | 2724113.207 | 1277360.6848 | 2724114.1706 | 1277359.0904 | 2724124.1563 | 1277344.5421
8 | 2723958.4629 | 1276991.7127 | 2723970.3794 | 1276980.2715
9 | 2723980.7815 | 1276973.1973 | 2723973.7545 | 1276977.0311 | 2723970.3794 | 1276980.2715
10 | 2723958.4629 | 1276991.7127 | 2723951.9797 | 1276990.3511
11 | 2723958.4629 | 1276991.7127 | 2723977.296 | 1276998.804 | 2723982.2957 | 1277001.7265
12 | 2723980.7815 | 1276973.1973 | 2723980.7815 | 1276973.1973 | 2724018.7028 | 1276970.9699 | 2724022.5116 | 1276971.4436
13 | 2724181.4614 | 1277086.7251 | 2724179.5461 | 1277080.1453 | 2724177.9038 | 1277076.2534
14 | 2724169.9883 | 1277066.7203 | 2724175.7297 | 1277071.1008 | 2724177.9038 | 1277076.2534
15 | 2723808.1266 | 1276936.1735 | 2723808.4305 | 1276943.4391 | 2723810.4882 | 1276951.0562 | 2723815.4727 | 1276961.8756
16 | 2723820.8202 | 1276973.4832 | 2723815.4727 | 1276961.8756
17 | 2723820.8202 | 1276973.4832 | 2723833.8122 | 1276974.6337
18 | 2723776.0016 | 1276821.9214 | 2723767.7155 | 1276795.4892
19 | 2723776.0016 | 1276821.9214 | 2723821.8655 | 1276827.6793
20 | 2723767.7155 | 1276795.4892 | 2723767.356 | 1276794.3472 | 2723762.945 | 1276780.2859 | 2723760.4857 | 1276772.4491 | 2723760.2435 | 1276772.0825
21 | 2723767.7155 | 1276795.4892 | 2723790.5455 | 1276794.2197
22 | 2723856.7494 | 1276832.0587 | 2723821.8655 | 1276827.6793
23 | 2723846.3406 | 1276975.7431 | 2723833.8122 | 1276974.6337
24 | 2723753.7274 | 1276762.2207 | 2723760.2435 | 1276772.0825
25 | 2723856.7494 | 1276832.0587 | 2723853.3095 | 1276868.7136
26 | 2723846.3406 | 1276975.7431 | 2723842.1058 | 1276971.9173 | 2723843.3326 | 1276964.3358 | 2723845.069 | 1276953.2507 | 2723846.986 | 1276933.9281 | 2723850.7922 | 1276895.5383 | 2723853.3095 | 1276868.7136
27 | 2723846.3406 | 1276975.7431 | 2723851.032 | 1276976.0792
28 | 2723823.6629 | 1276679.9424 | 2723822.3314 | 1276689.6458 | 2723814.9654 | 1276719.6308 | 2723809.9091 | 1276727.3431 | 2723810.4259 | 1276734.4122
29 | 2723823.6629 | 1276679.9424 | 2724276.4766 | 1276413.8058
30 | 2723823.6629 | 1276679.9424 | 2723764.6825 | 1276673.8882
31 | 2724138.1855 | 1276985.8299 | 2724215.2284 | 1276993.4829
32 | 2724138.1855 | 1276985.8299 | 2724022.5116 | 1276971.4436
33 | 2724138.1855 | 1276985.8299 | 2724137.6586 | 1276993.7152 | 2724139.9212 | 1277001.5813 | 2724164.1405 | 1277054.0514
34 | 2724276.4766 | 1276413.8058 | 2724281.8127 | 1276415.5788 | 2724283.5825 | 1276415.7295
35 | 2724299.134 | 1276417.0542 | 2724283.5825 | 1276415.7295
36 | 2724028.0634 | 1277496.4881 | 2723834.0529 | 1277403.9027
37 | 2724028.0634 | 1277496.4881 | 2724040.2098 | 1277480.8286 | 2724058.6621 | 1277450.9326 | 2724113.207 | 1277360.6848
38 | 2723764.6825 | 1276673.8882 | 2723760.6896 | 1276715.1101 | 2723759.6679 | 1276725.0982 | 2723756.7648 | 1276729.8084
39 | 2723756.7648 | 1276729.8084 | 2723750.8784 | 1276735.6396
40 | 2724003.686 | 1277080.5694 | 2723994.2906 | 1277108.3094 | 2723990.4695 | 1277116.8208
41 | 2724009.0706 | 1277058.6173 | 2724008.3726 | 1277065.7094 | 2724005.4962 | 1277075.2246 | 2724003.686 | 1277080.5694
42 | 2724009.0706 | 1277058.6173 | 2724014.4358 | 1277052.6578
43 | 2724009.0706 | 1277058.6173 | 2723991.4197 | 1277058.85
44 | 2724014.4358 | 1277052.6578 | 2724011.0942 | 1277046.0479 | 2724004.2525 | 1277031.7795 | 2723989.6313 | 1277006.0144 | 2723983.9276 | 1277002.6804
45 | 2723991.4197 | 1277058.85 | 2723985.6692 | 1277058.9258 | 2723968.8605 | 1277058.4632
46 | 2723983.9276 | 1277002.6804 | 2723982.2957 | 1277001.7265
47 | 2723968.8605 | 1277058.4632 | 2723954.8421 | 1277058.0774 | 2723950.3263 | 1277058.0799
48 | 2723748.846 | 1276753.2416 | 2723750.3065 | 1276757.0432 | 2723753.7274 | 1276762.2207
49 | 2723748.846 | 1276753.2416 | 2723746.6495 | 1276747.5242 | 2723747.9585 | 1276738.532 | 2723750.8784 | 1276735.6396
50 | 2724165.9657 | 1277058.0055 | 2724164.1405 | 1277054.0514
51 | 2724169.9883 | 1277066.7203 | 2724165.9657 | 1277058.0055
52 | 2723913.4986 | 1276983.1235 | 2723915.082 | 1276983.3842
53 | 2723913.3346 | 1276983.0964 | 2723913.4986 | 1276983.1235
54 | 2723932.2885 | 1276986.2178 | 2723915.082 | 1276983.3842
55 | 2723896.1827 | 1276980.2718 | 2723913.3346 | 1276983.0964
56 | 2723944.256 | 1276988.7291 | 2723932.3338 | 1276986.2253 | 2723932.2885 | 1276986.2178
57 | 2723896.1827 | 1276980.2718 | 2723894.521 | 1276979.9982
58 | 2723951.9797 | 1276990.3511 | 2723944.256 | 1276988.7291
59 | 2723869.4659 | 1276977.3997 | 2723885.8846 | 1276978.5759 | 2723894.521 | 1276979.9982
60 | 2723959.0853 | 1277088.7216 | 2723949.6408 | 1277088.0524
61 | 2723963.0251 | 1277089.0008 | 2723959.0853 | 1277088.7216
62 | 2723937.5858 | 1277087.1981 | 2723949.6408 | 1277088.0524
63 | 2723937.5858 | 1277087.1981 | 2723939.451 | 1277070.6484
64 | 2723937.5858 | 1277087.1981 | 2723935.3204 | 1277107.2324
65 | 2723939.451 | 1277070.6484 | 2723939.9517 | 1277066.2056 | 2723942.2951 | 1277060.2269 | 2723944.7433 | 1277058.6215
66 | 2723935.3166 | 1277107.2656 | 2723935.3204 | 1277107.2324
67 | 2723950.3263 | 1277058.0799 | 2723945.5652 | 1277058.0825 | 2723944.7433 | 1277058.6215
68 | 2723935.2141 | 1277108.1724 | 2723935.3166 | 1277107.2656
69 | 2723858.6655 | 1276976.626 | 2723851.032 | 1276976.0792
70 | 2723869.4659 | 1276977.3997 | 2723858.6655 | 1276976.626

## bus_geodata
| x | y | coords
0 | 2724221.249 | 1277202.8344
1 | 2724194.2507 | 1277130.6607
2 | 2724227.5859 | 1277214.5287
3 | 2724193.7379 | 1277128.8993
4 | 2724149.2788 | 1277312.9296
5 | 2724186.7807 | 1277104.9987
6 | 2724124.1563 | 1277344.5421
7 | 2723970.3794 | 1276980.2715
8 | 2723958.4629 | 1276991.7127
9 | 2723980.7815 | 1276973.1973
10 | 2724181.4614 | 1277086.7251
11 | 2724177.9038 | 1277076.2534
12 | 2723808.1266 | 1276936.1735
13 | 2723815.4727 | 1276961.8756
14 | 2723820.8202 | 1276973.4832
15 | 2723776.0016 | 1276821.9214
16 | 2723767.7155 | 1276795.4892
17 | 2723821.8655 | 1276827.6793
18 | 2723833.8122 | 1276974.6337
19 | 2723760.2435 | 1276772.0825
20 | 2723790.5455 | 1276794.2197
21 | 2723856.7494 | 1276832.0587
22 | 2723846.3406 | 1276975.7431
23 | 2723853.3095 | 1276868.7136
24 | 2723810.4259 | 1276734.4122
25 | 2723823.6629 | 1276679.9424
26 | 2724215.2284 | 1276993.4829
27 | 2724138.1855 | 1276985.8299
28 | 2724283.5825 | 1276415.7295
29 | 2724276.4766 | 1276413.8058
30 | 2724299.134 | 1276417.0542
31 | 2723834.0529 | 1277403.9027
32 | 2724028.0634 | 1277496.4881
33 | 2723764.6825 | 1276673.8882
34 | 2723756.7648 | 1276729.8084
35 | 2724003.686 | 1277080.5694
36 | 2723990.4695 | 1277116.8208
37 | 2724009.0706 | 1277058.6173
38 | 2724014.4358 | 1277052.6578
39 | 2723991.4197 | 1277058.85
40 | 2723983.9276 | 1277002.6804
41 | 2723968.8605 | 1277058.4632
42 | 2723748.846 | 1276753.2416
43 | 2723753.7274 | 1276762.2207
44 | 2723750.8784 | 1276735.6396
45 | 2724165.9657 | 1277058.0055
46 | 2724164.1405 | 1277054.0514
47 | 2724169.9883 | 1277066.7203
48 | 2724022.5116 | 1276971.4436
49 | 2723913.4986 | 1276983.1235
50 | 2723915.082 | 1276983.3842
51 | 2723913.3346 | 1276983.0964
52 | 2723932.2885 | 1276986.2178
53 | 2723896.1827 | 1276980.2718
54 | 2723944.256 | 1276988.7291
55 | 2723894.521 | 1276979.9982
56 | 2723982.2957 | 1277001.7265
57 | 2723951.9797 | 1276990.3511
58 | 2723959.0853 | 1277088.7216
59 | 2723949.6408 | 1277088.0524
60 | 2723963.0251 | 1277089.0008
61 | 2723937.5858 | 1277087.1981
62 | 2723939.451 | 1277070.6484
63 | 2723935.3204 | 1277107.2324
64 | 2723950.3263 | 1277058.0799
65 | 2723944.7433 | 1277058.6215
66 | 2723935.3166 | 1277107.2656
67 | 2723858.6655 | 1276976.626
68 | 2723851.032 | 1276976.0792
69 | 2723869.4659 | 1276977.3997
70 | 2723935.2141 | 1277108.1724
71 | 2724113.207 | 1277360.6848
72 | 2724009.0706 | 1277058.6173

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1