## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_4911-8_2_2_node_128 | 0.4 | n |  | TRUE
1 | bus_LV_4911-8_2_2_node_121 | 0.4 | n |  | TRUE
2 | bus_LV_4911-8_2_2_node_119 | 0.4 | n |  | TRUE
3 | bus_LV_4911-8_2_2_node_129 | 0.4 | n |  | TRUE
4 | bus_LV_4911-8_2_2_node_118 | 0.4 | n |  | TRUE
5 | bus_LV_4911-8_2_2_node_130 | 0.4 | n |  | TRUE
6 | bus_LV_4911-8_2_2_node_120 | 0.4 | n |  | TRUE
7 | bus_LV_4911-8_2_2_node_131 | 0.4 | n |  | TRUE
8 | bus_LV_4911-8_2_2_node_132 | 0.4 | n |  | TRUE
9 | bus_LV_4911-8_2_2_node_133 | 0.4 | n |  | TRUE
10 | bus_LV_4911-8_2_2_node_99 | 0.4 | n |  | TRUE
11 | bus_LV_4911-8_2_2_node_134 | 0.4 | n |  | TRUE
12 | bus_LV_4911-8_2_2_node_122 | 0.4 | n |  | TRUE
13 | bus_LV_4911-8_2_2_node_138 | 0.4 | n |  | TRUE
14 | bus_LV_4911-8_2_2_node_135 | 0.4 | n |  | TRUE
15 | bus_LV_4911-8_2_2_node_136 | 0.4 | n |  | TRUE
16 | bus_LV_4911-8_2_2_node_137 | 0.4 | n |  | TRUE
17 | bus_LV_4911-8_2_2_node_139 | 0.4 | n |  | TRUE
18 | bus_LV_4911-8_2_2_node_146 | 0.4 | n |  | TRUE
19 | bus_LV_4911-8_2_2_node_148 | 0.4 | n |  | TRUE
20 | bus_LV_4911-8_2_2_node_147 | 0.4 | n |  | TRUE
21 | bus_LV_4911-8_2_2_node_140 | 0.4 | n |  | TRUE
22 | bus_LV_4911-8_2_2_node_141 | 0.4 | n |  | TRUE
23 | bus_LV_4911-8_2_2_node_142 | 0.4 | n |  | TRUE
24 | bus_LV_4911-8_2_2_node_143 | 0.4 | n |  | TRUE
25 | bus_LV_4911-8_2_2_node_144 | 0.4 | n |  | TRUE
26 | bus_LV_4911-8_2_2_node_145 | 0.4 | n |  | TRUE
27 | bus_LV_4911-8_2_2_node_149 | 0.4 | n |  | TRUE
28 | bus_LV_4911-8_2_2_node_86 | 0.4 | n |  | TRUE
29 | bus_LV_4911-8_2_2_node_87 | 0.4 | n |  | TRUE
30 | bus_LV_4911-8_2_2_node_88 | 0.4 | n |  | TRUE
31 | bus_LV_4911-8_2_2_node_89 | 0.4 | n |  | TRUE
32 | bus_LV_4911-8_2_2_node_90 | 0.4 | n |  | TRUE
33 | bus_LV_4911-8_2_2_node_91 | 0.4 | n |  | TRUE
34 | bus_LV_4911-8_2_2_node_92 | 0.4 | n |  | TRUE
35 | bus_LV_4911-8_2_2_node_93 | 0.4 | n |  | TRUE
36 | bus_LV_4911-8_2_2_node_125 | 0.4 | n |  | TRUE
37 | bus_LV_4911-8_2_2_node_94 | 0.4 | n |  | TRUE
38 | bus_LV_4911-8_2_2_node_95 | 0.4 | n |  | TRUE
39 | bus_LV_4911-8_2_2_node_96 | 0.4 | n |  | TRUE
40 | bus_LV_4911-8_2_2_node_100 | 0.4 | n |  | TRUE
41 | bus_LV_4911-8_2_2_node_101 | 0.4 | n |  | TRUE
42 | bus_LV_4911-8_2_2_node_98 | 0.4 | n |  | TRUE
43 | bus_LV_4911-8_2_2_node_116 | 0.4 | n |  | TRUE
44 | bus_LV_4911-8_2_2_node_113 | 0.4 | n |  | TRUE
45 | bus_LV_4911-8_2_2_node_102 | 0.4 | n |  | TRUE
46 | bus_LV_4911-8_2_2_node_112 | 0.4 | n |  | TRUE
47 | bus_LV_4911-8_2_2_node_124 | 0.4 | n |  | TRUE
48 | bus_LV_4911-8_2_2_node_103 | 0.4 | n |  | TRUE
49 | bus_LV_4911-8_2_2_node_105 | 0.4 | n |  | TRUE
50 | bus_LV_4911-8_2_2_node_107 | 0.4 | n |  | TRUE
51 | bus_LV_4911-8_2_2_node_108 | 0.4 | n |  | TRUE
52 | bus_LV_4911-8_2_2_node_109 | 0.4 | n |  | TRUE
53 | bus_LV_4911-8_2_2_node_110 | 0.4 | n |  | TRUE
54 | bus_LV_4911-8_2_2_node_111 | 0.4 | n |  | TRUE
55 | bus_LV_4911-8_2_2_node_114 | 0.4 | n |  | TRUE
56 | bus_LV_4911-8_2_2_node_115 | 0.4 | n |  | TRUE
57 | bus_LV_4911-8_2_2_node_117 | 0.4 | n |  | TRUE
58 | bus_LV_4911-8_2_2_node_123 | 0.4 | n |  | TRUE
59 | bus_LV_4911-8_2_2_node_127 | 0.4 | n |  | TRUE
60 | bus_LV_4911-8_2_2_node_126 | 0.4 | n |  | TRUE
61 | bus_MV_0_node_113 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_4911-8_2_2_load_128 | 0 | 0.00055987 | 0.00014032 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_4911-8_2_2_load_129 | 3 | 0.00038261 | 9.5891e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_4911-8_2_2_load_130 | 5 | 0.0018705 | 0.00046878 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_4911-8_2_2_load_131 | 7 | 0.00066838 | 0.00016751 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_4911-8_2_2_load_132 | 8 | 0.00095963 | 0.00024051 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_4911-8_2_2_load_133 | 9 | 0.00043732 | 0.0001096 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_4911-8_2_2_load_134 | 11 | 0.0011758 | 0.00029469 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_4911-8_2_2_load_135 | 14 | 0.003651 | 0.00091503 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_4911-8_2_2_load_136 | 15 | 0.00080362 | 0.00020141 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_4911-8_2_2_load_146 | 18 | 0.00041471 | 0.00010394 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_4911-8_2_2_load_147 | 20 | 0.0014429 | 0.00036162 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_4911-8_2_2_load_140 | 21 | 0.00030946 | 7.7558e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_4911-8_2_2_load_142 | 23 | 0.00091299 | 0.00022882 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_4911-8_2_2_load_144 | 25 | 0.00053583 | 0.00013429 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_4911-8_2_2_load_145 | 26 | 0.0009558 | 0.00023955 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_4911-8_2_2_load_149 | 27 | 0.0008396 | 0.00021042 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_4911-8_2_2_load_86 | 28 | 0.0033158 | 0.00083102 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_4911-8_2_2_load_87 | 29 | 0.00072768 | 0.00018237 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_4911-8_2_2_load_89 | 31 | 0.00027728 | 6.9494e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_4911-8_2_2_load_91 | 33 | 0.0035622 | 0.00089276 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_4911-8_2_2_load_92 | 34 | 0.00063704 | 0.00015966 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_4911-8_2_2_load_93 | 35 | 0.00028516 | 7.1467e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_4911-8_2_2_load_125 | 36 | 0.00099579 | 0.00024957 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_4911-8_2_2_load_94 | 37 | 0.0015243 | 0.00038203 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_4911-8_2_2_load_101 | 41 | 0.00040838 | 0.00010235 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_4911-8_2_2_load_113 | 44 | 0.00057454 | 0.00014399 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_4911-8_2_2_load_102 | 45 | 0.00064765 | 0.00016232 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_4911-8_2_2_load_112 | 46 | 0.0010444 | 0.00026175 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_4911-8_2_2_load_124 | 47 | 0.00060374 | 0.00015131 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_4911-8_2_2_load_103 | 48 | 0.0029153 | 0.00073064 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_4911-8_2_2_load_107 | 50 | 0.0040575 | 0.0010169 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_4911-8_2_2_load_108 | 51 | 0.00084321 | 0.00021133 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_4911-8_2_2_load_109 | 52 | 0.0020477 | 0.0005132 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_4911-8_2_2_load_110 | 53 | 0.00086353 | 0.00021642 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_4911-8_2_2_load_111 | 54 | 0.0021473 | 0.00053816 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_4911-8_2_2_load_114 | 55 | 0.00012574 | 3.1513e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_4911-8_2_2_load_123 | 58 | 0.00074069 | 0.00018563 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_4911-8_2_2_load_126 | 60 | 0.0012914 | 0.00032365 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 44 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_4911-8_2_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0096976 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_4911-8_2_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.0062088 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_4911-8_2_2_line_2 | NAYY 4x150 SE | 1 | 53 | 0.020399 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_4911-8_2_2_line_3 | NAYY 4x150 SE | 2 | 6 | 0.025938 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_4911-8_2_2_line_4 | NAYY 4x150 SE | 2 | 56 | 0.021541 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_4911-8_2_2_line_5 | NAYY 4x150 SE | 3 | 4 | 0.004208 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_4911-8_2_2_line_6 | NAYY 4x150 SE | 4 | 6 | 0.00523 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_4911-8_2_2_line_7 | NAYY 4x150 SE | 4 | 59 | 0.00849 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_4911-8_2_2_line_8 | NAYY 4x150 SE | 5 | 6 | 0.003741 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_4911-8_2_2_line_9 | NAYY 4x150 SE | 7 | 8 | 0.0048792 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_4911-8_2_2_line_10 | NAYY 4x150 SE | 7 | 9 | 0.010657 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_4911-8_2_2_line_11 | NAYY 4x150 SE | 8 | 10 | 0.018505 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_4911-8_2_2_line_12 | NAYY 4x150 SE | 10 | 45 | 0.039158 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_4911-8_2_2_line_13 | NAYY 4x150 SE | 10 | 40 | 0.020293 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_4911-8_2_2_line_14 | NAYY 4x150 SE | 11 | 12 | 0.016316 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_4911-8_2_2_line_15 | NAYY 4x150 SE | 11 | 13 | 0.031199 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_4911-8_2_2_line_16 | NAYY 4x150 SE | 12 | 43 | 0.1597 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_4911-8_2_2_line_17 | NAYY 4x150 SE | 13 | 18 | 0.01876 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_4911-8_2_2_line_18 | NAYY 4x150 SE | 13 | 16 | 0.07026 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_4911-8_2_2_line_19 | NAYY 4x150 SE | 14 | 15 | 0.032787 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_4911-8_2_2_line_20 | NAYY 4x150 SE | 15 | 16 | 0.017823 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_4911-8_2_2_line_21 | NAYY 4x150 SE | 16 | 17 | 0.021067 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_4911-8_2_2_line_22 | NAYY 4x150 SE | 17 | 19 | 0.02924 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_4911-8_2_2_line_23 | NAYY 4x150 SE | 17 | 20 | 0.026882 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_4911-8_2_2_line_24 | NAYY 4x150 SE | 18 | 26 | 0.017908 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_4911-8_2_2_line_25 | NAYY 4x150 SE | 19 | 27 | 0.02955 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_4911-8_2_2_line_26 | NAYY 4x150 SE | 21 | 22 | 0.027439 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_4911-8_2_2_line_27 | NAYY 4x150 SE | 21 | 23 | 0.011328 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_4911-8_2_2_line_28 | NAYY 4x150 SE | 22 | 24 | 0.033378 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_4911-8_2_2_line_29 | NAYY 4x150 SE | 24 | 25 | 0.022546 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_4911-8_2_2_line_30 | NAYY 4x150 SE | 24 | 26 | 0.018007 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_4911-8_2_2_line_31 | NAYY 4x150 SE | 28 | 29 | 0.042148 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_4911-8_2_2_line_32 | NAYY 4x150 SE | 28 | 30 | 0.037833 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_4911-8_2_2_line_33 | NAYY 4x150 SE | 29 | 31 | 6.8427e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_4911-8_2_2_line_34 | NAYY 4x150 SE | 30 | 32 | 0.013222 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_4911-8_2_2_line_35 | NAYY 4x150 SE | 31 | 33 | 0.015139 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_4911-8_2_2_line_36 | NAYY 4x150 SE | 32 | 34 | 0.037641 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_4911-8_2_2_line_37 | NAYY 4x150 SE | 32 | 35 | 0.061975 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_4911-8_2_2_line_38 | NAYY 4x150 SE | 35 | 36 | 0.026439 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_4911-8_2_2_line_39 | NAYY 4x150 SE | 36 | 60 | 0.061007 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_4911-8_2_2_line_40 | NAYY 4x150 SE | 37 | 38 | 0.32973 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_4911-8_2_2_line_41 | NAYY 4x150 SE | 37 | 39 | 0.0061893 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_4911-8_2_2_line_42 | NAYY 4x150 SE | 38 | 40 | 0.041323 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_4911-8_2_2_line_43 | NAYY 4x150 SE | 39 | 41 | 0.031309 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_4911-8_2_2_line_44 | NAYY 4x150 SE | 40 | 46 | 0.040775 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_4911-8_2_2_line_45 | NAYY 4x150 SE | 41 | 47 | 0.012102 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_4911-8_2_2_line_46 | NAYY 4x150 SE | 42 | 43 | 0.022016 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_4911-8_2_2_line_47 | NAYY 4x150 SE | 42 | 44 | 0.16668 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_4911-8_2_2_line_48 | NAYY 4x150 SE | 43 | 58 | 0.43067 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_4911-8_2_2_line_49 | NAYY 4x150 SE | 44 | 55 | 0.0037479 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_4911-8_2_2_line_50 | NAYY 4x150 SE | 47 | 57 | 0.0033208 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_4911-8_2_2_line_51 | NAYY 4x150 SE | 48 | 49 | 0.0042531 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_4911-8_2_2_line_52 | NAYY 4x150 SE | 49 | 50 | 0.027075 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_4911-8_2_2_line_53 | NAYY 4x150 SE | 49 | 51 | 0.039864 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_4911-8_2_2_line_54 | NAYY 4x150 SE | 50 | 52 | 0.00039555 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_4911-8_2_2_line_55 | NAYY 4x150 SE | 51 | 53 | 0.0033058 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_4911-8_2_2_line_56 | NAYY 4x150 SE | 52 | 54 | 0.012246 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_4911-8_2_2_line_57 | NAYY 4x150 SE | 55 | 56 | 0.025508 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_4911-8_2_2_line_58 | NAYY 4x150 SE | 56 | 57 | 0.041121 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_4911-8_2_2_line_59 | NAYY 4x150 SE | 59 | 60 | 0.027328 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_4911-8_2_2_trafo_113 | 0.25 MVA 20/0.4 kV | 61 | 44 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2730584.0158 | 1269093.2683 | 2730588.4833 | 1269092.0992 | 2730593.5497 | 1269091.7317
1 | 2730599.7484 | 1269091.6256 | 2730596.5891 | 1269091.5112 | 2730593.5497 | 1269091.7317
2 | 2730584.0158 | 1269093.2683 | 2730569.6413 | 1269093.0726 | 2730563.6453 | 1269093.6431
3 | 2730599.7484 | 1269091.6256 | 2730598.4108 | 1269093.8982 | 2730597.7222 | 1269096.4409 | 2730597.7394 | 1269099.066 | 2730598.4588 | 1269101.5954 | 2730600.0077 | 1269104.0653 | 2730598.7639 | 1269107.5411 | 2730597.1196 | 1269116.1907
4 | 2730599.7484 | 1269091.6256 | 2730601.7709 | 1269089.7018 | 2730604.2531 | 1269088.4332 | 2730606.6247 | 1269085.3605 | 2730613.4476 | 1269075.3908
5 | 2730601.9211 | 1269118.2988 | 2730605.7831 | 1269119.9969
6 | 2730601.9211 | 1269118.2988 | 2730597.1196 | 1269116.1907
7 | 2730597.4402 | 1269125.5177 | 2730601.9211 | 1269118.2988
8 | 2730597.1196 | 1269116.1907 | 2730593.6823 | 1269114.6911
9 | 2731042.6525 | 1269197.5939 | 2731041.3621 | 1269192.8884 | 2731041.3621 | 1269192.8884
10 | 2731045.471 | 1269207.8715 | 2731042.6525 | 1269197.5939
11 | 2731031.6866 | 1269179.7503 | 2731032.6396 | 1269185.6548 | 2731034.1215 | 1269187.4004 | 2731038.1457 | 1269187.8901 | 2731040.1289 | 1269189.4356 | 2731041.3621 | 1269192.8884
12 | 2731031.6866 | 1269179.7503 | 2731043.976 | 1269176.1972 | 2731068.7988 | 1269167.3112
13 | 2731031.6866 | 1269179.7503 | 2731023.1312 | 1269179.9051 | 2731019.0202 | 1269180.6146 | 2731011.5686 | 1269181.9173
14 | 2730706.837 | 1268709.4545 | 2730710.889 | 1268693.6496
15 | 2730718.6372 | 1268663.4276 | 2730710.889 | 1268693.6496
16 | 2730667.1618 | 1268864.1677 | 2730706.837 | 1268709.4545
17 | 2730718.6372 | 1268663.4276 | 2730705.5873 | 1268658.4454 | 2730701.257 | 1268656.3956
18 | 2730718.6372 | 1268663.4276 | 2730736.1279 | 1268595.3725
19 | 2730782.4184 | 1268615.8293 | 2730752.4296 | 1268602.5766
20 | 2730736.1279 | 1268595.3725 | 2730752.4296 | 1268602.5766
21 | 2730741.3756 | 1268574.9694 | 2730736.7209 | 1268593.0724 | 2730736.1279 | 1268595.3725
22 | 2730748.6584 | 1268546.6482 | 2730741.3756 | 1268574.9694
23 | 2730741.3756 | 1268574.9694 | 2730735.7278 | 1268573.3206 | 2730724.7353 | 1268568.2393 | 2730716.9296 | 1268563.9885
24 | 2730701.257 | 1268656.3956 | 2730685.0707 | 1268648.7337
25 | 2730748.6584 | 1268546.6482 | 2730771.7117 | 1268553.7873 | 2730775.6652 | 1268557.4894
26 | 2730641.7726 | 1268621.0766 | 2730646.9836 | 1268594.1366
27 | 2730649.1349 | 1268583.0145 | 2730646.9836 | 1268594.1366
28 | 2730669.5557 | 1268639.6974 | 2730645.6049 | 1268623.4525 | 2730641.7726 | 1268621.0766
29 | 2730659.3011 | 1268659.7896 | 2730669.5557 | 1268639.6974
30 | 2730669.5557 | 1268639.6974 | 2730677.8336 | 1268645.308 | 2730685.0707 | 1268648.7337
31 | 2730582.286 | 1269306.6407 | 2730610.5192 | 1269305.7107 | 2730624.1871 | 1269303.1853
32 | 2730544.474 | 1269307.8864 | 2730582.286 | 1269306.6407
33 | 2730624.1871 | 1269303.1853 | 2730624.2544 | 1269303.1729
34 | 2730544.474 | 1269307.8864 | 2730548.2922 | 1269295.2254
35 | 2730624.2544 | 1269303.1729 | 2730638.4717 | 1269300.546 | 2730639.1415 | 1269300.4224
36 | 2730548.2922 | 1269295.2254 | 2730510.6545 | 1269294.7177
37 | 2730548.2922 | 1269295.2254 | 2730566.6717 | 1269236.0387
38 | 2730574.4099 | 1269210.7577 | 2730572.2514 | 1269218.0708 | 2730566.6717 | 1269236.0387
39 | 2730574.4099 | 1269210.7577 | 2730583.555 | 1269179.7732 | 2730591.2542 | 1269152.1241
40 | 2731016.0692 | 1269147.0396 | 2730932.3758 | 1269137.3418 | 2730841.4135 | 1269127.1504 | 2730720.0821 | 1269113.2293 | 2730688.4956 | 1269109.4159
41 | 2730684.5511 | 1269104.6463 | 2730688.4956 | 1269109.4159
42 | 2731016.0692 | 1269147.0396 | 2731017.805 | 1269174.9935 | 2731019.0202 | 1269180.6146 | 2731011.5686 | 1269181.9173
43 | 2730684.5511 | 1269104.6463 | 2730666.279 | 1269102.6625 | 2730653.4391 | 1269101.1391
44 | 2731011.5686 | 1269181.9173 | 2731010.3727 | 1269190.688 | 2731009.0213 | 1269208.8419 | 2731008.1364 | 1269222.5319
45 | 2730641.42 | 1269099.7247 | 2730652.6812 | 1269101.0492 | 2730653.4391 | 1269101.1391
46 | 2730667.1618 | 1268864.1677 | 2730665.6658 | 1268869.8511 | 2730662.7348 | 1268881.8643 | 2730661.8106 | 1268885.5251
47 | 2730661.8106 | 1268885.5251 | 2730631.7891 | 1269004.1623 | 2730620.5928 | 1269047.0223
48 | 2730667.1618 | 1268864.1677 | 2730660.5388 | 1268863.7319 | 2730644.8764 | 1268863.1962 | 2730608.3081 | 1268855.8252 | 2730403.7893 | 1268814.2687 | 2730349.5832 | 1268802.7172 | 2730330.557 | 1268800.0617 | 2730311.1832 | 1268800.1901 | 2730288.91 | 1268804.4585 | 2730252.5871 | 1268818.3485 | 2730246.2447 | 1268820.7688
49 | 2730620.5928 | 1269047.0223 | 2730619.6455 | 1269050.6485
50 | 2730638.122 | 1269099.3368 | 2730641.42 | 1269099.7247
51 | 2730521.6764 | 1269103.4226 | 2730517.5612 | 1269104.4969
52 | 2730521.6764 | 1269103.4226 | 2730540.674 | 1269122.7133
53 | 2730521.6764 | 1269103.4226 | 2730556.5524 | 1269094.3179 | 2730560.3543 | 1269093.9562
54 | 2730540.674 | 1269122.7133 | 2730540.9516 | 1269122.9951
55 | 2730563.6453 | 1269093.6431 | 2730560.3543 | 1269093.9562
56 | 2730549.5446 | 1269131.7207 | 2730540.9516 | 1269122.9951
57 | 2730613.4476 | 1269075.3908 | 2730616.9677 | 1269060.8994 | 2730619.6455 | 1269050.6485
58 | 2730613.4476 | 1269075.3908 | 2730614.2885 | 1269087.3985 | 2730614.8151 | 1269091.1582 | 2730616.2878 | 1269093.3261 | 2730620.4059 | 1269094.3403 | 2730626.0181 | 1269095.5322 | 2730638.122 | 1269099.3368
59 | 2730597.4402 | 1269125.5177 | 2730593.5892 | 1269143.7387 | 2730591.2542 | 1269152.1241

## bus_geodata
| x | y | coords
0 | 2730593.5497 | 1269091.7317
1 | 2730584.0158 | 1269093.2683
2 | 2730599.7484 | 1269091.6256
3 | 2730605.7831 | 1269119.9969
4 | 2730601.9211 | 1269118.2988
5 | 2730593.6823 | 1269114.6911
6 | 2730597.1196 | 1269116.1907
7 | 2731042.6525 | 1269197.5939
8 | 2731041.3621 | 1269192.8884
9 | 2731045.471 | 1269207.8715
10 | 2731031.6866 | 1269179.7503
11 | 2730710.889 | 1268693.6496
12 | 2730706.837 | 1268709.4545
13 | 2730718.6372 | 1268663.4276
14 | 2730782.4184 | 1268615.8293
15 | 2730752.4296 | 1268602.5766
16 | 2730736.1279 | 1268595.3725
17 | 2730741.3756 | 1268574.9694
18 | 2730701.257 | 1268656.3956
19 | 2730748.6584 | 1268546.6482
20 | 2730716.9296 | 1268563.9885
21 | 2730646.9836 | 1268594.1366
22 | 2730641.7726 | 1268621.0766
23 | 2730649.1349 | 1268583.0145
24 | 2730669.5557 | 1268639.6974
25 | 2730659.3011 | 1268659.7896
26 | 2730685.0707 | 1268648.7337
27 | 2730775.6652 | 1268557.4894
28 | 2730582.286 | 1269306.6407
29 | 2730624.1871 | 1269303.1853
30 | 2730544.474 | 1269307.8864
31 | 2730624.2544 | 1269303.1729
32 | 2730548.2922 | 1269295.2254
33 | 2730639.1415 | 1269300.4224
34 | 2730510.6545 | 1269294.7177
35 | 2730566.6717 | 1269236.0387
36 | 2730574.4099 | 1269210.7577
37 | 2730688.4956 | 1269109.4159
38 | 2731016.0692 | 1269147.0396
39 | 2730684.5511 | 1269104.6463
40 | 2731011.5686 | 1269181.9173
41 | 2730653.4391 | 1269101.1391
42 | 2730661.8106 | 1268885.5251
43 | 2730667.1618 | 1268864.1677
44 | 2730620.5928 | 1269047.0223
45 | 2731068.7988 | 1269167.3112
46 | 2731008.1364 | 1269222.5319
47 | 2730641.42 | 1269099.7247
48 | 2730517.5612 | 1269104.4969
49 | 2730521.6764 | 1269103.4226
50 | 2730540.674 | 1269122.7133
51 | 2730560.3543 | 1269093.9562
52 | 2730540.9516 | 1269122.9951
53 | 2730563.6453 | 1269093.6431
54 | 2730549.5446 | 1269131.7207
55 | 2730619.6455 | 1269050.6485
56 | 2730613.4476 | 1269075.3908
57 | 2730638.122 | 1269099.3368
58 | 2730246.2447 | 1268820.7688
59 | 2730597.4402 | 1269125.5177
60 | 2730591.2542 | 1269152.1241
61 | 2730620.5928 | 1269047.0223

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1