## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_4921-11_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_4921-11_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_4921-11_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_4921-11_0_3_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_4921-11_0_3_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_4921-11_0_3_node_67 | 0.4 | n |  | TRUE
6 | bus_LV_4921-11_0_3_node_66 | 0.4 | n |  | TRUE
7 | bus_LV_4921-11_0_3_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_4921-11_0_3_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_4921-11_0_3_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_4921-11_0_3_node_41 | 0.4 | n |  | TRUE
11 | bus_LV_4921-11_0_3_node_10 | 0.4 | n |  | TRUE
12 | bus_LV_4921-11_0_3_node_21 | 0.4 | n |  | TRUE
13 | bus_LV_4921-11_0_3_node_63 | 0.4 | n |  | TRUE
14 | bus_LV_4921-11_0_3_node_42 | 0.4 | n |  | TRUE
15 | bus_LV_4921-11_0_3_node_46 | 0.4 | n |  | TRUE
16 | bus_LV_4921-11_0_3_node_59 | 0.4 | n |  | TRUE
17 | bus_LV_4921-11_0_3_node_45 | 0.4 | n |  | TRUE
18 | bus_LV_4921-11_0_3_node_44 | 0.4 | n |  | TRUE
19 | bus_LV_4921-11_0_3_node_22 | 0.4 | n |  | TRUE
20 | bus_LV_4921-11_0_3_node_20 | 0.4 | n |  | TRUE
21 | bus_LV_4921-11_0_3_node_64 | 0.4 | n |  | TRUE
22 | bus_LV_4921-11_0_3_node_11 | 0.4 | n |  | TRUE
23 | bus_LV_4921-11_0_3_node_12 | 0.4 | n |  | TRUE
24 | bus_LV_4921-11_0_3_node_13 | 0.4 | n |  | TRUE
25 | bus_LV_4921-11_0_3_node_15 | 0.4 | n |  | TRUE
26 | bus_LV_4921-11_0_3_node_16 | 0.4 | n |  | TRUE
27 | bus_LV_4921-11_0_3_node_17 | 0.4 | n |  | TRUE
28 | bus_LV_4921-11_0_3_node_36 | 0.4 | n |  | TRUE
29 | bus_LV_4921-11_0_3_node_18 | 0.4 | n |  | TRUE
30 | bus_LV_4921-11_0_3_node_19 | 0.4 | n |  | TRUE
31 | bus_LV_4921-11_0_3_node_26 | 0.4 | n |  | TRUE
32 | bus_LV_4921-11_0_3_node_30 | 0.4 | n |  | TRUE
33 | bus_LV_4921-11_0_3_node_32 | 0.4 | n |  | TRUE
34 | bus_LV_4921-11_0_3_node_28 | 0.4 | n |  | TRUE
35 | bus_LV_4921-11_0_3_node_40 | 0.4 | n |  | TRUE
36 | bus_LV_4921-11_0_3_node_38 | 0.4 | n |  | TRUE
37 | bus_LV_4921-11_0_3_node_23 | 0.4 | n |  | TRUE
38 | bus_LV_4921-11_0_3_node_24 | 0.4 | n |  | TRUE
39 | bus_LV_4921-11_0_3_node_25 | 0.4 | n |  | TRUE
40 | bus_LV_4921-11_0_3_node_27 | 0.4 | n |  | TRUE
41 | bus_LV_4921-11_0_3_node_33 | 0.4 | n |  | TRUE
42 | bus_LV_4921-11_0_3_node_43 | 0.4 | n |  | TRUE
43 | bus_LV_4921-11_0_3_node_34 | 0.4 | n |  | TRUE
44 | bus_LV_4921-11_0_3_node_72 | 0.4 | n |  | TRUE
45 | bus_LV_4921-11_0_3_node_29 | 0.4 | n |  | TRUE
46 | bus_LV_4921-11_0_3_node_31 | 0.4 | n |  | TRUE
47 | bus_LV_4921-11_0_3_node_56 | 0.4 | n |  | TRUE
48 | bus_LV_4921-11_0_3_node_65 | 0.4 | n |  | TRUE
49 | bus_LV_4921-11_0_3_node_57 | 0.4 | n |  | TRUE
50 | bus_LV_4921-11_0_3_node_35 | 0.4 | n |  | TRUE
51 | bus_LV_4921-11_0_3_node_53 | 0.4 | n |  | TRUE
52 | bus_LV_4921-11_0_3_node_54 | 0.4 | n |  | TRUE
53 | bus_LV_4921-11_0_3_node_55 | 0.4 | n |  | TRUE
54 | bus_LV_4921-11_0_3_node_37 | 0.4 | n |  | TRUE
55 | bus_LV_4921-11_0_3_node_39 | 0.4 | n |  | TRUE
56 | bus_LV_4921-11_0_3_node_60 | 0.4 | n |  | TRUE
57 | bus_LV_4921-11_0_3_node_61 | 0.4 | n |  | TRUE
58 | bus_LV_4921-11_0_3_node_48 | 0.4 | n |  | TRUE
59 | bus_LV_4921-11_0_3_node_49 | 0.4 | n |  | TRUE
60 | bus_LV_4921-11_0_3_node_50 | 0.4 | n |  | TRUE
61 | bus_LV_4921-11_0_3_node_51 | 0.4 | n |  | TRUE
62 | bus_LV_4921-11_0_3_node_52 | 0.4 | n |  | TRUE
63 | bus_LV_4921-11_0_3_node_58 | 0.4 | n |  | TRUE
64 | bus_LV_4921-11_0_3_node_71 | 0.4 | n |  | TRUE
65 | bus_MV_487_1_node_133 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_4921-11_0_3_load_0 | 0 | 0.00029124 | 7.2992e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_4921-11_0_3_load_1 | 1 | 0.0011343 | 0.00028428 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_4921-11_0_3_load_4 | 3 | 0.00045456 | 0.00011392 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_4921-11_0_3_load_3 | 4 | 0.00064772 | 0.00016234 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_4921-11_0_3_load_67 | 5 | 8.467e-05 | 2.122e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_4921-11_0_3_load_66 | 6 | 0.00023487 | 5.8863e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_4921-11_0_3_load_5 | 7 | 0.0036719 | 0.00092027 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_4921-11_0_3_load_6 | 8 | 0.0032904 | 0.00082464 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_4921-11_0_3_load_8 | 9 | 0.00089735 | 0.0002249 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_4921-11_0_3_load_41 | 10 | 0.00066915 | 0.00016771 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_4921-11_0_3_load_63 | 13 | 0.0030931 | 0.00077521 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_4921-11_0_3_load_42 | 14 | 0.0012026 | 0.00030141 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_4921-11_0_3_load_59 | 16 | 0.0086138 | 0.0021588 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_4921-11_0_3_load_45 | 17 | 0.0052422 | 0.0013138 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_4921-11_0_3_load_44 | 18 | 0.0029046 | 0.00072796 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_4921-11_0_3_load_22 | 19 | 0.0017831 | 0.00044689 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_4921-11_0_3_load_20 | 20 | 0.0045057 | 0.0011292 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_4921-11_0_3_load_64 | 21 | 0.0014376 | 0.0003603 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_4921-11_0_3_load_11 | 22 | 0.0019302 | 0.00048374 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_4921-11_0_3_load_12 | 23 | 0.0017155 | 0.00042994 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_4921-11_0_3_load_15 | 25 | 0.0026113 | 0.00065446 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_4921-11_0_3_load_16 | 26 | 0.00072215 | 0.00018099 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_4921-11_0_3_load_36 | 28 | 0.0027502 | 0.00068926 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_4921-11_0_3_load_18 | 29 | 0.0044838 | 0.0011237 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_4921-11_0_3_load_19 | 30 | 0.00086858 | 0.00021769 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_4921-11_0_3_load_32 | 33 | 0.00024581 | 6.1606e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_4921-11_0_3_load_28 | 34 | 0.001612 | 0.00040402 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_4921-11_0_3_load_38 | 36 | 0.00032901 | 8.2458e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_4921-11_0_3_load_23 | 37 | 0.0022946 | 0.00057507 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_4921-11_0_3_load_24 | 38 | 0.00068746 | 0.00017229 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_4921-11_0_3_load_25 | 39 | 0.00032144 | 8.0559e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_4921-11_0_3_load_27 | 40 | 0.001859 | 0.00046592 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_4921-11_0_3_load_33 | 41 | 0.0022291 | 0.00055866 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_4921-11_0_3_load_34 | 43 | 0.00062698 | 0.00015714 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_4921-11_0_3_load_72 | 44 | 0.0033774 | 0.00084645 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_4921-11_0_3_load_29 | 45 | 0.00078826 | 0.00019756 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_4921-11_0_3_load_31 | 46 | 0.0031291 | 0.00078422 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_4921-11_0_3_load_56 | 47 | 0.0005559 | 0.00013932 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_4921-11_0_3_load_65 | 48 | 0.00073855 | 0.0001851 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_4921-11_0_3_load_57 | 49 | 0.0019853 | 0.00049756 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_4921-11_0_3_load_35 | 50 | 0.00068746 | 0.00017229 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_4921-11_0_3_load_55 | 53 | 0.0070481 | 0.0017664 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_4921-11_0_3_load_37 | 54 | 0.00039446 | 9.886e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_4921-11_0_3_load_39 | 55 | 0.00077092 | 0.00019321 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_4921-11_0_3_load_60 | 56 | 0.0028818 | 0.00072226 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_4921-11_0_3_load_61 | 57 | 0.0018778 | 0.00047063 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_4921-11_0_3_load_48 | 58 | 0.0043832 | 0.0010985 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_4921-11_0_3_load_49 | 59 | 0.0029368 | 0.00073603 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_4921-11_0_3_load_50 | 60 | 0.0039989 | 0.0010022 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_4921-11_0_3_load_51 | 61 | 0.002639 | 0.0006614 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_4921-11_0_3_load_52 | 62 | 0.0057663 | 0.0014452 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_4921-11_0_3_load_71 | 64 | 0.0016405 | 0.00041116 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 14 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_4921-11_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.051978 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_4921-11_0_3_line_1 | NAYY 4x150 SE | 1 | 2 | 0.031896 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_4921-11_0_3_line_2 | NAYY 4x150 SE | 2 | 3 | 0.031413 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_4921-11_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.034286 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_4921-11_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.027993 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_4921-11_0_3_line_5 | NAYY 4x150 SE | 5 | 6 | 0.0036558 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_4921-11_0_3_line_6 | NAYY 4x150 SE | 6 | 48 | 0.0061435 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_4921-11_0_3_line_7 | NAYY 4x150 SE | 7 | 8 | 0.0062817 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_4921-11_0_3_line_8 | NAYY 4x150 SE | 8 | 9 | 0.014319 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_4921-11_0_3_line_9 | NAYY 4x150 SE | 9 | 10 | 0.0083106 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_4921-11_0_3_line_10 | NAYY 4x150 SE | 10 | 14 | 0.007369 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_4921-11_0_3_line_11 | NAYY 4x150 SE | 11 | 12 | 0.019523 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_4921-11_0_3_line_12 | NAYY 4x150 SE | 11 | 13 | 0.031813 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_4921-11_0_3_line_13 | NAYY 4x150 SE | 12 | 19 | 0.044991 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_4921-11_0_3_line_14 | NAYY 4x150 SE | 12 | 20 | 0.030815 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_4921-11_0_3_line_15 | NAYY 4x150 SE | 13 | 21 | 0.027631 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_4921-11_0_3_line_16 | NAYY 4x150 SE | 14 | 30 | 0.03759 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
17 | LV_4921-11_0_3_line_17 | NAYY 4x150 SE | 15 | 16 | 0.013522 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_4921-11_0_3_line_18 | NAYY 4x150 SE | 15 | 17 | 0.025837 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_4921-11_0_3_line_19 | NAYY 4x150 SE | 16 | 52 | 0.011892 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_4921-11_0_3_line_20 | NAYY 4x150 SE | 17 | 18 | 0.012397 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_4921-11_0_3_line_21 | NAYY 4x150 SE | 19 | 35 | 0.1196 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_4921-11_0_3_line_22 | NAYY 4x150 SE | 21 | 63 | 0.011677 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_4921-11_0_3_line_23 | NAYY 4x150 SE | 22 | 23 | 0.0090411 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_4921-11_0_3_line_24 | NAYY 4x150 SE | 22 | 24 | 0.079084 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_4921-11_0_3_line_25 | NAYY 4x150 SE | 24 | 25 | 0.024852 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_4921-11_0_3_line_26 | NAYY 4x150 SE | 24 | 26 | 0.052155 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_4921-11_0_3_line_27 | NAYY 4x150 SE | 25 | 27 | 0.023806 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_4921-11_0_3_line_28 | NAYY 4x150 SE | 26 | 28 | 0.0010501 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_4921-11_0_3_line_29 | NAYY 4x150 SE | 27 | 29 | 0.02681 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_4921-11_0_3_line_30 | NAYY 4x150 SE | 27 | 30 | 0.041996 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_4921-11_0_3_line_31 | NAYY 4x150 SE | 28 | 31 | 0.012818 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_4921-11_0_3_line_32 | NAYY 4x150 SE | 29 | 32 | 0.031341 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_4921-11_0_3_line_33 | NAYY 4x150 SE | 31 | 41 | 0.0078814 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_4921-11_0_3_line_34 | NAYY 4x150 SE | 31 | 38 | 0.021597 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_4921-11_0_3_line_35 | NAYY 4x150 SE | 32 | 33 | 0.047049 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_4921-11_0_3_line_36 | NAYY 4x150 SE | 32 | 34 | 0.032201 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_4921-11_0_3_line_37 | NAYY 4x150 SE | 33 | 48 | 0.0197 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_4921-11_0_3_line_38 | NAYY 4x150 SE | 34 | 45 | 0.014665 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_4921-11_0_3_line_39 | NAYY 4x150 SE | 35 | 36 | 0.032926 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_4921-11_0_3_line_40 | NAYY 4x150 SE | 36 | 54 | 0.009954 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_4921-11_0_3_line_41 | NAYY 4x150 SE | 37 | 38 | 0.0097303 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_4921-11_0_3_line_42 | NAYY 4x150 SE | 37 | 39 | 0.010231 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_4921-11_0_3_line_43 | NAYY 4x150 SE | 39 | 40 | 0.021489 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_4921-11_0_3_line_44 | NAYY 4x150 SE | 40 | 42 | 0.015551 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_4921-11_0_3_line_45 | NAYY 4x150 SE | 41 | 43 | 0.0081113 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_4921-11_0_3_line_46 | NAYY 4x150 SE | 42 | 44 | 0.043774 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_4921-11_0_3_line_47 | NAYY 4x150 SE | 43 | 50 | 0.0054522 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_4921-11_0_3_line_48 | NAYY 4x150 SE | 45 | 46 | 0.010934 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_4921-11_0_3_line_49 | NAYY 4x150 SE | 46 | 47 | 0.011987 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_4921-11_0_3_line_50 | NAYY 4x150 SE | 47 | 49 | 0.003321 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_4921-11_0_3_line_51 | NAYY 4x150 SE | 49 | 63 | 0.044476 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_4921-11_0_3_line_52 | NAYY 4x150 SE | 50 | 51 | 0.050024 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_4921-11_0_3_line_53 | NAYY 4x150 SE | 51 | 52 | 0.027369 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_4921-11_0_3_line_54 | NAYY 4x150 SE | 51 | 53 | 0.023902 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_4921-11_0_3_line_55 | NAYY 4x150 SE | 52 | 61 | 0.011027 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_4921-11_0_3_line_56 | NAYY 4x150 SE | 54 | 55 | 0.028008 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_4921-11_0_3_line_57 | NAYY 4x150 SE | 56 | 57 | 0.0038292 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_4921-11_0_3_line_58 | NAYY 4x150 SE | 57 | 62 | 0.010886 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_4921-11_0_3_line_59 | NAYY 4x150 SE | 58 | 59 | 0.0080301 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_4921-11_0_3_line_60 | NAYY 4x150 SE | 58 | 60 | 0.026382 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_4921-11_0_3_line_61 | NAYY 4x150 SE | 59 | 61 | 0.04352 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_4921-11_0_3_line_62 | NAYY 4x150 SE | 60 | 62 | 0.0056407 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_4921-11_0_3_line_63 | NAYY 4x150 SE | 63 | 64 | 0.021321 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_4921-11_0_3_trafo_42 | 0.25 MVA 20/0.4 kV | 65 | 14 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2726618.1984 | 1266370.3477 | 2726627.2978 | 1266351.3139 | 2726634.1377 | 1266341.418 | 2726641.8044 | 1266335.1098 | 2726649.899 | 1266331.3553
1 | 2726680.2796 | 1266321.9109 | 2726669.8931 | 1266324.0459 | 2726650.8341 | 1266330.9216 | 2726649.899 | 1266331.3553
2 | 2726680.2796 | 1266321.9109 | 2726685.6332 | 1266291.075 | 2726685.6644 | 1266290.9637
3 | 2726680.2796 | 1266321.9109 | 2726678.9594 | 1266342.3793 | 2726679.3666 | 1266356.1487
4 | 2726693.2206 | 1266264.0097 | 2726685.6644 | 1266290.9637
5 | 2726694.2074 | 1266260.4896 | 2726693.2206 | 1266264.0097
6 | 2726695.9242 | 1266254.591 | 2726694.5555 | 1266259.248 | 2726694.2074 | 1266260.4896
7 | 2726640.23 | 1266053.8605 | 2726645.9662 | 1266056.4209
8 | 2726658.715 | 1266062.9025 | 2726656.5365 | 1266061.5066 | 2726648.2409 | 1266057.4362 | 2726645.9662 | 1266056.4209
9 | 2726658.715 | 1266062.9025 | 2726665.7122 | 1266067.3864
10 | 2726665.7122 | 1266067.3864 | 2726665.7122 | 1266067.3864 | 2726670.7135 | 1266072.7984
11 | 2726571.6776 | 1266091.639 | 2726587.2069 | 1266079.7494
12 | 2726587.2069 | 1266079.7494 | 2726596.6777 | 1266102.4287 | 2726600.6891 | 1266108.4507
13 | 2726571.6776 | 1266091.639 | 2726552.6098 | 1266106.9782 | 2726540.361 | 1266118.6823 | 2726538.5451 | 1266121.7651
14 | 2726571.6776 | 1266091.639 | 2726545.4823 | 1266075.4097
15 | 2726600.6891 | 1266108.4507 | 2726616.0072 | 1266131.4466
16 | 2726670.7135 | 1266072.7984 | 2726672.234 | 1266074.4437 | 2726684.6345 | 1266088.3445 | 2726695.9072 | 1266100.695
17 | 2726703.9181 | 1265968.1693 | 2726714.9556 | 1265975.9803
18 | 2726703.9181 | 1265968.1693 | 2726699.4874 | 1265973.8796 | 2726684.5194 | 1265984.9365
19 | 2726724.6624 | 1265982.8497 | 2726714.9556 | 1265975.9803
20 | 2726674.5483 | 1265992.3022 | 2726684.5194 | 1265984.9365
21 | 2726521.7715 | 1266237.9165 | 2726525.679 | 1266227.4349 | 2726529.0861 | 1266214.2957 | 2726529.79 | 1266201.8326 | 2726527.568 | 1266162.1151 | 2726527.7929 | 1266151.2655 | 2726529.729 | 1266140.6972 | 2726533.3031 | 1266130.6645 | 2726538.5451 | 1266121.7651
22 | 2726623.2154 | 1266140.5656 | 2726619.7578 | 1266137.0772 | 2726616.0072 | 1266131.4466
23 | 2726846.6743 | 1266172.3069 | 2726838.9627 | 1266167.5876
24 | 2726768.8908 | 1266131.2348 | 2726810.4963 | 1266150.1668 | 2726838.9627 | 1266167.5876
25 | 2726768.8908 | 1266131.2348 | 2726744.1601 | 1266128.7799
26 | 2726768.8908 | 1266131.2348 | 2726770.01 | 1266079.0913
27 | 2726721.2014 | 1266133.9703 | 2726739.8726 | 1266128.3543 | 2726744.1601 | 1266128.7799
28 | 2726770.01 | 1266079.0913 | 2726770.0326 | 1266078.0415
29 | 2726721.2014 | 1266133.9703 | 2726723.1911 | 1266140.9305 | 2726724.1686 | 1266150.4825 | 2726724.0442 | 1266152.0702 | 2726723.3679 | 1266160.4189
30 | 2726721.2014 | 1266133.9703 | 2726717.6586 | 1266127.088 | 2726708.7272 | 1266114.7408 | 2726695.9072 | 1266100.695
31 | 2726770.3077 | 1266065.2265 | 2726770.0326 | 1266078.0415
32 | 2726714.7454 | 1266190.5508 | 2726723.3679 | 1266160.4189
33 | 2726770.3077 | 1266065.2265 | 2726763.8209 | 1266060.75 | 2726763.8209 | 1266060.75
34 | 2726770.3077 | 1266065.2265 | 2726784.4003 | 1266056.7765 | 2726788.5565 | 1266053.7096
35 | 2726714.7454 | 1266190.5508 | 2726714.2172 | 1266192.3522 | 2726701.4794 | 1266235.6905
36 | 2726714.7454 | 1266190.5508 | 2726704.2347 | 1266188.2789 | 2726684.2124 | 1266180.5904
37 | 2726695.9242 | 1266254.591 | 2726701.4794 | 1266235.6905
38 | 2726670.522 | 1266175.3334 | 2726684.2124 | 1266180.5904
39 | 2726521.7715 | 1266237.9165 | 2726533.1409 | 1266247.9135 | 2726537.5105 | 1266255.236 | 2726538.8657 | 1266264.3957
40 | 2726538.8657 | 1266264.3957 | 2726538.3044 | 1266274.3338
41 | 2726795.3641 | 1266047.1985 | 2726794.7396 | 1266049.1468 | 2726788.5565 | 1266053.7096
42 | 2726798.161 | 1266037.3733 | 2726797.678 | 1266039.9792 | 2726795.3641 | 1266047.1985
43 | 2726798.161 | 1266037.3733 | 2726802.0767 | 1266016.2444
44 | 2726804.9105 | 1266000.9539 | 2726802.0767 | 1266016.2444
45 | 2726762.2121 | 1266052.7999 | 2726763.8209 | 1266060.75
46 | 2726804.9105 | 1266000.9539 | 2726813.2345 | 1265957.9785
47 | 2726761.1306 | 1266047.456 | 2726762.2121 | 1266052.7999
48 | 2726670.522 | 1266175.3334 | 2726670.522 | 1266175.3334 | 2726674.6034 | 1266165.1892 | 2726674.6034 | 1266165.1892
49 | 2726663.5134 | 1266160.6405 | 2726674.6034 | 1266165.1892
50 | 2726663.5134 | 1266160.6405 | 2726660.4407 | 1266159.3802
51 | 2726623.2154 | 1266140.5656 | 2726633.3882 | 1266150.1701 | 2726644.4435 | 1266156.902 | 2726648.7112 | 1266154.5691 | 2726660.4407 | 1266159.3802
52 | 2726739.3922 | 1266003.3288 | 2726752.5529 | 1266022.5175 | 2726757.8285 | 1266031.1386 | 2726761.1306 | 1266047.456
53 | 2726739.3922 | 1266003.3288 | 2726726.9663 | 1265995.1771 | 2726724.6624 | 1265982.8497
54 | 2726739.3922 | 1266003.3288 | 2726750.9206 | 1265982.3907
55 | 2726724.6624 | 1265982.8497 | 2726723.635 | 1265977.3782 | 2726722.3346 | 1265972.0754
56 | 2726538.0933 | 1266302.3076 | 2726537.5187 | 1266288.2444 | 2726538.3044 | 1266274.3338
57 | 2726728.4595 | 1265880.8824 | 2726730.2149 | 1265884.2855
58 | 2726730.2149 | 1265884.2855 | 2726733.7264 | 1265891.0928 | 2726732.2598 | 1265893.9665
59 | 2726717.7025 | 1265922.4893 | 2726717.7025 | 1265922.4893 | 2726720.7535 | 1265929.9172
60 | 2726717.7025 | 1265922.4893 | 2726729.6956 | 1265898.9907
61 | 2726722.3346 | 1265972.0754 | 2726721.2525 | 1265967.6626 | 2726725.376 | 1265941.171 | 2726720.7535 | 1265929.9172
62 | 2726732.2598 | 1265893.9665 | 2726729.6956 | 1265898.9907
63 | 2726623.2154 | 1266140.5656 | 2726608.2707 | 1266155.772

## bus_geodata
| x | y | coords
0 | 2726618.1984 | 1266370.3477
1 | 2726649.899 | 1266331.3553
2 | 2726680.2796 | 1266321.9109
3 | 2726685.6644 | 1266290.9637
4 | 2726679.3666 | 1266356.1487
5 | 2726693.2206 | 1266264.0097
6 | 2726694.2074 | 1266260.4896
7 | 2726640.23 | 1266053.8605
8 | 2726645.9662 | 1266056.4209
9 | 2726658.715 | 1266062.9025
10 | 2726665.7122 | 1266067.3864
11 | 2726587.2069 | 1266079.7494
12 | 2726571.6776 | 1266091.639
13 | 2726600.6891 | 1266108.4507
14 | 2726670.7135 | 1266072.7984
15 | 2726703.9181 | 1265968.1693
16 | 2726714.9556 | 1265975.9803
17 | 2726684.5194 | 1265984.9365
18 | 2726674.5483 | 1265992.3022
19 | 2726538.5451 | 1266121.7651
20 | 2726545.4823 | 1266075.4097
21 | 2726616.0072 | 1266131.4466
22 | 2726838.9627 | 1266167.5876
23 | 2726846.6743 | 1266172.3069
24 | 2726768.8908 | 1266131.2348
25 | 2726744.1601 | 1266128.7799
26 | 2726770.01 | 1266079.0913
27 | 2726721.2014 | 1266133.9703
28 | 2726770.0326 | 1266078.0415
29 | 2726723.3679 | 1266160.4189
30 | 2726695.9072 | 1266100.695
31 | 2726770.3077 | 1266065.2265
32 | 2726714.7454 | 1266190.5508
33 | 2726701.4794 | 1266235.6905
34 | 2726684.2124 | 1266180.5904
35 | 2726521.7715 | 1266237.9165
36 | 2726538.8657 | 1266264.3957
37 | 2726795.3641 | 1266047.1985
38 | 2726788.5565 | 1266053.7096
39 | 2726798.161 | 1266037.3733
40 | 2726802.0767 | 1266016.2444
41 | 2726763.8209 | 1266060.75
42 | 2726804.9105 | 1266000.9539
43 | 2726762.2121 | 1266052.7999
44 | 2726813.2345 | 1265957.9785
45 | 2726670.522 | 1266175.3334
46 | 2726674.6034 | 1266165.1892
47 | 2726663.5134 | 1266160.6405
48 | 2726695.9242 | 1266254.591
49 | 2726660.4407 | 1266159.3802
50 | 2726761.1306 | 1266047.456
51 | 2726739.3922 | 1266003.3288
52 | 2726724.6624 | 1265982.8497
53 | 2726750.9206 | 1265982.3907
54 | 2726538.3044 | 1266274.3338
55 | 2726538.0933 | 1266302.3076
56 | 2726728.4595 | 1265880.8824
57 | 2726730.2149 | 1265884.2855
58 | 2726717.7025 | 1265922.4893
59 | 2726720.7535 | 1265929.9172
60 | 2726729.6956 | 1265898.9907
61 | 2726722.3346 | 1265972.0754
62 | 2726732.2598 | 1265893.9665
63 | 2726623.2154 | 1266140.5656
64 | 2726608.2707 | 1266155.772
65 | 2726623.1664 | 1266046.2443

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1