## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_4951-1_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_4951-1_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_4951-1_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_4951-1_0_2_node_125 | 0.4 | n |  | TRUE
4 | bus_LV_4951-1_0_2_node_182 | 0.4 | n |  | TRUE
5 | bus_LV_4951-1_0_2_node_128 | 0.4 | n |  | TRUE
6 | bus_LV_4951-1_0_2_node_127 | 0.4 | n |  | TRUE
7 | bus_LV_4951-1_0_2_node_129 | 0.4 | n |  | TRUE
8 | bus_LV_4951-1_0_2_node_130 | 0.4 | n |  | TRUE
9 | bus_LV_4951-1_0_2_node_131 | 0.4 | n |  | TRUE
10 | bus_LV_4951-1_0_2_node_132 | 0.4 | n |  | TRUE
11 | bus_LV_4951-1_0_2_node_133 | 0.4 | n |  | TRUE
12 | bus_LV_4951-1_0_2_node_134 | 0.4 | n |  | TRUE
13 | bus_LV_4951-1_0_2_node_136 | 0.4 | n |  | TRUE
14 | bus_LV_4951-1_0_2_node_137 | 0.4 | n |  | TRUE
15 | bus_LV_4951-1_0_2_node_140 | 0.4 | n |  | TRUE
16 | bus_LV_4951-1_0_2_node_143 | 0.4 | n |  | TRUE
17 | bus_LV_4951-1_0_2_node_144 | 0.4 | n |  | TRUE
18 | bus_LV_4951-1_0_2_node_138 | 0.4 | n |  | TRUE
19 | bus_LV_4951-1_0_2_node_145 | 0.4 | n |  | TRUE
20 | bus_LV_4951-1_0_2_node_142 | 0.4 | n |  | TRUE
21 | bus_LV_4951-1_0_2_node_139 | 0.4 | n |  | TRUE
22 | bus_LV_4951-1_0_2_node_141 | 0.4 | n |  | TRUE
23 | bus_LV_4951-1_0_2_node_147 | 0.4 | n |  | TRUE
24 | bus_LV_4951-1_0_2_node_146 | 0.4 | n |  | TRUE
25 | bus_LV_4951-1_0_2_node_149 | 0.4 | n |  | TRUE
26 | bus_LV_4951-1_0_2_node_148 | 0.4 | n |  | TRUE
27 | bus_LV_4951-1_0_2_node_176 | 0.4 | n |  | TRUE
28 | bus_LV_4951-1_0_2_node_153 | 0.4 | n |  | TRUE
29 | bus_LV_4951-1_0_2_node_175 | 0.4 | n |  | TRUE
30 | bus_LV_4951-1_0_2_node_150 | 0.4 | n |  | TRUE
31 | bus_LV_4951-1_0_2_node_151 | 0.4 | n |  | TRUE
32 | bus_LV_4951-1_0_2_node_154 | 0.4 | n |  | TRUE
33 | bus_LV_4951-1_0_2_node_155 | 0.4 | n |  | TRUE
34 | bus_LV_4951-1_0_2_node_152 | 0.4 | n |  | TRUE
35 | bus_LV_4951-1_0_2_node_156 | 0.4 | n |  | TRUE
36 | bus_LV_4951-1_0_2_node_157 | 0.4 | n |  | TRUE
37 | bus_LV_4951-1_0_2_node_160 | 0.4 | n |  | TRUE
38 | bus_LV_4951-1_0_2_node_161 | 0.4 | n |  | TRUE
39 | bus_LV_4951-1_0_2_node_158 | 0.4 | n |  | TRUE
40 | bus_LV_4951-1_0_2_node_159 | 0.4 | n |  | TRUE
41 | bus_LV_4951-1_0_2_node_162 | 0.4 | n |  | TRUE
42 | bus_LV_4951-1_0_2_node_163 | 0.4 | n |  | TRUE
43 | bus_LV_4951-1_0_2_node_164 | 0.4 | n |  | TRUE
44 | bus_LV_4951-1_0_2_node_165 | 0.4 | n |  | TRUE
45 | bus_LV_4951-1_0_2_node_167 | 0.4 | n |  | TRUE
46 | bus_LV_4951-1_0_2_node_169 | 0.4 | n |  | TRUE
47 | bus_LV_4951-1_0_2_node_168 | 0.4 | n |  | TRUE
48 | bus_LV_4951-1_0_2_node_181 | 0.4 | n |  | TRUE
49 | bus_LV_4951-1_0_2_node_171 | 0.4 | n |  | TRUE
50 | bus_LV_4951-1_0_2_node_170 | 0.4 | n |  | TRUE
51 | bus_LV_4951-1_0_2_node_172 | 0.4 | n |  | TRUE
52 | bus_LV_4951-1_0_2_node_173 | 0.4 | n |  | TRUE
53 | bus_LV_4951-1_0_2_node_174 | 0.4 | n |  | TRUE
54 | bus_LV_4951-1_0_2_node_179 | 0.4 | n |  | TRUE
55 | bus_LV_4951-1_0_2_node_177 | 0.4 | n |  | TRUE
56 | bus_LV_4951-1_0_2_node_178 | 0.4 | n |  | TRUE
57 | bus_LV_4951-1_0_2_node_180 | 0.4 | n |  | TRUE
58 | bus_LV_4951-1_0_2_node_124 | 0.4 | n |  | TRUE
59 | bus_LV_4951-1_0_2_node_126 | 0.4 | n |  | TRUE
60 | bus_MV_0_node_138 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_4951-1_0_2_load_0 | 0 | 0.00042124 | 0.00010557 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_4951-1_0_2_load_2 | 2 | 0.00020236 | 5.0716e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_4951-1_0_2_load_127 | 6 | 0.0019618 | 0.00049168 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_4951-1_0_2_load_129 | 7 | 0.0023726 | 0.00059463 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_4951-1_0_2_load_130 | 8 | 0.0011294 | 0.00028305 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_4951-1_0_2_load_131 | 9 | 0.00047896 | 0.00012004 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_4951-1_0_2_load_132 | 10 | 0.0019882 | 0.0004983 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_4951-1_0_2_load_133 | 11 | 0.00093234 | 0.00023367 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_4951-1_0_2_load_140 | 15 | 0.002861 | 0.00071703 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_4951-1_0_2_load_143 | 16 | 0.00075768 | 0.00018989 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_4951-1_0_2_load_144 | 17 | 0.0040606 | 0.0010177 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_4951-1_0_2_load_145 | 19 | 0.00081924 | 0.00020532 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_4951-1_0_2_load_142 | 20 | 0.0018103 | 0.00045371 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_4951-1_0_2_load_139 | 21 | 0.0061211 | 0.0015341 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_4951-1_0_2_load_147 | 23 | 0.00083783 | 0.00020998 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_4951-1_0_2_load_146 | 24 | 0.00025751 | 6.4537e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_4951-1_0_2_load_176 | 27 | 0.00026948 | 6.7537e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_4951-1_0_2_load_153 | 28 | 0.0006402 | 0.00016045 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_4951-1_0_2_load_175 | 29 | 0.0012625 | 0.00031642 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_4951-1_0_2_load_150 | 30 | 0.00062806 | 0.00015741 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_4951-1_0_2_load_151 | 31 | 0.00064374 | 0.00016134 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_4951-1_0_2_load_154 | 32 | 0.00033688 | 8.4429e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_4951-1_0_2_load_152 | 34 | 0.00071788 | 0.00017992 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_4951-1_0_2_load_156 | 35 | 0.00015997 | 4.0092e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_4951-1_0_2_load_157 | 36 | 0.0019863 | 0.00049781 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_4951-1_0_2_load_160 | 37 | 0.00024998 | 6.2651e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_4951-1_0_2_load_158 | 39 | 0.00059973 | 0.00015031 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_4951-1_0_2_load_159 | 40 | 0.00036711 | 9.2005e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_4951-1_0_2_load_162 | 41 | 0.00064335 | 0.00016124 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_4951-1_0_2_load_163 | 42 | 0.0010408 | 0.00026084 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_4951-1_0_2_load_164 | 43 | 0.00030533 | 7.6523e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_4951-1_0_2_load_165 | 44 | 0.00034714 | 8.7003e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_4951-1_0_2_load_167 | 45 | 0.00024287 | 6.0869e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_4951-1_0_2_load_181 | 48 | 0.00015067 | 3.7762e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_4951-1_0_2_load_171 | 49 | 0.00063891 | 0.00016013 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_4951-1_0_2_load_170 | 50 | 0.00042275 | 0.00010595 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_4951-1_0_2_load_172 | 51 | 0.0013983 | 0.00035044 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_4951-1_0_2_load_173 | 52 | 0.00010081 | 2.5266e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_4951-1_0_2_load_174 | 53 | 0.00011265 | 2.8232e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_4951-1_0_2_load_179 | 54 | 0.00029402 | 7.3687e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_4951-1_0_2_load_177 | 55 | 0.0013423 | 0.00033642 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_4951-1_0_2_load_178 | 56 | 0.00027006 | 6.7685e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_4951-1_0_2_load_180 | 57 | 0.00026064 | 6.5322e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_4951-1_0_2_load_124 | 58 | 0.00092755 | 0.00023247 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 18 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_4951-1_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.12562 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_4951-1_0_2_line_1 | NAYY 4x150 SE | 1 | 2 | 0.040776 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_4951-1_0_2_line_2 | NAYY 4x150 SE | 1 | 3 | 0.39338 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_4951-1_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.40212 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_4951-1_0_2_line_4 | NAYY 4x150 SE | 3 | 59 | 0.092846 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_4951-1_0_2_line_5 | NAYY 4x150 SE | 3 | 58 | 0.048295 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_4951-1_0_2_line_6 | NAYY 4x150 SE | 4 | 48 | 0.011167 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_4951-1_0_2_line_7 | NAYY 4x150 SE | 4 | 57 | 0.025761 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_4951-1_0_2_line_8 | NAYY 4x150 SE | 5 | 6 | 0.012053 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_4951-1_0_2_line_9 | NAYY 4x150 SE | 5 | 7 | 0.019661 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_4951-1_0_2_line_10 | NAYY 4x150 SE | 5 | 8 | 0.012605 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_4951-1_0_2_line_11 | NAYY 4x150 SE | 6 | 59 | 0.014017 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_4951-1_0_2_line_12 | NAYY 4x150 SE | 8 | 9 | 0.0068478 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_4951-1_0_2_line_13 | NAYY 4x150 SE | 9 | 10 | 0.0044161 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_4951-1_0_2_line_14 | NAYY 4x150 SE | 11 | 12 | 0.011272 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_4951-1_0_2_line_15 | NAYY 4x150 SE | 12 | 13 | 0.020515 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_4951-1_0_2_line_16 | NAYY 4x150 SE | 12 | 14 | 0.054551 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_4951-1_0_2_line_17 | NAYY 4x150 SE | 13 | 15 | 0.006899 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_4951-1_0_2_line_18 | NAYY 4x150 SE | 13 | 16 | 0.025521 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_4951-1_0_2_line_19 | NAYY 4x150 SE | 14 | 17 | 0.055455 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_4951-1_0_2_line_20 | NAYY 4x150 SE | 15 | 21 | 0.088709 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_4951-1_0_2_line_21 | NAYY 4x150 SE | 18 | 19 | 0.040857 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_4951-1_0_2_line_22 | NAYY 4x150 SE | 18 | 20 | 0.038665 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_4951-1_0_2_line_23 | NAYY 4x150 SE | 19 | 23 | 0.031617 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_4951-1_0_2_line_24 | NAYY 4x150 SE | 20 | 22 | 0.0574 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_4951-1_0_2_line_25 | NAYY 4x150 SE | 21 | 22 | 0.063876 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_4951-1_0_2_line_26 | NAYY 4x150 SE | 23 | 26 | 0.021827 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_4951-1_0_2_line_27 | NAYY 4x150 SE | 24 | 25 | 0.037281 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_4951-1_0_2_line_28 | NAYY 4x150 SE | 25 | 30 | 0.019144 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_4951-1_0_2_line_29 | NAYY 4x150 SE | 25 | 31 | 0.043262 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_4951-1_0_2_line_30 | NAYY 4x150 SE | 26 | 27 | 0.024784 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_4951-1_0_2_line_31 | NAYY 4x150 SE | 26 | 28 | 0.026278 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_4951-1_0_2_line_32 | NAYY 4x150 SE | 26 | 29 | 0.023942 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_4951-1_0_2_line_33 | NAYY 4x150 SE | 27 | 54 | 0.0087359 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_4951-1_0_2_line_34 | NAYY 4x150 SE | 28 | 34 | 0.0019866 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_4951-1_0_2_line_35 | NAYY 4x150 SE | 30 | 32 | 0.031667 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_4951-1_0_2_line_36 | NAYY 4x150 SE | 31 | 33 | 0.086298 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_4951-1_0_2_line_37 | NAYY 4x150 SE | 32 | 34 | 0.0056355 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_4951-1_0_2_line_38 | NAYY 4x150 SE | 33 | 35 | 0.035767 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_4951-1_0_2_line_39 | NAYY 4x150 SE | 33 | 36 | 0.056254 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_4951-1_0_2_line_40 | NAYY 4x150 SE | 35 | 37 | 0.0244 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_4951-1_0_2_line_41 | NAYY 4x150 SE | 36 | 38 | 0.1988 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_4951-1_0_2_line_42 | NAYY 4x150 SE | 37 | 40 | 0.037706 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_4951-1_0_2_line_43 | NAYY 4x150 SE | 38 | 41 | 0.062592 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_4951-1_0_2_line_44 | NAYY 4x150 SE | 39 | 40 | 0.00099607 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_4951-1_0_2_line_45 | NAYY 4x150 SE | 41 | 42 | 0.039092 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_4951-1_0_2_line_46 | NAYY 4x150 SE | 43 | 44 | 0.017599 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_4951-1_0_2_line_47 | NAYY 4x150 SE | 44 | 45 | 0.00021076 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_4951-1_0_2_line_48 | NAYY 4x150 SE | 45 | 46 | 0.0088829 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_4951-1_0_2_line_49 | NAYY 4x150 SE | 46 | 50 | 0.020932 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_4951-1_0_2_line_50 | NAYY 4x150 SE | 46 | 49 | 0.043043 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_4951-1_0_2_line_51 | NAYY 4x150 SE | 47 | 48 | 0.013351 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_4951-1_0_2_line_52 | NAYY 4x150 SE | 47 | 49 | 0.0055991 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_4951-1_0_2_line_53 | NAYY 4x150 SE | 50 | 51 | 0.0066531 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_4951-1_0_2_line_54 | NAYY 4x150 SE | 51 | 52 | 0.0055884 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_4951-1_0_2_line_55 | NAYY 4x150 SE | 52 | 53 | 0.0028857 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_4951-1_0_2_line_56 | NAYY 4x150 SE | 54 | 55 | 0.011901 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_4951-1_0_2_line_57 | NAYY 4x150 SE | 55 | 56 | 0.004533 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_4951-1_0_2_line_58 | NAYY 4x150 SE | 56 | 57 | 0.033939 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_4951-1_0_2_trafo_138 | 0.25 MVA 20/0.4 kV | 60 | 18 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2720613.7992 | 1274298.8961 | 2720639.7844 | 1274295.9465 | 2720679.9245 | 1274282.688 | 2720708.1775 | 1274274.7694 | 2720736.0315 | 1274274.5661
1 | 2720613.7992 | 1274298.8961 | 2720627.0571 | 1274334.2776 | 2720628.549 | 1274336.8709
2 | 2720222.4951 | 1274339.2402 | 2720613.7992 | 1274298.8961
3 | 2720401.3188 | 1274668.6349 | 2720628.549 | 1274336.8709
4 | 2720222.4951 | 1274339.2402 | 2720165.3831 | 1274322.5397 | 2720162.9198 | 1274328.6396 | 2720161.1896 | 1274332.7193 | 2720154.0997 | 1274342.573 | 2720147.7846 | 1274350.5741
5 | 2720222.4951 | 1274339.2402 | 2720208.7433 | 1274385.5364
6 | 2720401.3188 | 1274668.6349 | 2720399.0848 | 1274679.5761
7 | 2720401.3188 | 1274668.6349 | 2720375.6292 | 1274666.7207
8 | 2720136.1707 | 1274373.9149 | 2720141.5402 | 1274363.1237
9 | 2720136.1707 | 1274373.9149 | 2720134.0052 | 1274393.4556
10 | 2720136.1707 | 1274373.9149 | 2720124.2178 | 1274369.9127
11 | 2720147.7846 | 1274350.5741 | 2720141.5402 | 1274363.1237
12 | 2720117.7244 | 1274367.7384 | 2720124.2178 | 1274369.9127
13 | 2720113.5368 | 1274366.3362 | 2720117.7244 | 1274367.7384
14 | 2720153.6625 | 1274547.4985 | 2720154.4433 | 1274556.0556 | 2720155.0111 | 1274558.6743
15 | 2720133.1488 | 1274545.8906 | 2720153.6625 | 1274547.4985
16 | 2720169.9031 | 1274504.8785 | 2720171.1493 | 1274515.3246 | 2720173.1357 | 1274526.7201 | 2720164.84 | 1274528.5863 | 2720158.6784 | 1274530.9074 | 2720156.0063 | 1274537.6593 | 2720153.6625 | 1274547.4985
17 | 2720133.1488 | 1274545.8906 | 2720126.2505 | 1274545.9836
18 | 2720133.1488 | 1274545.8906 | 2720131.1112 | 1274571.33
19 | 2720169.9031 | 1274504.8785 | 2720114.5964 | 1274500.8318
20 | 2720092.5894 | 1274601.551 | 2720090.9406 | 1274601.4054 | 2720093.101 | 1274551.4475 | 2720096.5606 | 1274551.0731 | 2720124.0672 | 1274551.6333 | 2720126.2505 | 1274545.9836
21 | 2720210.7269 | 1274652.0239 | 2720227.2073 | 1274651.8816 | 2720241.8143 | 1274654.7263 | 2720250.1151 | 1274659.3346
22 | 2720210.7269 | 1274652.0239 | 2720200.8476 | 1274653.0014 | 2720172.2874 | 1274649.8186
23 | 2720250.1151 | 1274659.3346 | 2720258.784 | 1274664.1474 | 2720267.8413 | 1274669.181 | 2720277.7545 | 1274674.6877
24 | 2720115.2404 | 1274643.4611 | 2720172.2874 | 1274649.8186
25 | 2720115.2404 | 1274643.4611 | 2720118.4819 | 1274606.5261 | 2720112.7261 | 1274603.3282 | 2720092.5894 | 1274601.551
26 | 2720296.8352 | 1274685.2868 | 2720277.7545 | 1274674.6877
27 | 2720236.3874 | 1274736.4693 | 2720225.5481 | 1274700.7985
28 | 2720236.3874 | 1274736.4693 | 2720253.5091 | 1274727.9047
29 | 2720236.3874 | 1274736.4693 | 2720249.7764 | 1274777.6077
30 | 2720296.8352 | 1274685.2868 | 2720301.2759 | 1274680.3171 | 2720317.7566 | 1274672.786
31 | 2720296.8352 | 1274685.2868 | 2720294.2879 | 1274701.7724 | 2720288.869 | 1274707.8787 | 2720287.6832 | 1274708.6835
32 | 2720296.8352 | 1274685.2868 | 2720318.1749 | 1274696.1429
33 | 2720317.7566 | 1274672.786 | 2720319.8441 | 1274671.8321 | 2720326.0048 | 1274669.9536
34 | 2720286.0395 | 1274709.7991 | 2720287.6832 | 1274708.6835
35 | 2720253.5091 | 1274727.9047 | 2720264.7353 | 1274722.2892 | 2720272.8194 | 1274718.2502 | 2720275.7446 | 1274716.7862 | 2720281.3765 | 1274712.9639
36 | 2720290.8359 | 1274853.3094 | 2720265.8502 | 1274812.1732 | 2720258.3786 | 1274797.9855 | 2720250.8387 | 1274780.8716 | 2720249.7764 | 1274777.6077
37 | 2720286.0395 | 1274709.7991 | 2720281.3765 | 1274712.9639
38 | 2720290.8359 | 1274853.3094 | 2720267.9067 | 1274851.8297 | 2720255.6645 | 1274848.1262
39 | 2720290.8359 | 1274853.3094 | 2720310.6801 | 1274880.3055 | 2720326.9752 | 1274896.1793
40 | 2720232.562 | 1274840.3125 | 2720244.3332 | 1274844.6983 | 2720255.6645 | 1274848.1262
41 | 2720326.9752 | 1274896.1793 | 2720508.1499 | 1274978.0246
42 | 2720197.2286 | 1274827.1476 | 2720232.562 | 1274840.3125
43 | 2720508.1499 | 1274978.0246 | 2720533.1434 | 1274974.1425 | 2720541.5969 | 1274974.1039 | 2720549.6324 | 1274976.4814 | 2720562.3336 | 1274986.7948 | 2720566.0316 | 1274988.5753
44 | 2720196.2952 | 1274826.7998 | 2720197.2286 | 1274827.1476
45 | 2720604.2605 | 1274987.0516 | 2720571.5006 | 1274991.2084 | 2720566.0316 | 1274988.5753
46 | 2720406.89 | 1274750.3651 | 2720395.1898 | 1274744.8807 | 2720390.9142 | 1274742.984
47 | 2720390.9142 | 1274742.984 | 2720390.7216 | 1274742.8985
48 | 2720382.6018 | 1274739.2965 | 2720390.7216 | 1274742.8985
49 | 2720382.6018 | 1274739.2965 | 2720363.6966 | 1274730.3112
50 | 2720382.6018 | 1274739.2965 | 2720394.824 | 1274698.0257
51 | 2720396.4139 | 1274692.6571 | 2720399.0848 | 1274679.5761
52 | 2720396.4139 | 1274692.6571 | 2720394.824 | 1274698.0257
53 | 2720357.6877 | 1274727.4553 | 2720357.6877 | 1274727.4553 | 2720363.6966 | 1274730.3112
54 | 2720357.6877 | 1274727.4553 | 2720353.4319 | 1274723.8333
55 | 2720353.4319 | 1274723.8333 | 2720351.2344 | 1274721.963 | 2720351.2344 | 1274721.963
56 | 2720337.3884 | 1274666.4826 | 2720326.0048 | 1274669.9536
57 | 2720337.3884 | 1274666.4826 | 2720340.3901 | 1274665.5674 | 2720341.7815 | 1274665.4692
58 | 2720375.6292 | 1274666.7207 | 2720350.5424 | 1274664.8514 | 2720341.7815 | 1274665.4692

## bus_geodata
| x | y | coords
0 | 2720736.0315 | 1274274.5661
1 | 2720613.7992 | 1274298.8961
2 | 2720628.549 | 1274336.8709
3 | 2720222.4951 | 1274339.2402
4 | 2720401.3188 | 1274668.6349
5 | 2720136.1707 | 1274373.9149
6 | 2720141.5402 | 1274363.1237
7 | 2720134.0052 | 1274393.4556
8 | 2720124.2178 | 1274369.9127
9 | 2720117.7244 | 1274367.7384
10 | 2720113.5368 | 1274366.3362
11 | 2720155.0111 | 1274558.6743
12 | 2720153.6625 | 1274547.4985
13 | 2720133.1488 | 1274545.8906
14 | 2720169.9031 | 1274504.8785
15 | 2720126.2505 | 1274545.9836
16 | 2720131.1112 | 1274571.33
17 | 2720114.5964 | 1274500.8318
18 | 2720210.7269 | 1274652.0239
19 | 2720250.1151 | 1274659.3346
20 | 2720172.2874 | 1274649.8186
21 | 2720092.5894 | 1274601.551
22 | 2720115.2404 | 1274643.4611
23 | 2720277.7545 | 1274674.6877
24 | 2720225.5481 | 1274700.7985
25 | 2720236.3874 | 1274736.4693
26 | 2720296.8352 | 1274685.2868
27 | 2720317.7566 | 1274672.786
28 | 2720287.6832 | 1274708.6835
29 | 2720318.1749 | 1274696.1429
30 | 2720253.5091 | 1274727.9047
31 | 2720249.7764 | 1274777.6077
32 | 2720281.3765 | 1274712.9639
33 | 2720290.8359 | 1274853.3094
34 | 2720286.0395 | 1274709.7991
35 | 2720255.6645 | 1274848.1262
36 | 2720326.9752 | 1274896.1793
37 | 2720232.562 | 1274840.3125
38 | 2720508.1499 | 1274978.0246
39 | 2720196.2952 | 1274826.7998
40 | 2720197.2286 | 1274827.1476
41 | 2720566.0316 | 1274988.5753
42 | 2720604.2605 | 1274987.0516
43 | 2720406.89 | 1274750.3651
44 | 2720390.9142 | 1274742.984
45 | 2720390.7216 | 1274742.8985
46 | 2720382.6018 | 1274739.2965
47 | 2720396.4139 | 1274692.6571
48 | 2720399.0848 | 1274679.5761
49 | 2720394.824 | 1274698.0257
50 | 2720363.6966 | 1274730.3112
51 | 2720357.6877 | 1274727.4552
52 | 2720353.4319 | 1274723.8333
53 | 2720351.2344 | 1274721.963
54 | 2720326.0048 | 1274669.9536
55 | 2720337.3884 | 1274666.4826
56 | 2720341.7815 | 1274665.4692
57 | 2720375.6292 | 1274666.7207
58 | 2720208.7433 | 1274385.5364
59 | 2720147.7846 | 1274350.5741
60 | 2720210.7269 | 1274652.0239

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1