## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_552-13_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_552-13_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_552-13_0_3_node_94 | 0.4 | n |  | TRUE
3 | bus_LV_552-13_0_3_node_95 | 0.4 | n |  | TRUE
4 | bus_LV_552-13_0_3_node_93 | 0.4 | n |  | TRUE
5 | bus_LV_552-13_0_3_node_3 | 0.4 | n |  | TRUE
6 | bus_LV_552-13_0_3_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_552-13_0_3_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_552-13_0_3_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_552-13_0_3_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_552-13_0_3_node_10 | 0.4 | n |  | TRUE
11 | bus_LV_552-13_0_3_node_21 | 0.4 | n |  | TRUE
12 | bus_LV_552-13_0_3_node_39 | 0.4 | n |  | TRUE
13 | bus_LV_552-13_0_3_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_552-13_0_3_node_20 | 0.4 | n |  | TRUE
15 | bus_LV_552-13_0_3_node_37 | 0.4 | n |  | TRUE
16 | bus_LV_552-13_0_3_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_552-13_0_3_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_552-13_0_3_node_16 | 0.4 | n |  | TRUE
19 | bus_LV_552-13_0_3_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_552-13_0_3_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_552-13_0_3_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_552-13_0_3_node_17 | 0.4 | n |  | TRUE
23 | bus_LV_552-13_0_3_node_18 | 0.4 | n |  | TRUE
24 | bus_LV_552-13_0_3_node_19 | 0.4 | n |  | TRUE
25 | bus_LV_552-13_0_3_node_22 | 0.4 | n |  | TRUE
26 | bus_LV_552-13_0_3_node_23 | 0.4 | n |  | TRUE
27 | bus_LV_552-13_0_3_node_24 | 0.4 | n |  | TRUE
28 | bus_LV_552-13_0_3_node_25 | 0.4 | n |  | TRUE
29 | bus_LV_552-13_0_3_node_103 | 0.4 | n |  | TRUE
30 | bus_LV_552-13_0_3_node_26 | 0.4 | n |  | TRUE
31 | bus_LV_552-13_0_3_node_83 | 0.4 | n |  | TRUE
32 | bus_LV_552-13_0_3_node_27 | 0.4 | n |  | TRUE
33 | bus_LV_552-13_0_3_node_80 | 0.4 | n |  | TRUE
34 | bus_LV_552-13_0_3_node_81 | 0.4 | n |  | TRUE
35 | bus_LV_552-13_0_3_node_28 | 0.4 | n |  | TRUE
36 | bus_LV_552-13_0_3_node_29 | 0.4 | n |  | TRUE
37 | bus_LV_552-13_0_3_node_30 | 0.4 | n |  | TRUE
38 | bus_LV_552-13_0_3_node_31 | 0.4 | n |  | TRUE
39 | bus_LV_552-13_0_3_node_32 | 0.4 | n |  | TRUE
40 | bus_LV_552-13_0_3_node_33 | 0.4 | n |  | TRUE
41 | bus_LV_552-13_0_3_node_56 | 0.4 | n |  | TRUE
42 | bus_LV_552-13_0_3_node_44 | 0.4 | n |  | TRUE
43 | bus_LV_552-13_0_3_node_78 | 0.4 | n |  | TRUE
44 | bus_LV_552-13_0_3_node_55 | 0.4 | n |  | TRUE
45 | bus_LV_552-13_0_3_node_46 | 0.4 | n |  | TRUE
46 | bus_LV_552-13_0_3_node_42 | 0.4 | n |  | TRUE
47 | bus_LV_552-13_0_3_node_79 | 0.4 | n |  | TRUE
48 | bus_LV_552-13_0_3_node_34 | 0.4 | n |  | TRUE
49 | bus_LV_552-13_0_3_node_35 | 0.4 | n |  | TRUE
50 | bus_LV_552-13_0_3_node_36 | 0.4 | n |  | TRUE
51 | bus_LV_552-13_0_3_node_105 | 0.4 | n |  | TRUE
52 | bus_LV_552-13_0_3_node_104 | 0.4 | n |  | TRUE
53 | bus_LV_552-13_0_3_node_38 | 0.4 | n |  | TRUE
54 | bus_LV_552-13_0_3_node_40 | 0.4 | n |  | TRUE
55 | bus_LV_552-13_0_3_node_41 | 0.4 | n |  | TRUE
56 | bus_LV_552-13_0_3_node_43 | 0.4 | n |  | TRUE
57 | bus_LV_552-13_0_3_node_45 | 0.4 | n |  | TRUE
58 | bus_LV_552-13_0_3_node_75 | 0.4 | n |  | TRUE
59 | bus_LV_552-13_0_3_node_49 | 0.4 | n |  | TRUE
60 | bus_LV_552-13_0_3_node_76 | 0.4 | n |  | TRUE
61 | bus_LV_552-13_0_3_node_98 | 0.4 | n |  | TRUE
62 | bus_LV_552-13_0_3_node_74 | 0.4 | n |  | TRUE
63 | bus_LV_552-13_0_3_node_47 | 0.4 | n |  | TRUE
64 | bus_LV_552-13_0_3_node_77 | 0.4 | n |  | TRUE
65 | bus_LV_552-13_0_3_node_48 | 0.4 | n |  | TRUE
66 | bus_LV_552-13_0_3_node_50 | 0.4 | n |  | TRUE
67 | bus_LV_552-13_0_3_node_51 | 0.4 | n |  | TRUE
68 | bus_LV_552-13_0_3_node_52 | 0.4 | n |  | TRUE
69 | bus_LV_552-13_0_3_node_53 | 0.4 | n |  | TRUE
70 | bus_LV_552-13_0_3_node_54 | 0.4 | n |  | TRUE
71 | bus_LV_552-13_0_3_node_57 | 0.4 | n |  | TRUE
72 | bus_LV_552-13_0_3_node_58 | 0.4 | n |  | TRUE
73 | bus_LV_552-13_0_3_node_59 | 0.4 | n |  | TRUE
74 | bus_LV_552-13_0_3_node_60 | 0.4 | n |  | TRUE
75 | bus_LV_552-13_0_3_node_61 | 0.4 | n |  | TRUE
76 | bus_LV_552-13_0_3_node_62 | 0.4 | n |  | TRUE
77 | bus_LV_552-13_0_3_node_64 | 0.4 | n |  | TRUE
78 | bus_LV_552-13_0_3_node_66 | 0.4 | n |  | TRUE
79 | bus_LV_552-13_0_3_node_63 | 0.4 | n |  | TRUE
80 | bus_LV_552-13_0_3_node_67 | 0.4 | n |  | TRUE
81 | bus_LV_552-13_0_3_node_68 | 0.4 | n |  | TRUE
82 | bus_LV_552-13_0_3_node_69 | 0.4 | n |  | TRUE
83 | bus_LV_552-13_0_3_node_70 | 0.4 | n |  | TRUE
84 | bus_LV_552-13_0_3_node_71 | 0.4 | n |  | TRUE
85 | bus_LV_552-13_0_3_node_72 | 0.4 | n |  | TRUE
86 | bus_LV_552-13_0_3_node_73 | 0.4 | n |  | TRUE
87 | bus_LV_552-13_0_3_node_101 | 0.4 | n |  | TRUE
88 | bus_LV_552-13_0_3_node_102 | 0.4 | n |  | TRUE
89 | bus_LV_552-13_0_3_node_99 | 0.4 | n |  | TRUE
90 | bus_LV_552-13_0_3_node_82 | 0.4 | n |  | TRUE
91 | bus_LV_552-13_0_3_node_84 | 0.4 | n |  | TRUE
92 | bus_LV_552-13_0_3_node_85 | 0.4 | n |  | TRUE
93 | bus_LV_552-13_0_3_node_86 | 0.4 | n |  | TRUE
94 | bus_LV_552-13_0_3_node_87 | 0.4 | n |  | TRUE
95 | bus_LV_552-13_0_3_node_88 | 0.4 | n |  | TRUE
96 | bus_LV_552-13_0_3_node_91 | 0.4 | n |  | TRUE
97 | bus_LV_552-13_0_3_node_89 | 0.4 | n |  | TRUE
98 | bus_LV_552-13_0_3_node_90 | 0.4 | n |  | TRUE
99 | bus_LV_552-13_0_3_node_92 | 0.4 | n |  | TRUE
100 | bus_LV_552-13_0_3_node_96 | 0.4 | n |  | TRUE
101 | bus_LV_552-13_0_3_node_97 | 0.4 | n |  | TRUE
102 | bus_LV_552-13_0_3_node_100 | 0.4 | n |  | TRUE
103 | bus_MV_386_1_node_111 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_552-13_0_3_load_0 | 0 | 0.0013247 | 0.000332 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_552-13_0_3_load_1 | 1 | 0.0045888 | 0.0011501 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_552-13_0_3_load_95 | 3 | 0.0020507 | 0.00051394 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_552-13_0_3_load_93 | 4 | 0.002961 | 0.0007421 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_552-13_0_3_load_3 | 5 | 0.0033663 | 0.00084366 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_552-13_0_3_load_4 | 6 | 0.0020588 | 0.00051599 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_552-13_0_3_load_8 | 9 | 0.0032294 | 0.00080936 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_552-13_0_3_load_10 | 10 | 0.0013346 | 0.00033448 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_552-13_0_3_load_21 | 11 | 0.001286 | 0.0003223 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_552-13_0_3_load_39 | 12 | 0.0025173 | 0.00063089 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_552-13_0_3_load_9 | 13 | 0.0029653 | 0.00074318 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_552-13_0_3_load_20 | 14 | 0.0020796 | 0.0005212 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_552-13_0_3_load_37 | 15 | 0.00055931 | 0.00014018 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_552-13_0_3_load_11 | 16 | 0.0027516 | 0.00068963 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_552-13_0_3_load_16 | 18 | 0.011447 | 0.0028689 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_552-13_0_3_load_13 | 19 | 0.0027082 | 0.00067875 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_552-13_0_3_load_14 | 20 | 0.0024685 | 0.00061867 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_552-13_0_3_load_15 | 21 | 0.0013518 | 0.00033878 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_552-13_0_3_load_17 | 22 | 0.0012354 | 0.00030961 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_552-13_0_3_load_18 | 23 | 0.0010371 | 0.00025993 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_552-13_0_3_load_19 | 24 | 0.0042662 | 0.0010692 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_552-13_0_3_load_22 | 25 | 0.0020018 | 0.00050169 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_552-13_0_3_load_24 | 27 | 0.0016747 | 0.00041973 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_552-13_0_3_load_25 | 28 | 0.002555 | 0.00064035 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_552-13_0_3_load_103 | 29 | 0.0024835 | 0.00062242 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_552-13_0_3_load_26 | 30 | 0.0027683 | 0.0006938 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_552-13_0_3_load_27 | 32 | 0.0023594 | 0.00059131 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_552-13_0_3_load_80 | 33 | 0.0021853 | 0.0005477 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_552-13_0_3_load_81 | 34 | 0.0027912 | 0.00069955 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_552-13_0_3_load_28 | 35 | 0.0031205 | 0.00078207 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_552-13_0_3_load_29 | 36 | 0.0033005 | 0.00082718 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_552-13_0_3_load_31 | 38 | 0.00089363 | 0.00022396 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_552-13_0_3_load_32 | 39 | 0.0013496 | 0.00033825 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_552-13_0_3_load_33 | 40 | 0.0036679 | 0.00091927 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_552-13_0_3_load_56 | 41 | 0.0037081 | 0.00092935 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_552-13_0_3_load_78 | 43 | 0.0030309 | 0.00075961 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_552-13_0_3_load_55 | 44 | 0.0013792 | 0.00034565 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_552-13_0_3_load_46 | 45 | 0.0024068 | 0.0006032 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_552-13_0_3_load_42 | 46 | 0.0023412 | 0.00058677 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_552-13_0_3_load_79 | 47 | 0.0029034 | 0.00072766 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_552-13_0_3_load_34 | 48 | 0.0018708 | 0.00046885 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_552-13_0_3_load_35 | 49 | 0.0033005 | 0.00082719 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_552-13_0_3_load_36 | 50 | 0.0034648 | 0.00086837 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_552-13_0_3_load_105 | 51 | 0.0038366 | 0.00096154 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_552-13_0_3_load_104 | 52 | 0.0020845 | 0.00052242 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_552-13_0_3_load_38 | 53 | 0.00062041 | 0.00015549 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_552-13_0_3_load_40 | 54 | 0.0018809 | 0.00047139 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_552-13_0_3_load_41 | 55 | 0.0018971 | 0.00047546 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_552-13_0_3_load_43 | 56 | 0.0028847 | 0.00072298 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_552-13_0_3_load_49 | 59 | 0.0014498 | 0.00036334 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_552-13_0_3_load_76 | 60 | 0.0014594 | 0.00036577 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_552-13_0_3_load_98 | 61 | 0.0016248 | 0.00040722 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_552-13_0_3_load_74 | 62 | 0.0024037 | 0.00060243 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_552-13_0_3_load_47 | 63 | 0.0022446 | 0.00056255 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_552-13_0_3_load_77 | 64 | 0.0025588 | 0.00064129 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_552-13_0_3_load_48 | 65 | 0.001338 | 0.00033534 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_552-13_0_3_load_50 | 66 | 0.00067806 | 0.00016994 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_552-13_0_3_load_51 | 67 | 0.0014347 | 0.00035958 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_552-13_0_3_load_52 | 68 | 0.0012701 | 0.00031832 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_552-13_0_3_load_53 | 69 | 0.0015135 | 0.00037932 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_552-13_0_3_load_54 | 70 | 0.0018754 | 0.00047003 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_552-13_0_3_load_57 | 71 | 0.001397 | 0.00035011 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_552-13_0_3_load_58 | 72 | 0.0020346 | 0.00050992 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_552-13_0_3_load_59 | 73 | 0.0028703 | 0.00071937 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_552-13_0_3_load_60 | 74 | 0.0017859 | 0.0004476 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_552-13_0_3_load_61 | 75 | 0.0032689 | 0.00081927 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_552-13_0_3_load_64 | 77 | 0.0017051 | 0.00042734 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_552-13_0_3_load_66 | 78 | 0.0016758 | 0.00041999 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_552-13_0_3_load_63 | 79 | 0.0014681 | 0.00036794 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_552-13_0_3_load_67 | 80 | 0.0013621 | 0.00034139 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_552-13_0_3_load_68 | 81 | 0.0018331 | 0.00045941 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_552-13_0_3_load_69 | 82 | 0.0021643 | 0.00054241 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_552-13_0_3_load_71 | 84 | 0.0013182 | 0.00033038 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_552-13_0_3_load_72 | 85 | 0.0028792 | 0.0007216 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_552-13_0_3_load_73 | 86 | 0.0021941 | 0.0005499 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_552-13_0_3_load_101 | 87 | 0.0013589 | 0.00034057 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_552-13_0_3_load_102 | 88 | 0.0012773 | 0.00032012 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_552-13_0_3_load_99 | 89 | 0.0010473 | 0.00026247 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_552-13_0_3_load_84 | 91 | 0.0031833 | 0.0007978 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_552-13_0_3_load_85 | 92 | 0.0023791 | 0.00059626 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_552-13_0_3_load_86 | 93 | 0.0035083 | 0.00087927 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_552-13_0_3_load_87 | 94 | 0.0030328 | 0.0007601 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_552-13_0_3_load_88 | 95 | 0.0026683 | 0.00066873 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_552-13_0_3_load_91 | 96 | 0.0022777 | 0.00057085 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_552-13_0_3_load_89 | 97 | 0.0017889 | 0.00044834 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_552-13_0_3_load_90 | 98 | 0.0023648 | 0.00059268 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_552-13_0_3_load_96 | 100 | 0.0020976 | 0.00052572 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_552-13_0_3_load_97 | 101 | 0.0012092 | 0.00030305 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_552-13_0_3_load_100 | 102 | 0.002039 | 0.00051103 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 43 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_552-13_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.013184 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_552-13_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.26608 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_552-13_0_3_line_2 | NAYY 4x150 SE | 2 | 3 | 0.033751 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_552-13_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.012979 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_552-13_0_3_line_4 | NAYY 4x150 SE | 3 | 99 | 0.012317 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_552-13_0_3_line_5 | NAYY 4x150 SE | 4 | 78 | 0.022706 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_552-13_0_3_line_6 | NAYY 4x150 SE | 5 | 6 | 0.013481 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_552-13_0_3_line_7 | NAYY 4x150 SE | 5 | 7 | 0.036857 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_552-13_0_3_line_8 | NAYY 4x150 SE | 7 | 8 | 0.009104 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_552-13_0_3_line_9 | NAYY 4x150 SE | 7 | 9 | 0.031035 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_552-13_0_3_line_10 | NAYY 4x150 SE | 8 | 10 | 0.015946 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_552-13_0_3_line_11 | NAYY 4x150 SE | 8 | 11 | 0.011529 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_552-13_0_3_line_12 | NAYY 4x150 SE | 9 | 12 | 0.030864 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_552-13_0_3_line_13 | NAYY 4x150 SE | 10 | 13 | 0.022202 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_552-13_0_3_line_14 | NAYY 4x150 SE | 11 | 14 | 0.002737 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_552-13_0_3_line_15 | NAYY 4x150 SE | 12 | 15 | 0.015391 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_552-13_0_3_line_16 | NAYY 4x150 SE | 13 | 16 | 0.020756 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_552-13_0_3_line_17 | NAYY 4x150 SE | 14 | 25 | 0.01114 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_552-13_0_3_line_18 | NAYY 4x150 SE | 15 | 53 | 2.8591e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_552-13_0_3_line_19 | NAYY 4x150 SE | 16 | 17 | 0.011274 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_552-13_0_3_line_20 | NAYY 4x150 SE | 17 | 18 | 0.030305 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_552-13_0_3_line_21 | NAYY 4x150 SE | 17 | 19 | 0.011716 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_552-13_0_3_line_22 | NAYY 4x150 SE | 19 | 20 | 0.0044065 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_552-13_0_3_line_23 | NAYY 4x150 SE | 20 | 21 | 0.01461 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_552-13_0_3_line_24 | NAYY 4x150 SE | 21 | 22 | 0.0058984 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_552-13_0_3_line_25 | NAYY 4x150 SE | 22 | 23 | 0.0032904 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_552-13_0_3_line_26 | NAYY 4x150 SE | 23 | 24 | 0.0076586 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_552-13_0_3_line_27 | NAYY 4x150 SE | 25 | 26 | 0.024981 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_552-13_0_3_line_28 | NAYY 4x150 SE | 25 | 27 | 0.013254 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_552-13_0_3_line_29 | NAYY 4x150 SE | 26 | 28 | 0.004633 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_552-13_0_3_line_30 | NAYY 4x150 SE | 27 | 29 | 0.010488 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_552-13_0_3_line_31 | NAYY 4x150 SE | 28 | 30 | 0.018381 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_552-13_0_3_line_32 | NAYY 4x150 SE | 29 | 31 | 0.011282 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_552-13_0_3_line_33 | NAYY 4x150 SE | 30 | 32 | 0.012 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_552-13_0_3_line_34 | NAYY 4x150 SE | 31 | 90 | 0.011487 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_552-13_0_3_line_35 | NAYY 4x150 SE | 32 | 33 | 0.0023183 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_552-13_0_3_line_36 | NAYY 4x150 SE | 33 | 34 | 0.017627 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_552-13_0_3_line_37 | NAYY 4x150 SE | 35 | 36 | 0.0077311 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_552-13_0_3_line_38 | NAYY 4x150 SE | 35 | 37 | 0.027365 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_552-13_0_3_line_39 | NAYY 4x150 SE | 36 | 38 | 0.020534 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_552-13_0_3_line_40 | NAYY 4x150 SE | 37 | 39 | 0.027034 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_552-13_0_3_line_41 | NAYY 4x150 SE | 37 | 40 | 0.0052419 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_552-13_0_3_line_42 | NAYY 4x150 SE | 38 | 41 | 0.0074084 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_552-13_0_3_line_43 | NAYY 4x150 SE | 39 | 42 | 0.0018146 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_552-13_0_3_line_44 | NAYY 4x150 SE | 40 | 43 | 0.038616 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_552-13_0_3_line_45 | NAYY 4x150 SE | 41 | 44 | 0.023542 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_552-13_0_3_line_46 | NAYY 4x150 SE | 42 | 45 | 0.011545 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_552-13_0_3_line_47 | NAYY 4x150 SE | 42 | 46 | 0.023722 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_552-13_0_3_line_48 | NAYY 4x150 SE | 43 | 47 | 0.011082 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
49 | LV_552-13_0_3_line_49 | NAYY 4x150 SE | 44 | 71 | 0.0059689 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_552-13_0_3_line_50 | NAYY 4x150 SE | 45 | 60 | 0.012994 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_552-13_0_3_line_51 | NAYY 4x150 SE | 46 | 56 | 0.0059351 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_552-13_0_3_line_52 | NAYY 4x150 SE | 47 | 90 | 0.019142 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
53 | LV_552-13_0_3_line_53 | NAYY 4x150 SE | 48 | 49 | 0.024248 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_552-13_0_3_line_54 | NAYY 4x150 SE | 49 | 50 | 0.010903 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_552-13_0_3_line_55 | NAYY 4x150 SE | 50 | 51 | 0.040535 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_552-13_0_3_line_56 | NAYY 4x150 SE | 51 | 52 | 0.038387 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_552-13_0_3_line_57 | NAYY 4x150 SE | 52 | 55 | 0.032539 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_552-13_0_3_line_58 | NAYY 4x150 SE | 53 | 54 | 0.024358 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_552-13_0_3_line_59 | NAYY 4x150 SE | 54 | 55 | 0.00082022 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_552-13_0_3_line_60 | NAYY 4x150 SE | 56 | 57 | 0.012487 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_552-13_0_3_line_61 | NAYY 4x150 SE | 57 | 58 | 0.002902 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_552-13_0_3_line_62 | NAYY 4x150 SE | 57 | 59 | 0.029762 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_552-13_0_3_line_63 | NAYY 4x150 SE | 58 | 61 | 0.013446 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_552-13_0_3_line_64 | NAYY 4x150 SE | 58 | 62 | 0.023848 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_552-13_0_3_line_65 | NAYY 4x150 SE | 59 | 63 | 0.0067624 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_552-13_0_3_line_66 | NAYY 4x150 SE | 60 | 64 | 0.008183 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_552-13_0_3_line_67 | NAYY 4x150 SE | 61 | 89 | 0.0039054 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_552-13_0_3_line_68 | NAYY 4x150 SE | 62 | 85 | 0.0054544 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_552-13_0_3_line_69 | NAYY 4x150 SE | 63 | 65 | 0.021936 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_552-13_0_3_line_70 | NAYY 4x150 SE | 65 | 66 | 0.016067 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_552-13_0_3_line_71 | NAYY 4x150 SE | 66 | 67 | 0.0061321 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_552-13_0_3_line_72 | NAYY 4x150 SE | 67 | 68 | 0.022316 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_552-13_0_3_line_73 | NAYY 4x150 SE | 68 | 69 | 0.021241 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_552-13_0_3_line_74 | NAYY 4x150 SE | 69 | 70 | 0.023457 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_552-13_0_3_line_75 | NAYY 4x150 SE | 71 | 72 | 0.02032 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_552-13_0_3_line_76 | NAYY 4x150 SE | 72 | 73 | 0.011478 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_552-13_0_3_line_77 | NAYY 4x150 SE | 73 | 74 | 0.016997 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_552-13_0_3_line_78 | NAYY 4x150 SE | 74 | 75 | 0.015186 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_552-13_0_3_line_79 | NAYY 4x150 SE | 75 | 76 | 0.019793 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_552-13_0_3_line_80 | NAYY 4x150 SE | 76 | 77 | 0.018263 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_552-13_0_3_line_81 | NAYY 4x150 SE | 77 | 79 | 0.02956 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_552-13_0_3_line_82 | NAYY 4x150 SE | 80 | 81 | 0.02004 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_552-13_0_3_line_83 | NAYY 4x150 SE | 80 | 82 | 0.013488 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_552-13_0_3_line_84 | NAYY 4x150 SE | 81 | 83 | 0.0049357 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_552-13_0_3_line_85 | NAYY 4x150 SE | 82 | 84 | 0.0043937 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_552-13_0_3_line_86 | NAYY 4x150 SE | 83 | 85 | 0.016441 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_552-13_0_3_line_87 | NAYY 4x150 SE | 83 | 86 | 0.018824 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_552-13_0_3_line_88 | NAYY 4x150 SE | 84 | 87 | 0.040496 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_552-13_0_3_line_89 | NAYY 4x150 SE | 86 | 88 | 0.019002 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_552-13_0_3_line_90 | NAYY 4x150 SE | 89 | 102 | 0.022661 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_552-13_0_3_line_91 | NAYY 4x150 SE | 90 | 91 | 0.0035742 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_552-13_0_3_line_92 | NAYY 4x150 SE | 91 | 92 | 0.014563 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_552-13_0_3_line_93 | NAYY 4x150 SE | 92 | 93 | 0.019118 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_552-13_0_3_line_94 | NAYY 4x150 SE | 93 | 94 | 0.0030445 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_552-13_0_3_line_95 | NAYY 4x150 SE | 94 | 95 | 0.00035885 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_552-13_0_3_line_96 | NAYY 4x150 SE | 95 | 96 | 0.020759 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_552-13_0_3_line_97 | NAYY 4x150 SE | 96 | 97 | 0.0018146 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_552-13_0_3_line_98 | NAYY 4x150 SE | 97 | 98 | 0.021464 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_552-13_0_3_line_99 | NAYY 4x150 SE | 98 | 99 | 0.030105 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_552-13_0_3_line_100 | NAYY 4x150 SE | 99 | 100 | 0.022891 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_552-13_0_3_line_101 | NAYY 4x150 SE | 100 | 101 | 0.013207 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_552-13_0_3_trafo_78 | 0.25 MVA 20/0.4 kV | 103 | 43 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2
0 | 2609639.1136 | 1219974.7268 | 2609635.4884 | 1219962.0507
1 | 2609414.6098 | 1220117.5469 | 2609639.1136 | 1219974.7268
2 | 2609414.6098 | 1220117.5469 | 2609380.8616 | 1220117.1213
3 | 2609414.6098 | 1220117.5469 | 2609416.0563 | 1220130.4455
4 | 2609368.5505 | 1220116.7966 | 2609374.339 | 1220117.0391 | 2609380.8616 | 1220117.1213
5 | 2609418.5869 | 1220153.0102 | 2609416.0563 | 1220130.4455
6 | 2609138.2333 | 1220086.4601 | 2609135.4576 | 1220086.1417 | 2609125.3061 | 1220082.8004
7 | 2609174.85 | 1220090.66 | 2609138.2333 | 1220086.4601
8 | 2609174.85 | 1220090.66 | 2609183.7999 | 1220092.4636
9 | 2609174.85 | 1220090.66 | 2609178.355 | 1220059.824
10 | 2609183.7999 | 1220092.4636 | 2609180.5643 | 1220108.0777
11 | 2609183.7999 | 1220092.4636 | 2609195.3154 | 1220093.016
12 | 2609181.8407 | 1220029.1576 | 2609178.355 | 1220059.824
13 | 2609176.0594 | 1220129.8178 | 2609180.5643 | 1220108.0777
14 | 2609198.0492 | 1220093.1472 | 2609195.3154 | 1220093.016
15 | 2609197.2009 | 1220030.1358 | 2609181.8407 | 1220029.1576 | 2609181.8407 | 1220029.1576
16 | 2609171.8478 | 1220150.1417 | 2609176.0594 | 1220129.8178
17 | 2609209.1765 | 1220093.681 | 2609198.0492 | 1220093.1472
18 | 2609197.2294 | 1220030.1376 | 2609197.2009 | 1220030.1358
19 | 2609169.5602 | 1220161.1813 | 2609171.8478 | 1220150.1417
20 | 2609169.5602 | 1220161.1813 | 2609139.4465 | 1220157.0774
21 | 2609169.5602 | 1220161.1813 | 2609167.7167 | 1220172.7514
22 | 2609167.7167 | 1220172.7514 | 2609167.0234 | 1220177.103
23 | 2609167.0234 | 1220177.103 | 2609164.7245 | 1220191.5311
24 | 2609163.7964 | 1220197.356 | 2609164.7245 | 1220191.5311
25 | 2609163.7964 | 1220197.356 | 2609163.2787 | 1220200.6054
26 | 2609170.9101 | 1220201.2508 | 2609163.2787 | 1220200.6054
27 | 2609205.9216 | 1220118.4457 | 2609209.1765 | 1220093.681
28 | 2609209.1765 | 1220093.681 | 2609222.4157 | 1220094.3121
29 | 2609205.9216 | 1220118.4457 | 2609205.5052 | 1220123.0599
30 | 2609232.8923 | 1220094.8116 | 2609222.4157 | 1220094.3121
31 | 2609205.5052 | 1220123.0599 | 2609203.8531 | 1220141.3668 | 2609203.8531 | 1220141.3668
32 | 2609244.119 | 1220095.7025 | 2609241.7071 | 1220095.2319 | 2609232.8923 | 1220094.8116
33 | 2609215.6978 | 1220143.2936 | 2609203.8531 | 1220141.3668
34 | 2609255.6043 | 1220096.5985 | 2609244.119 | 1220095.7025
35 | 2609217.986 | 1220143.6659 | 2609215.6978 | 1220143.2936
36 | 2609235.384 | 1220146.496 | 2609217.986 | 1220143.6659
37 | 2609276.0694 | 1220173.5589 | 2609283.748 | 1220174.4584
38 | 2609248.8899 | 1220170.375 | 2609276.0694 | 1220173.5589
39 | 2609283.748 | 1220174.4584 | 2609304.1426 | 1220176.8474
40 | 2609248.8899 | 1220170.375 | 2609246.4879 | 1220197.3023
41 | 2609248.8899 | 1220170.375 | 2609249.365 | 1220165.1546
42 | 2609311.5006 | 1220177.7094 | 2609304.1426 | 1220176.8474
43 | 2609246.3267 | 1220199.1098 | 2609246.4879 | 1220197.3023
44 | 2609249.365 | 1220165.1546 | 2609252.865 | 1220126.6973
45 | 2609334.7471 | 1220181.4284 | 2609311.5006 | 1220177.7094 | 2609311.5006 | 1220177.7094
46 | 2609246.3267 | 1220199.1098 | 2609234.8289 | 1220198.0683
47 | 2609246.3267 | 1220199.1098 | 2609248.3252 | 1220211.7868 | 2609247.2967 | 1220222.6264
48 | 2609253.8694 | 1220115.6613 | 2609252.865 | 1220126.6973
49 | 2609334.7471 | 1220181.4284 | 2609340.6411 | 1220182.3713
50 | 2609221.8877 | 1220196.8961 | 2609234.8289 | 1220198.0683
51 | 2609247.2967 | 1220222.6264 | 2609246.7361 | 1220228.5349
52 | 2609255.6043 | 1220096.5985 | 2609253.8694 | 1220115.6613
53 | 2609189.7649 | 1219981.6409 | 2609213.9164 | 1219983.8034
54 | 2609224.776 | 1219984.7757 | 2609213.9164 | 1219983.8034
55 | 2609224.776 | 1219984.7757 | 2609259.1116 | 1220006.3191
56 | 2609252.4463 | 1220044.1229 | 2609259.1116 | 1220006.3191
57 | 2609222.3565 | 1220031.7379 | 2609252.4463 | 1220044.1229
58 | 2609197.2294 | 1220030.1376 | 2609221.5379 | 1220031.6858
59 | 2609222.3565 | 1220031.7379 | 2609221.5379 | 1220031.6858
60 | 2609245.5566 | 1220240.966 | 2609246.7361 | 1220228.5349
61 | 2609245.5566 | 1220240.966 | 2609245.2942 | 1220243.8561
62 | 2609245.5566 | 1220240.966 | 2609275.1131 | 1220244.4538
63 | 2609245.2942 | 1220243.8561 | 2609242.17 | 1220256.9339
64 | 2609245.2942 | 1220243.8561 | 2609221.481 | 1220242.5675
65 | 2609281.8289 | 1220245.2463 | 2609275.1131 | 1220244.4538
66 | 2609213.7381 | 1220196.1579 | 2609221.8877 | 1220196.8961
67 | 2609242.17 | 1220256.9339 | 2609241.2625 | 1220260.7324
68 | 2609216.0346 | 1220242.2728 | 2609221.481 | 1220242.5675
69 | 2609281.8289 | 1220245.2463 | 2609303.6134 | 1220247.817
70 | 2609303.6134 | 1220247.817 | 2609319.5696 | 1220249.6999
71 | 2609325.6594 | 1220250.4186 | 2609319.5696 | 1220249.6999
72 | 2609325.6594 | 1220250.4186 | 2609347.8221 | 1220253.0339
73 | 2609347.8221 | 1220253.0339 | 2609368.9165 | 1220255.5231
74 | 2609368.9165 | 1220255.5231 | 2609392.212 | 1220258.2721
75 | 2609360.7059 | 1220185.5813 | 2609340.6411 | 1220182.3713
76 | 2609360.7059 | 1220185.5813 | 2609372.04 | 1220187.3946
77 | 2609388.8236 | 1220190.0797 | 2609372.04 | 1220187.3946
78 | 2609388.8236 | 1220190.0797 | 2609403.8192 | 1220192.4787
79 | 2609423.3638 | 1220195.6055 | 2609403.8192 | 1220192.4787
80 | 2609423.3638 | 1220195.6055 | 2609425.2637 | 1220213.7694
81 | 2609428.3389 | 1220243.1695 | 2609425.2637 | 1220213.7694
82 | 2609174.6793 | 1220240.0311 | 2609194.6894 | 1220241.117
83 | 2609174.6793 | 1220240.0311 | 2609161.2115 | 1220239.3002
84 | 2609199.6179 | 1220241.3845 | 2609194.6894 | 1220241.117
85 | 2609156.8243 | 1220239.0621 | 2609161.2115 | 1220239.3002
86 | 2609199.6179 | 1220241.3845 | 2609216.0346 | 1220242.2728
87 | 2609199.6179 | 1220241.3845 | 2609197.55 | 1220260.0943
88 | 2609156.8243 | 1220239.0621 | 2609143.9067 | 1220277.4427
89 | 2609195.4626 | 1220278.9814 | 2609197.55 | 1220260.0943
90 | 2609241.2625 | 1220260.7324 | 2609235.9971 | 1220282.7734
91 | 2609255.6043 | 1220096.5985 | 2609259.1177 | 1220097.2555
92 | 2609273.4321 | 1220099.9321 | 2609259.1177 | 1220097.2555
93 | 2609273.4321 | 1220099.9321 | 2609292.2244 | 1220103.4461
94 | 2609292.2244 | 1220103.4461 | 2609295.217 | 1220104.0056
95 | 2609295.5698 | 1220104.0716 | 2609295.217 | 1220104.0056
96 | 2609295.5698 | 1220104.0716 | 2609315.9748 | 1220107.8871
97 | 2609317.7585 | 1220108.2206 | 2609315.9748 | 1220107.8871
98 | 2609317.7585 | 1220108.2206 | 2609338.8566 | 1220112.1657
99 | 2609368.5505 | 1220116.7966 | 2609362.2614 | 1220116.5422 | 2609338.8566 | 1220112.1657
100 | 2609368.5505 | 1220116.7966 | 2609372.268 | 1220139.3838
101 | 2609374.4127 | 1220152.4151 | 2609372.268 | 1220139.3838

## bus_geodata
| x | y | coords
0 | 2609639.1136 | 1219974.7268
1 | 2609635.4884 | 1219962.0507
2 | 2609414.6098 | 1220117.5469
3 | 2609380.8616 | 1220117.1213
4 | 2609416.0563 | 1220130.4455
5 | 2609138.2333 | 1220086.4601
6 | 2609125.3061 | 1220082.8004
7 | 2609174.85 | 1220090.66
8 | 2609183.7999 | 1220092.4636
9 | 2609178.355 | 1220059.824
10 | 2609180.5643 | 1220108.0777
11 | 2609195.3154 | 1220093.016
12 | 2609181.8407 | 1220029.1576
13 | 2609176.0594 | 1220129.8178
14 | 2609198.0492 | 1220093.1472
15 | 2609197.2009 | 1220030.1358
16 | 2609171.8478 | 1220150.1417
17 | 2609169.5602 | 1220161.1813
18 | 2609139.4465 | 1220157.0774
19 | 2609167.7167 | 1220172.7514
20 | 2609167.0234 | 1220177.103
21 | 2609164.7245 | 1220191.5311
22 | 2609163.7964 | 1220197.356
23 | 2609163.2787 | 1220200.6054
24 | 2609170.9101 | 1220201.2508
25 | 2609209.1765 | 1220093.681
26 | 2609205.9216 | 1220118.4457
27 | 2609222.4157 | 1220094.3121
28 | 2609205.5052 | 1220123.06
29 | 2609232.8923 | 1220094.8116
30 | 2609203.8531 | 1220141.3668
31 | 2609244.119 | 1220095.7025
32 | 2609215.6978 | 1220143.2936
33 | 2609217.986 | 1220143.6659
34 | 2609235.384 | 1220146.496
35 | 2609276.0694 | 1220173.5589
36 | 2609283.748 | 1220174.4584
37 | 2609248.8899 | 1220170.375
38 | 2609304.1426 | 1220176.8474
39 | 2609246.4879 | 1220197.3023
40 | 2609249.365 | 1220165.1546
41 | 2609311.5006 | 1220177.7094
42 | 2609246.3267 | 1220199.1098
43 | 2609252.865 | 1220126.6973
44 | 2609334.7471 | 1220181.4284
45 | 2609234.8289 | 1220198.0683
46 | 2609247.2967 | 1220222.6264
47 | 2609253.8694 | 1220115.6613
48 | 2609189.7649 | 1219981.6409
49 | 2609213.9164 | 1219983.8034
50 | 2609224.776 | 1219984.7757
51 | 2609259.1116 | 1220006.3191
52 | 2609252.4463 | 1220044.1229
53 | 2609197.2294 | 1220030.1376
54 | 2609221.5379 | 1220031.6858
55 | 2609222.3565 | 1220031.7379
56 | 2609246.7361 | 1220228.5349
57 | 2609245.5566 | 1220240.966
58 | 2609245.2942 | 1220243.8561
59 | 2609275.1131 | 1220244.4538
60 | 2609221.8877 | 1220196.8961
61 | 2609242.17 | 1220256.9339
62 | 2609221.481 | 1220242.5675
63 | 2609281.8289 | 1220245.2463
64 | 2609213.7381 | 1220196.1579
65 | 2609303.6134 | 1220247.817
66 | 2609319.5696 | 1220249.6999
67 | 2609325.6594 | 1220250.4186
68 | 2609347.8221 | 1220253.0339
69 | 2609368.9165 | 1220255.5231
70 | 2609392.212 | 1220258.2721
71 | 2609340.6411 | 1220182.3713
72 | 2609360.7059 | 1220185.5813
73 | 2609372.04 | 1220187.3946
74 | 2609388.8236 | 1220190.0797
75 | 2609403.8192 | 1220192.4787
76 | 2609423.3638 | 1220195.6055
77 | 2609425.2637 | 1220213.7694
78 | 2609418.5869 | 1220153.0102
79 | 2609428.3389 | 1220243.1695
80 | 2609174.6793 | 1220240.0311
81 | 2609194.6894 | 1220241.117
82 | 2609161.2115 | 1220239.3002
83 | 2609199.6179 | 1220241.3845
84 | 2609156.8243 | 1220239.0621
85 | 2609216.0346 | 1220242.2728
86 | 2609197.55 | 1220260.0943
87 | 2609143.9067 | 1220277.4427
88 | 2609195.4626 | 1220278.9814
89 | 2609241.2625 | 1220260.7324
90 | 2609255.6043 | 1220096.5985
91 | 2609259.1177 | 1220097.2555
92 | 2609273.4321 | 1220099.9321
93 | 2609292.2244 | 1220103.4461
94 | 2609295.217 | 1220104.0056
95 | 2609295.5698 | 1220104.0716
96 | 2609315.9748 | 1220107.8871
97 | 2609317.7585 | 1220108.2206
98 | 2609338.8566 | 1220112.1657
99 | 2609368.5505 | 1220116.7966
100 | 2609372.268 | 1220139.3838
101 | 2609374.4127 | 1220152.4151
102 | 2609235.9971 | 1220282.7734
103 | 2609255.6043 | 1220096.5985

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1