## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_989-3_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_989-3_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_989-3_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_989-3_0_4_node_5 | 0.4 | n |  | TRUE
4 | bus_LV_989-3_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_989-3_0_4_node_12 | 0.4 | n |  | TRUE
6 | bus_LV_989-3_0_4_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_989-3_0_4_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_989-3_0_4_node_13 | 0.4 | n |  | TRUE
9 | bus_LV_989-3_0_4_node_11 | 0.4 | n |  | TRUE
10 | bus_LV_989-3_0_4_node_63 | 0.4 | n |  | TRUE
11 | bus_LV_989-3_0_4_node_17 | 0.4 | n |  | TRUE
12 | bus_LV_989-3_0_4_node_21 | 0.4 | n |  | TRUE
13 | bus_LV_989-3_0_4_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_989-3_0_4_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_989-3_0_4_node_61 | 0.4 | n |  | TRUE
16 | bus_LV_989-3_0_4_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_989-3_0_4_node_73 | 0.4 | n |  | TRUE
18 | bus_LV_989-3_0_4_node_22 | 0.4 | n |  | TRUE
19 | bus_LV_989-3_0_4_node_74 | 0.4 | n |  | TRUE
20 | bus_LV_989-3_0_4_node_20 | 0.4 | n |  | TRUE
21 | bus_LV_989-3_0_4_node_28 | 0.4 | n |  | TRUE
22 | bus_LV_989-3_0_4_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_989-3_0_4_node_23 | 0.4 | n |  | TRUE
24 | bus_LV_989-3_0_4_node_62 | 0.4 | n |  | TRUE
25 | bus_LV_989-3_0_4_node_67 | 0.4 | n |  | TRUE
26 | bus_LV_989-3_0_4_node_24 | 0.4 | n |  | TRUE
27 | bus_LV_989-3_0_4_node_59 | 0.4 | n |  | TRUE
28 | bus_LV_989-3_0_4_node_53 | 0.4 | n |  | TRUE
29 | bus_LV_989-3_0_4_node_54 | 0.4 | n |  | TRUE
30 | bus_LV_989-3_0_4_node_14 | 0.4 | n |  | TRUE
31 | bus_LV_989-3_0_4_node_16 | 0.4 | n |  | TRUE
32 | bus_LV_989-3_0_4_node_18 | 0.4 | n |  | TRUE
33 | bus_LV_989-3_0_4_node_19 | 0.4 | n |  | TRUE
34 | bus_LV_989-3_0_4_node_32 | 0.4 | n |  | TRUE
35 | bus_LV_989-3_0_4_node_72 | 0.4 | n |  | TRUE
36 | bus_LV_989-3_0_4_node_26 | 0.4 | n |  | TRUE
37 | bus_LV_989-3_0_4_node_30 | 0.4 | n |  | TRUE
38 | bus_LV_989-3_0_4_node_70 | 0.4 | n |  | TRUE
39 | bus_LV_989-3_0_4_node_66 | 0.4 | n |  | TRUE
40 | bus_LV_989-3_0_4_node_60 | 0.4 | n |  | TRUE
41 | bus_LV_989-3_0_4_node_25 | 0.4 | n |  | TRUE
42 | bus_LV_989-3_0_4_node_27 | 0.4 | n |  | TRUE
43 | bus_LV_989-3_0_4_node_29 | 0.4 | n |  | TRUE
44 | bus_LV_989-3_0_4_node_37 | 0.4 | n |  | TRUE
45 | bus_LV_989-3_0_4_node_35 | 0.4 | n |  | TRUE
46 | bus_LV_989-3_0_4_node_31 | 0.4 | n |  | TRUE
47 | bus_LV_989-3_0_4_node_34 | 0.4 | n |  | TRUE
48 | bus_LV_989-3_0_4_node_36 | 0.4 | n |  | TRUE
49 | bus_LV_989-3_0_4_node_38 | 0.4 | n |  | TRUE
50 | bus_LV_989-3_0_4_node_64 | 0.4 | n |  | TRUE
51 | bus_LV_989-3_0_4_node_65 | 0.4 | n |  | TRUE
52 | bus_LV_989-3_0_4_node_39 | 0.4 | n |  | TRUE
53 | bus_LV_989-3_0_4_node_40 | 0.4 | n |  | TRUE
54 | bus_LV_989-3_0_4_node_41 | 0.4 | n |  | TRUE
55 | bus_LV_989-3_0_4_node_42 | 0.4 | n |  | TRUE
56 | bus_LV_989-3_0_4_node_43 | 0.4 | n |  | TRUE
57 | bus_LV_989-3_0_4_node_44 | 0.4 | n |  | TRUE
58 | bus_LV_989-3_0_4_node_55 | 0.4 | n |  | TRUE
59 | bus_LV_989-3_0_4_node_56 | 0.4 | n |  | TRUE
60 | bus_LV_989-3_0_4_node_45 | 0.4 | n |  | TRUE
61 | bus_LV_989-3_0_4_node_52 | 0.4 | n |  | TRUE
62 | bus_LV_989-3_0_4_node_46 | 0.4 | n |  | TRUE
63 | bus_LV_989-3_0_4_node_47 | 0.4 | n |  | TRUE
64 | bus_LV_989-3_0_4_node_71 | 0.4 | n |  | TRUE
65 | bus_LV_989-3_0_4_node_48 | 0.4 | n |  | TRUE
66 | bus_LV_989-3_0_4_node_49 | 0.4 | n |  | TRUE
67 | bus_LV_989-3_0_4_node_50 | 0.4 | n |  | TRUE
68 | bus_LV_989-3_0_4_node_51 | 0.4 | n |  | TRUE
69 | bus_LV_989-3_0_4_node_69 | 0.4 | n |  | TRUE
70 | bus_LV_989-3_0_4_node_58 | 0.4 | n |  | TRUE
71 | bus_LV_989-3_0_4_node_68 | 0.4 | n |  | TRUE
72 | bus_MV_184_1_node_278 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_989-3_0_4_load_0 | 0 | 0.0033894 | 0.00084947 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_989-3_0_4_load_1 | 1 | 0.0021536 | 0.00053975 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_989-3_0_4_load_3 | 2 | 0.0063719 | 0.001597 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_989-3_0_4_load_4 | 4 | 0.0050037 | 0.001254 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_989-3_0_4_load_13 | 8 | 0.0042917 | 0.0010756 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_989-3_0_4_load_63 | 10 | 0.005211 | 0.001306 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_989-3_0_4_load_21 | 12 | 0.0057801 | 0.0014486 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_989-3_0_4_load_8 | 13 | 0.0020569 | 0.00051551 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_989-3_0_4_load_61 | 15 | 0.0039405 | 0.00098758 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_989-3_0_4_load_22 | 18 | 0.0022667 | 0.00056808 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_989-3_0_4_load_74 | 19 | 0.0079857 | 0.0020014 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_989-3_0_4_load_20 | 20 | 0.011039 | 0.0027666 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_989-3_0_4_load_28 | 21 | 0.00842 | 0.0021103 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_989-3_0_4_load_15 | 22 | 0.0022476 | 0.0005633 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_989-3_0_4_load_67 | 25 | 0.0065494 | 0.0016414 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_989-3_0_4_load_59 | 27 | 0.01031 | 0.0025838 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_989-3_0_4_load_54 | 29 | 0.0038955 | 0.00097632 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_989-3_0_4_load_14 | 30 | 0.0045223 | 0.0011334 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_989-3_0_4_load_18 | 32 | 0.0038113 | 0.0009552 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_989-3_0_4_load_19 | 33 | 0.0067347 | 0.0016879 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_989-3_0_4_load_32 | 34 | 0.00069031 | 0.00017301 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_989-3_0_4_load_72 | 35 | 0.0017611 | 0.00044138 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_989-3_0_4_load_26 | 36 | 0.0055508 | 0.0013912 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_989-3_0_4_load_30 | 37 | 0.0028786 | 0.00072145 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_989-3_0_4_load_70 | 38 | 0.0012796 | 0.00032071 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_989-3_0_4_load_66 | 39 | 0.0014661 | 0.00036743 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_989-3_0_4_load_60 | 40 | 0.0019774 | 0.00049557 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_989-3_0_4_load_25 | 41 | 0.00044835 | 0.00011237 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_989-3_0_4_load_27 | 42 | 0.0021971 | 0.00055063 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_989-3_0_4_load_29 | 43 | 0.0010276 | 0.00025754 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_989-3_0_4_load_37 | 44 | 0.0011242 | 0.00028176 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_989-3_0_4_load_35 | 45 | 0.0019221 | 0.00048173 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_989-3_0_4_load_31 | 46 | 0.00083875 | 0.00021021 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_989-3_0_4_load_34 | 47 | 0.00071149 | 0.00017832 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_989-3_0_4_load_36 | 48 | 0.0079508 | 0.0019927 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_989-3_0_4_load_38 | 49 | 0.0029367 | 0.000736 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_989-3_0_4_load_64 | 50 | 0.0047978 | 0.0012025 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_989-3_0_4_load_65 | 51 | 0.011657 | 0.0029216 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_989-3_0_4_load_39 | 52 | 0.0011411 | 0.00028599 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_989-3_0_4_load_40 | 53 | 0.0012811 | 0.00032107 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_989-3_0_4_load_43 | 56 | 0.0029969 | 0.00075108 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_989-3_0_4_load_44 | 57 | 0.0027081 | 0.00067871 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_989-3_0_4_load_56 | 59 | 0.0037208 | 0.00093252 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_989-3_0_4_load_52 | 61 | 0.0018882 | 0.00047323 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_989-3_0_4_load_47 | 63 | 0.0012807 | 0.00032098 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_989-3_0_4_load_71 | 64 | 0.00046943 | 0.00011765 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_989-3_0_4_load_48 | 65 | 0.0045066 | 0.0011295 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_989-3_0_4_load_50 | 67 | 0.0041488 | 0.0010398 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_989-3_0_4_load_69 | 69 | 0.0014166 | 0.00035503 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_989-3_0_4_load_58 | 70 | 0.011072 | 0.0027749 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_989-3_0_4_load_68 | 71 | 0.0068059 | 0.0017057 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 11 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_989-3_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.020304 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_989-3_0_4_line_1 | NAYY 4x150 SE | 1 | 2 | 0.02357 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_989-3_0_4_line_2 | NAYY 4x150 SE | 2 | 3 | 0.020881 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_989-3_0_4_line_3 | NAYY 4x150 SE | 3 | 6 | 0.009073 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_989-3_0_4_line_4 | NAYY 4x150 SE | 3 | 7 | 0.02858 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_989-3_0_4_line_5 | NAYY 4x150 SE | 4 | 5 | 0.021386 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_989-3_0_4_line_6 | NAYY 4x150 SE | 5 | 8 | 0.014205 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_989-3_0_4_line_7 | NAYY 4x150 SE | 5 | 7 | 0.018271 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_989-3_0_4_line_8 | NAYY 4x150 SE | 6 | 9 | 0.016022 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_989-3_0_4_line_9 | NAYY 4x150 SE | 7 | 10 | 0.026774 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_989-3_0_4_line_10 | NAYY 4x150 SE | 8 | 28 | 0.038716 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_989-3_0_4_line_11 | NAYY 4x150 SE | 9 | 11 | 0.027213 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
12 | LV_989-3_0_4_line_12 | NAYY 4x150 SE | 9 | 12 | 0.022703 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_989-3_0_4_line_13 | NAYY 4x150 SE | 10 | 15 | 0.0097872 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_989-3_0_4_line_14 | NAYY 4x150 SE | 11 | 21 | 0.018801 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_989-3_0_4_line_15 | NAYY 4x150 SE | 11 | 22 | 0.028933 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_989-3_0_4_line_16 | NAYY 4x150 SE | 12 | 20 | 0.038037 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_989-3_0_4_line_17 | NAYY 4x150 SE | 13 | 14 | 0.027553 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_989-3_0_4_line_18 | NAYY 4x150 SE | 14 | 16 | 0.00307 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_989-3_0_4_line_19 | NAYY 4x150 SE | 15 | 40 | 0.011874 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_989-3_0_4_line_20 | NAYY 4x150 SE | 16 | 17 | 0.04644 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_989-3_0_4_line_21 | NAYY 4x150 SE | 16 | 18 | 0.0077187 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_989-3_0_4_line_22 | NAYY 4x150 SE | 17 | 19 | 0.023083 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_989-3_0_4_line_23 | NAYY 4x150 SE | 18 | 20 | 0.03703 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_989-3_0_4_line_24 | NAYY 4x150 SE | 21 | 36 | 0.015019 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_989-3_0_4_line_25 | NAYY 4x150 SE | 22 | 30 | 0.047633 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_989-3_0_4_line_26 | NAYY 4x150 SE | 23 | 24 | 0.010715 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_989-3_0_4_line_27 | NAYY 4x150 SE | 23 | 25 | 0.034327 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_989-3_0_4_line_28 | NAYY 4x150 SE | 24 | 38 | 0.023553 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_989-3_0_4_line_29 | NAYY 4x150 SE | 24 | 26 | 0.007347 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_989-3_0_4_line_30 | NAYY 4x150 SE | 25 | 39 | 0.0042795 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_989-3_0_4_line_31 | NAYY 4x150 SE | 26 | 27 | 0.036395 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_989-3_0_4_line_32 | NAYY 4x150 SE | 27 | 40 | 0.02481 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_989-3_0_4_line_33 | NAYY 4x150 SE | 28 | 29 | 0.068791 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_989-3_0_4_line_34 | NAYY 4x150 SE | 29 | 70 | 0.024413 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_989-3_0_4_line_35 | NAYY 4x150 SE | 30 | 31 | 0.018546 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_989-3_0_4_line_36 | NAYY 4x150 SE | 31 | 32 | 0.050762 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_989-3_0_4_line_37 | NAYY 4x150 SE | 31 | 33 | 0.016189 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_989-3_0_4_line_38 | NAYY 4x150 SE | 32 | 34 | 0.025109 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_989-3_0_4_line_39 | NAYY 4x150 SE | 33 | 35 | 0.008482 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_989-3_0_4_line_40 | NAYY 4x150 SE | 34 | 37 | 0.0076498 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_989-3_0_4_line_41 | NAYY 4x150 SE | 36 | 41 | 0.024259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_989-3_0_4_line_42 | NAYY 4x150 SE | 37 | 46 | 0.0039659 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_989-3_0_4_line_43 | NAYY 4x150 SE | 38 | 68 | 0.019381 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_989-3_0_4_line_44 | NAYY 4x150 SE | 39 | 71 | 0.043066 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_989-3_0_4_line_45 | NAYY 4x150 SE | 41 | 42 | 0.0095761 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_989-3_0_4_line_46 | NAYY 4x150 SE | 42 | 43 | 0.00098853 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_989-3_0_4_line_47 | NAYY 4x150 SE | 43 | 44 | 0.018191 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_989-3_0_4_line_48 | NAYY 4x150 SE | 44 | 45 | 0.0013297 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_989-3_0_4_line_49 | NAYY 4x150 SE | 45 | 47 | 0.020518 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_989-3_0_4_line_50 | NAYY 4x150 SE | 47 | 48 | 0.012016 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_989-3_0_4_line_51 | NAYY 4x150 SE | 48 | 49 | 0.011594 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_989-3_0_4_line_52 | NAYY 4x150 SE | 49 | 50 | 0.037085 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_989-3_0_4_line_53 | NAYY 4x150 SE | 50 | 51 | 0.027083 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_989-3_0_4_line_54 | NAYY 4x150 SE | 52 | 53 | 0.013098 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_989-3_0_4_line_55 | NAYY 4x150 SE | 52 | 54 | 0.0093677 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_989-3_0_4_line_56 | NAYY 4x150 SE | 53 | 55 | 0.011554 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_989-3_0_4_line_57 | NAYY 4x150 SE | 54 | 56 | 0.023629 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_989-3_0_4_line_58 | NAYY 4x150 SE | 54 | 57 | 0.0068883 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_989-3_0_4_line_59 | NAYY 4x150 SE | 55 | 58 | 0.026082 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_989-3_0_4_line_60 | NAYY 4x150 SE | 55 | 59 | 0.013543 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_989-3_0_4_line_61 | NAYY 4x150 SE | 56 | 60 | 0.037395 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_989-3_0_4_line_62 | NAYY 4x150 SE | 58 | 61 | 0.015805 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_989-3_0_4_line_63 | NAYY 4x150 SE | 60 | 62 | 0.016888 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_989-3_0_4_line_64 | NAYY 4x150 SE | 60 | 63 | 0.025074 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_989-3_0_4_line_65 | NAYY 4x150 SE | 61 | 66 | 0.0024246 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_989-3_0_4_line_66 | NAYY 4x150 SE | 62 | 64 | 0.014451 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_989-3_0_4_line_67 | NAYY 4x150 SE | 65 | 66 | 0.017547 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_989-3_0_4_line_68 | NAYY 4x150 SE | 65 | 67 | 0.016929 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_989-3_0_4_line_69 | NAYY 4x150 SE | 66 | 68 | 0.011509 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_989-3_0_4_line_70 | NAYY 4x150 SE | 68 | 69 | 0.013452 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_989-3_0_4_trafo_17 | 0.25 MVA 20/0.4 kV | 72 | 11 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2622013.4714 | 1224710.8154 | 2622000.4848 | 1224711.595 | 2621995.9627 | 1224714.6579 | 2621995.3749 | 1224716.3935
1 | 2621987.8145 | 1224738.7177 | 2621995.3749 | 1224716.3935
2 | 2621981.1164 | 1224758.4957 | 2621987.8145 | 1224738.7177
3 | 2621972.1459 | 1224756.9729 | 2621981.1164 | 1224758.4957
4 | 2622009.3763 | 1224763.2805 | 2621997.1556 | 1224761.212 | 2621981.1164 | 1224758.4957
5 | 2622027.4615 | 1224766.2268 | 2622032.7222 | 1224745.498
6 | 2622027.4615 | 1224766.2268 | 2622041.4821 | 1224768.5108
7 | 2622009.3763 | 1224763.2805 | 2622027.4615 | 1224766.2268
8 | 2621972.1459 | 1224756.9729 | 2621962.8474 | 1224753.9702 | 2621956.8808 | 1224751.9693
9 | 2622009.3763 | 1224763.2805 | 2622003.5727 | 1224789.4178
10 | 2622079.6942 | 1224774.7359 | 2622041.4821 | 1224768.5108
11 | 2621956.8808 | 1224751.9693 | 2621944.2929 | 1224746.6643 | 2621932.2771 | 1224740.3942
12 | 2621956.8808 | 1224751.9693 | 2621960.5336 | 1224742.0213 | 2621963.4755 | 1224730.2785
13 | 2622001.4512 | 1224798.9723 | 2622003.5727 | 1224789.4178
14 | 2621932.2771 | 1224740.3942 | 2621921.873 | 1224734.9528 | 2621916.1632 | 1224730.8005
15 | 2621932.2771 | 1224740.3942 | 2621935.6536 | 1224711.659
16 | 2621972.7191 | 1224693.3813 | 2621963.4755 | 1224730.2785
17 | 2621986.5011 | 1224650.9855 | 2621979.8198 | 1224677.7157
18 | 2621983.5936 | 1224649.9742 | 2621986.5011 | 1224650.9855
19 | 2622001.4512 | 1224798.9723 | 2622001.4512 | 1224798.9723 | 2621996.8948 | 1224803.1358 | 2621991.3715 | 1224801.7209
20 | 2621983.104 | 1224614.1513 | 2621992.6411 | 1224614.1976 | 2621983.5936 | 1224649.9742
21 | 2621983.5936 | 1224649.9742 | 2621981.7179 | 1224657.4615
22 | 2621983.104 | 1224614.1513 | 2621978.7053 | 1224616.6366 | 2621961.1386 | 1224620.9633
23 | 2621981.7179 | 1224657.4615 | 2621972.7191 | 1224693.3813
24 | 2621904.0167 | 1224721.9672 | 2621916.1632 | 1224730.8005
25 | 2621935.6536 | 1224711.659 | 2621935.8224 | 1224710.2228 | 2621930.8254 | 1224664.3073
26 | 2621933.1328 | 1224802.4896 | 2621922.4 | 1224801.9498
27 | 2621922.4 | 1224801.9498 | 2621898.7421 | 1224801.2403 | 2621888.1403 | 1224800.1385
28 | 2621933.1328 | 1224802.4896 | 2621928.7046 | 1224825.623
29 | 2621933.1328 | 1224802.4896 | 2621934.2058 | 1224795.2225
30 | 2621883.8837 | 1224799.6961 | 2621888.1403 | 1224800.1385
31 | 2621934.2058 | 1224795.2225 | 2621959.2793 | 1224802.6636 | 2621967.1951 | 1224796.1667
32 | 2621967.1951 | 1224796.1667 | 2621967.1951 | 1224796.1667 | 2621983.6404 | 1224799.7405 | 2621991.3715 | 1224801.7209
33 | 2622079.6942 | 1224774.7359 | 2622075.8251 | 1224789.8083 | 2622067.842 | 1224806.2551 | 2622046.9372 | 1224823.6881 | 2622042.0464 | 1224829.6725
34 | 2622031.7532 | 1224851.4696 | 2622037.4255 | 1224835.3265 | 2622042.0464 | 1224829.6725
35 | 2621928.819 | 1224645.8702 | 2621930.8254 | 1224664.3073
36 | 2621928.819 | 1224645.8702 | 2621926.2743 | 1224622.4804 | 2621922.2679 | 1224595.543
37 | 2621928.819 | 1224645.8702 | 2621926.483 | 1224646.1285 | 2621922.5543 | 1224646.5587 | 2621915.7419 | 1224649.8134 | 2621914.9497 | 1224652.0117
38 | 2621922.2679 | 1224595.543 | 2621918.5741 | 1224570.7072
39 | 2621914.854 | 1224660.3831 | 2621914.4016 | 1224653.5329 | 2621914.9497 | 1224652.0117
40 | 2621918.5741 | 1224570.7072 | 2621917.4487 | 1224563.1406
41 | 2621904.0167 | 1224721.9672 | 2621891.8182 | 1224713.0962 | 2621884.3249 | 1224707.8001
42 | 2621916.8653 | 1224559.2178 | 2621917.4487 | 1224563.1406
43 | 2621922.6018 | 1224843.9753 | 2621927.9927 | 1224829.3421 | 2621928.7046 | 1224825.623
44 | 2621858.9583 | 1224773.9005 | 2621857.9137 | 1224779.6779 | 2621858.7368 | 1224788.853 | 2621867.7484 | 1224795.6789 | 2621880.0013 | 1224799.2926 | 2621883.8837 | 1224799.6961
45 | 2621876.5048 | 1224702.2731 | 2621884.3249 | 1224707.8001
46 | 2621876.5048 | 1224702.2731 | 2621875.6975 | 1224701.7025
47 | 2621860.626 | 1224691.5396 | 2621864.5738 | 1224693.8405 | 2621875.6975 | 1224701.7025
48 | 2621859.4773 | 1224690.8701 | 2621860.626 | 1224691.5396
49 | 2621841.75 | 1224680.538 | 2621841.75 | 1224680.538 | 2621859.4773 | 1224690.8701
50 | 2621841.75 | 1224680.538 | 2621831.1977 | 1224674.7901
51 | 2621821.016 | 1224669.244 | 2621831.1977 | 1224674.7901
52 | 2621788.4488 | 1224651.5043 | 2621821.016 | 1224669.244
53 | 2621788.4488 | 1224651.5043 | 2621764.6656 | 1224638.5494
54 | 2621874.428 | 1224881.9277 | 2621880.593 | 1224871.5151 | 2621881.1375 | 1224870.6798
55 | 2621870.2972 | 1224890.3329 | 2621874.0708 | 1224882.5311 | 2621874.428 | 1224881.9277
56 | 2621887.4469 | 1224861.0007 | 2621881.1375 | 1224870.6798
57 | 2621870.2972 | 1224890.3329 | 2621858.8456 | 1224885.3214 | 2621850.3912 | 1224879.5537 | 2621849.5127 | 1224879.3833
58 | 2621870.2972 | 1224890.3329 | 2621875.0272 | 1224895.3406
59 | 2621887.4469 | 1224861.0007 | 2621897.1512 | 1224864.9498 | 2621911.387 | 1224871.4948
60 | 2621875.0266 | 1224855.5186 | 2621887.4469 | 1224861.0007
61 | 2621833.4204 | 1224905.6625 | 2621834.9823 | 1224899.3867 | 2621837.5669 | 1224891.2358 | 2621837.7648 | 1224882.7426 | 2621842.3838 | 1224878.0012 | 2621849.5127 | 1224879.3833
62 | 2621911.387 | 1224871.4948 | 2621916.7821 | 1224859.7966 | 2621917.7908 | 1224857.0538
63 | 2621833.4204 | 1224905.6625 | 2621849.2501 | 1224911.6684
64 | 2621814.719 | 1224893.02 | 2621814.5354 | 1224897.6109 | 2621833.4204 | 1224905.6625
65 | 2621918.6276 | 1224854.7782 | 2621917.7908 | 1224857.0538
66 | 2621849.2501 | 1224911.6684 | 2621840.5675 | 1224923.2196
67 | 2621918.6276 | 1224854.7782 | 2621935.8627 | 1224857.9545 | 2621935.8836 | 1224857.9593
68 | 2621952.3829 | 1224861.7508 | 2621935.8836 | 1224857.9593
69 | 2621922.6018 | 1224843.9753 | 2621918.6276 | 1224854.7782
70 | 2621922.6018 | 1224843.9753 | 2621909.7383 | 1224840.0388

## bus_geodata
| x | y | coords
0 | 2622013.4714 | 1224710.8154
1 | 2621995.3749 | 1224716.3935
2 | 2621987.8145 | 1224738.7177
3 | 2621981.1164 | 1224758.4957
4 | 2622032.7222 | 1224745.498
5 | 2622027.4615 | 1224766.2268
6 | 2621972.1459 | 1224756.9729
7 | 2622009.3763 | 1224763.2805
8 | 2622041.4821 | 1224768.5108
9 | 2621956.8808 | 1224751.9693
10 | 2622003.5727 | 1224789.4178
11 | 2621932.2771 | 1224740.3942
12 | 2621963.4755 | 1224730.2785
13 | 2621979.8198 | 1224677.7157
14 | 2621986.5011 | 1224650.9855
15 | 2622001.4512 | 1224798.9723
16 | 2621983.5936 | 1224649.9742
17 | 2621983.104 | 1224614.1513
18 | 2621981.7179 | 1224657.4615
19 | 2621961.1386 | 1224620.9633
20 | 2621972.7191 | 1224693.3813
21 | 2621916.1632 | 1224730.8005
22 | 2621935.6536 | 1224711.659
23 | 2621922.4 | 1224801.9498
24 | 2621933.1328 | 1224802.4896
25 | 2621888.1403 | 1224800.1385
26 | 2621934.2057 | 1224795.2225
27 | 2621967.1951 | 1224796.1667
28 | 2622079.6942 | 1224774.7359
29 | 2622042.0464 | 1224829.6725
30 | 2621930.8254 | 1224664.3073
31 | 2621928.819 | 1224645.8702
32 | 2621922.2679 | 1224595.543
33 | 2621914.9497 | 1224652.0117
34 | 2621918.5741 | 1224570.7072
35 | 2621914.854 | 1224660.3831
36 | 2621904.0167 | 1224721.9672
37 | 2621917.4487 | 1224563.1406
38 | 2621928.7046 | 1224825.623
39 | 2621883.8837 | 1224799.6961
40 | 2621991.3715 | 1224801.7209
41 | 2621884.3249 | 1224707.8001
42 | 2621876.5048 | 1224702.2731
43 | 2621875.6975 | 1224701.7025
44 | 2621860.626 | 1224691.5396
45 | 2621859.4773 | 1224690.8701
46 | 2621916.8653 | 1224559.2178
47 | 2621841.75 | 1224680.538
48 | 2621831.1977 | 1224674.7901
49 | 2621821.016 | 1224669.244
50 | 2621788.4488 | 1224651.5043
51 | 2621764.6656 | 1224638.5494
52 | 2621874.428 | 1224881.9277
53 | 2621881.1375 | 1224870.6798
54 | 2621870.2972 | 1224890.3329
55 | 2621887.4469 | 1224861.0007
56 | 2621849.5127 | 1224879.3833
57 | 2621875.0272 | 1224895.3406
58 | 2621911.387 | 1224871.4948
59 | 2621875.0266 | 1224855.5186
60 | 2621833.4204 | 1224905.6625
61 | 2621917.7907 | 1224857.0538
62 | 2621849.2501 | 1224911.6684
63 | 2621814.719 | 1224893.02
64 | 2621840.5675 | 1224923.2196
65 | 2621935.8836 | 1224857.9593
66 | 2621918.6276 | 1224854.7782
67 | 2621952.3829 | 1224861.7508
68 | 2621922.6018 | 1224843.9753
69 | 2621909.7383 | 1224840.0388
70 | 2622031.7532 | 1224851.4696
71 | 2621858.9583 | 1224773.9005
72 | 2621944.2929 | 1224746.6643

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1