## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1024-34_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1024-34_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1024-34_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1024-34_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1024-34_0_6_node_8 | 0.4 | n |  | TRUE
5 | bus_LV_1024-34_0_6_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_1024-34_0_6_node_11 | 0.4 | n |  | TRUE
7 | bus_LV_1024-34_0_6_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_1024-34_0_6_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_1024-34_0_6_node_53 | 0.4 | n |  | TRUE
10 | bus_LV_1024-34_0_6_node_51 | 0.4 | n |  | TRUE
11 | bus_LV_1024-34_0_6_node_43 | 0.4 | n |  | TRUE
12 | bus_LV_1024-34_0_6_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_1024-34_0_6_node_44 | 0.4 | n |  | TRUE
14 | bus_LV_1024-34_0_6_node_12 | 0.4 | n |  | TRUE
15 | bus_LV_1024-34_0_6_node_54 | 0.4 | n |  | TRUE
16 | bus_LV_1024-34_0_6_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_1024-34_0_6_node_52 | 0.4 | n |  | TRUE
18 | bus_LV_1024-34_0_6_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_1024-34_0_6_node_120 | 0.4 | n |  | TRUE
20 | bus_LV_1024-34_0_6_node_23 | 0.4 | n |  | TRUE
21 | bus_LV_1024-34_0_6_node_48 | 0.4 | n |  | TRUE
22 | bus_LV_1024-34_0_6_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_1024-34_0_6_node_41 | 0.4 | n |  | TRUE
24 | bus_LV_1024-34_0_6_node_47 | 0.4 | n |  | TRUE
25 | bus_LV_1024-34_0_6_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_1024-34_0_6_node_107 | 0.4 | n |  | TRUE
27 | bus_LV_1024-34_0_6_node_34 | 0.4 | n |  | TRUE
28 | bus_LV_1024-34_0_6_node_104 | 0.4 | n |  | TRUE
29 | bus_LV_1024-34_0_6_node_18 | 0.4 | n |  | TRUE
30 | bus_LV_1024-34_0_6_node_22 | 0.4 | n |  | TRUE
31 | bus_LV_1024-34_0_6_node_96 | 0.4 | n |  | TRUE
32 | bus_LV_1024-34_0_6_node_109 | 0.4 | n |  | TRUE
33 | bus_LV_1024-34_0_6_node_19 | 0.4 | n |  | TRUE
34 | bus_LV_1024-34_0_6_node_110 | 0.4 | n |  | TRUE
35 | bus_LV_1024-34_0_6_node_20 | 0.4 | n |  | TRUE
36 | bus_LV_1024-34_0_6_node_24 | 0.4 | n |  | TRUE
37 | bus_LV_1024-34_0_6_node_26 | 0.4 | n |  | TRUE
38 | bus_LV_1024-34_0_6_node_126 | 0.4 | n |  | TRUE
39 | bus_LV_1024-34_0_6_node_21 | 0.4 | n |  | TRUE
40 | bus_LV_1024-34_0_6_node_112 | 0.4 | n |  | TRUE
41 | bus_LV_1024-34_0_6_node_125 | 0.4 | n |  | TRUE
42 | bus_LV_1024-34_0_6_node_123 | 0.4 | n |  | TRUE
43 | bus_LV_1024-34_0_6_node_124 | 0.4 | n |  | TRUE
44 | bus_LV_1024-34_0_6_node_79 | 0.4 | n |  | TRUE
45 | bus_LV_1024-34_0_6_node_74 | 0.4 | n |  | TRUE
46 | bus_LV_1024-34_0_6_node_73 | 0.4 | n |  | TRUE
47 | bus_LV_1024-34_0_6_node_29 | 0.4 | n |  | TRUE
48 | bus_LV_1024-34_0_6_node_113 | 0.4 | n |  | TRUE
49 | bus_LV_1024-34_0_6_node_111 | 0.4 | n |  | TRUE
50 | bus_LV_1024-34_0_6_node_31 | 0.4 | n |  | TRUE
51 | bus_LV_1024-34_0_6_node_40 | 0.4 | n |  | TRUE
52 | bus_LV_1024-34_0_6_node_88 | 0.4 | n |  | TRUE
53 | bus_LV_1024-34_0_6_node_35 | 0.4 | n |  | TRUE
54 | bus_LV_1024-34_0_6_node_87 | 0.4 | n |  | TRUE
55 | bus_LV_1024-34_0_6_node_36 | 0.4 | n |  | TRUE
56 | bus_LV_1024-34_0_6_node_86 | 0.4 | n |  | TRUE
57 | bus_LV_1024-34_0_6_node_75 | 0.4 | n |  | TRUE
58 | bus_LV_1024-34_0_6_node_37 | 0.4 | n |  | TRUE
59 | bus_LV_1024-34_0_6_node_119 | 0.4 | n |  | TRUE
60 | bus_LV_1024-34_0_6_node_77 | 0.4 | n |  | TRUE
61 | bus_LV_1024-34_0_6_node_97 | 0.4 | n |  | TRUE
62 | bus_LV_1024-34_0_6_node_38 | 0.4 | n |  | TRUE
63 | bus_LV_1024-34_0_6_node_70 | 0.4 | n |  | TRUE
64 | bus_LV_1024-34_0_6_node_39 | 0.4 | n |  | TRUE
65 | bus_LV_1024-34_0_6_node_91 | 0.4 | n |  | TRUE
66 | bus_LV_1024-34_0_6_node_117 | 0.4 | n |  | TRUE
67 | bus_LV_1024-34_0_6_node_127 | 0.4 | n |  | TRUE
68 | bus_LV_1024-34_0_6_node_55 | 0.4 | n |  | TRUE
69 | bus_LV_1024-34_0_6_node_50 | 0.4 | n |  | TRUE
70 | bus_LV_1024-34_0_6_node_89 | 0.4 | n |  | TRUE
71 | bus_LV_1024-34_0_6_node_131 | 0.4 | n |  | TRUE
72 | bus_LV_1024-34_0_6_node_106 | 0.4 | n |  | TRUE
73 | bus_LV_1024-34_0_6_node_129 | 0.4 | n |  | TRUE
74 | bus_LV_1024-34_0_6_node_128 | 0.4 | n |  | TRUE
75 | bus_LV_1024-34_0_6_node_105 | 0.4 | n |  | TRUE
76 | bus_LV_1024-34_0_6_node_95 | 0.4 | n |  | TRUE
77 | bus_LV_1024-34_0_6_node_78 | 0.4 | n |  | TRUE
78 | bus_LV_1024-34_0_6_node_108 | 0.4 | n |  | TRUE
79 | bus_LV_1024-34_0_6_node_61 | 0.4 | n |  | TRUE
80 | bus_LV_1024-34_0_6_node_102 | 0.4 | n |  | TRUE
81 | bus_LV_1024-34_0_6_node_71 | 0.4 | n |  | TRUE
82 | bus_LV_1024-34_0_6_node_90 | 0.4 | n |  | TRUE
83 | bus_LV_1024-34_0_6_node_85 | 0.4 | n |  | TRUE
84 | bus_LV_1024-34_0_6_node_60 | 0.4 | n |  | TRUE
85 | bus_LV_1024-34_0_6_node_72 | 0.4 | n |  | TRUE
86 | bus_LV_1024-34_0_6_node_58 | 0.4 | n |  | TRUE
87 | bus_LV_1024-34_0_6_node_76 | 0.4 | n |  | TRUE
88 | bus_LV_1024-34_0_6_node_68 | 0.4 | n |  | TRUE
89 | bus_LV_1024-34_0_6_node_92 | 0.4 | n |  | TRUE
90 | bus_LV_1024-34_0_6_node_115 | 0.4 | n |  | TRUE
91 | bus_LV_1024-34_0_6_node_56 | 0.4 | n |  | TRUE
92 | bus_LV_1024-34_0_6_node_121 | 0.4 | n |  | TRUE
93 | bus_LV_1024-34_0_6_node_122 | 0.4 | n |  | TRUE
94 | bus_LV_1024-34_0_6_node_118 | 0.4 | n |  | TRUE
95 | bus_LV_1024-34_0_6_node_57 | 0.4 | n |  | TRUE
96 | bus_LV_1024-34_0_6_node_59 | 0.4 | n |  | TRUE
97 | bus_LV_1024-34_0_6_node_62 | 0.4 | n |  | TRUE
98 | bus_LV_1024-34_0_6_node_63 | 0.4 | n |  | TRUE
99 | bus_LV_1024-34_0_6_node_64 | 0.4 | n |  | TRUE
100 | bus_LV_1024-34_0_6_node_65 | 0.4 | n |  | TRUE
101 | bus_LV_1024-34_0_6_node_66 | 0.4 | n |  | TRUE
102 | bus_LV_1024-34_0_6_node_67 | 0.4 | n |  | TRUE
103 | bus_LV_1024-34_0_6_node_98 | 0.4 | n |  | TRUE
104 | bus_LV_1024-34_0_6_node_93 | 0.4 | n |  | TRUE
105 | bus_LV_1024-34_0_6_node_99 | 0.4 | n |  | TRUE
106 | bus_LV_1024-34_0_6_node_94 | 0.4 | n |  | TRUE
107 | bus_LV_1024-34_0_6_node_100 | 0.4 | n |  | TRUE
108 | bus_LV_1024-34_0_6_node_101 | 0.4 | n |  | TRUE
109 | bus_LV_1024-34_0_6_node_69 | 0.4 | n |  | TRUE
110 | bus_LV_1024-34_0_6_node_81 | 0.4 | n |  | TRUE
111 | bus_LV_1024-34_0_6_node_82 | 0.4 | n |  | TRUE
112 | bus_LV_1024-34_0_6_node_83 | 0.4 | n |  | TRUE
113 | bus_LV_1024-34_0_6_node_84 | 0.4 | n |  | TRUE
114 | bus_LV_1024-34_0_6_node_103 | 0.4 | n |  | TRUE
115 | bus_LV_1024-34_0_6_node_130 | 0.4 | n |  | TRUE
116 | bus_LV_1024-34_0_6_node_114 | 0.4 | n |  | TRUE
117 | bus_LV_1024-34_0_6_node_116 | 0.4 | n |  | TRUE
118 | bus_MV_354_1_node_234 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1024-34_0_6_load_0 | 0 | 0.009505 | 0.0023822 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1024-34_0_6_load_1 | 1 | 0.00061288 | 0.0001536 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1024-34_0_6_load_2 | 2 | 0.0046442 | 0.0011639 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1024-34_0_6_load_4 | 5 | 0.00061282 | 0.00015359 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1024-34_0_6_load_6 | 8 | 0.0034402 | 0.0008622 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1024-34_0_6_load_53 | 9 | 0.0018482 | 0.0004632 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1024-34_0_6_load_51 | 10 | 0.0028234 | 0.00070761 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1024-34_0_6_load_43 | 11 | 0.007264 | 0.0018205 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1024-34_0_6_load_9 | 12 | 0.00030765 | 7.7104e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1024-34_0_6_load_44 | 13 | 0.0048882 | 0.0012251 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1024-34_0_6_load_54 | 15 | 0.004276 | 0.0010717 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1024-34_0_6_load_52 | 17 | 0.0015629 | 0.00039169 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1024-34_0_6_load_120 | 19 | 0.0031642 | 0.00079302 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1024-34_0_6_load_48 | 21 | 0.0024318 | 0.00060946 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1024-34_0_6_load_47 | 24 | 0.0018874 | 0.00047302 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1024-34_0_6_load_104 | 28 | 0.010025 | 0.0025124 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1024-34_0_6_load_96 | 31 | 0.040627 | 0.010182 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1024-34_0_6_load_109 | 32 | 0.04906 | 0.012296 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1024-34_0_6_load_110 | 34 | 0.043441 | 0.010887 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1024-34_0_6_load_126 | 38 | 0.015042 | 0.0037699 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1024-34_0_6_load_112 | 40 | 0.0084673 | 0.0021221 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1024-34_0_6_load_125 | 41 | 0.0051755 | 0.0012971 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1024-34_0_6_load_123 | 42 | 0.0040001 | 0.0010025 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1024-34_0_6_load_124 | 43 | 0.0022893 | 0.00057376 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1024-34_0_6_load_79 | 44 | 0.0098411 | 0.0024664 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1024-34_0_6_load_74 | 45 | 0.046474 | 0.011648 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1024-34_0_6_load_73 | 46 | 0.0050006 | 0.0012533 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1024-34_0_6_load_113 | 48 | 0.011565 | 0.0028984 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1024-34_0_6_load_111 | 49 | 0.0084673 | 0.0021221 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1024-34_0_6_load_88 | 52 | 0.0082761 | 0.0020742 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1024-34_0_6_load_87 | 54 | 0.012781 | 0.0032032 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1024-34_0_6_load_86 | 56 | 0.0014349 | 0.00035963 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1024-34_0_6_load_75 | 57 | 0.00031769 | 7.9621e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1024-34_0_6_load_119 | 59 | 0.00027097 | 6.7911e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1024-34_0_6_load_77 | 60 | 0.00029793 | 7.4667e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1024-34_0_6_load_117 | 66 | 0.0005787 | 0.00014504 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1024-34_0_6_load_127 | 67 | 0.003914 | 0.00098093 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1024-34_0_6_load_55 | 68 | 0.0017533 | 0.00043942 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1024-34_0_6_load_50 | 69 | 0.0038318 | 0.00096034 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1024-34_0_6_load_131 | 71 | 0.0070518 | 0.0017674 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1024-34_0_6_load_129 | 73 | 0.0070878 | 0.0017764 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1024-34_0_6_load_128 | 74 | 0.010141 | 0.0025417 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1024-34_0_6_load_105 | 75 | 0.0048917 | 0.001226 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1024-34_0_6_load_95 | 76 | 0.0017766 | 0.00044527 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1024-34_0_6_load_78 | 77 | 0.0039071 | 0.00097922 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1024-34_0_6_load_108 | 78 | 0.0024183 | 0.00060609 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1024-34_0_6_load_61 | 79 | 0.00030265 | 7.5851e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1024-34_0_6_load_102 | 80 | 0.004304 | 0.0010787 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1024-34_0_6_load_71 | 81 | 0.0026627 | 0.00066735 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1024-34_0_6_load_90 | 82 | 0.0072122 | 0.0018075 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1024-34_0_6_load_85 | 83 | 0.0039293 | 0.00098478 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1024-34_0_6_load_72 | 85 | 0.034982 | 0.0087673 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1024-34_0_6_load_58 | 86 | 0.014655 | 0.0036728 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1024-34_0_6_load_76 | 87 | 0.00013206 | 3.3098e-05 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1024-34_0_6_load_68 | 88 | 0.0095073 | 0.0023828 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1024-34_0_6_load_92 | 89 | 0.0022015 | 0.00055175 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1024-34_0_6_load_115 | 90 | 0.00062016 | 0.00015543 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1024-34_0_6_load_56 | 91 | 0.0040598 | 0.0010175 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1024-34_0_6_load_122 | 93 | 0.00062085 | 0.0001556 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1024-34_0_6_load_118 | 94 | 0.00057335 | 0.0001437 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1024-34_0_6_load_57 | 95 | 0.00010956 | 2.7459e-05 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1024-34_0_6_load_59 | 96 | 0.00011801 | 2.9576e-05 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1024-34_0_6_load_62 | 97 | 0.00032521 | 8.1504e-05 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1024-34_0_6_load_63 | 98 | 0.00031728 | 7.9517e-05 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1024-34_0_6_load_65 | 100 | 0.002304 | 0.00057743 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1024-34_0_6_load_66 | 101 | 0.0023682 | 0.00059353 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1024-34_0_6_load_67 | 102 | 0.0016499 | 0.00041351 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1024-34_0_6_load_98 | 103 | 0.002329 | 0.00058371 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1024-34_0_6_load_93 | 104 | 0.0025527 | 0.00063977 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1024-34_0_6_load_94 | 106 | 0.0024781 | 0.00062106 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1024-34_0_6_load_101 | 108 | 0.0050991 | 0.0012779 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1024-34_0_6_load_69 | 109 | 0.0036876 | 0.00092419 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1024-34_0_6_load_81 | 110 | 0.0047414 | 0.0011883 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1024-34_0_6_load_82 | 111 | 0.0057297 | 0.001436 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1024-34_0_6_load_84 | 113 | 0.002693 | 0.00067493 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1024-34_0_6_load_103 | 114 | 0.0030558 | 0.00076586 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1024-34_0_6_load_130 | 115 | 0.0043468 | 0.0010894 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1024-34_0_6_load_114 | 116 | 0.00057004 | 0.00014286 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1024-34_0_6_load_116 | 117 | 0.00060544 | 0.00015174 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 33 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1024-34_0_6_line_0 |  | 0 | 1 | 0.015538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1024-34_0_6_line_1 |  | 0 | 2 | 0.017963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1024-34_0_6_line_2 |  | 1 | 3 | 0.01361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1024-34_0_6_line_3 |  | 3 | 4 | 0.04176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1024-34_0_6_line_4 |  | 3 | 5 | 0.020988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1024-34_0_6_line_5 |  | 4 | 6 | 0.010135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1024-34_0_6_line_6 |  | 5 | 7 | 0.081238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1024-34_0_6_line_7 |  | 6 | 11 | 0.039081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1024-34_0_6_line_8 |  | 6 | 12 | 0.017067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1024-34_0_6_line_9 |  | 7 | 8 | 0.026882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1024-34_0_6_line_10 |  | 8 | 9 | 0.0036381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1024-34_0_6_line_11 |  | 9 | 10 | 0.017655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1024-34_0_6_line_12 |  | 10 | 69 | 0.016343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1024-34_0_6_line_13 |  | 12 | 13 | 0.046636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1024-34_0_6_line_14 |  | 14 | 15 | 0.010884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1024-34_0_6_line_15 |  | 14 | 16 | 0.18928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1024-34_0_6_line_16 |  | 14 | 17 | 0.014704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1024-34_0_6_line_17 |  | 16 | 18 | 0.065738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1024-34_0_6_line_18 |  | 16 | 19 | 0.02739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1024-34_0_6_line_19 |  | 17 | 69 | 0.025031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1024-34_0_6_line_20 |  | 18 | 20 | 0.044345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1024-34_0_6_line_21 |  | 18 | 21 | 0.0078666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1024-34_0_6_line_22 |  | 20 | 43 | 0.01244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1024-34_0_6_line_23 |  | 21 | 24 | 0.014747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1024-34_0_6_line_24 |  | 22 | 23 | 0.026774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1024-34_0_6_line_25 |  | 22 | 24 | 0.037323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1024-34_0_6_line_26 |  | 23 | 68 | 0.015526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1024-34_0_6_line_27 |  | 25 | 26 | 0.013321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1024-34_0_6_line_28 |  | 25 | 27 | 0.030556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1024-34_0_6_line_29 |  | 25 | 28 | 0.025456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1024-34_0_6_line_30 |  | 26 | 73 | 0.002665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1024-34_0_6_line_31 |  | 26 | 74 | 0.019746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1024-34_0_6_line_32 |  | 27 | 52 | 0.023802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1024-34_0_6_line_33 |  | 27 | 33 | 0.067327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
34 | LV_1024-34_0_6_line_34 |  | 27 | 36 | 0.041584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1024-34_0_6_line_35 |  | 28 | 75 | 0.024286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1024-34_0_6_line_36 |  | 29 | 30 | 0.11134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
37 | LV_1024-34_0_6_line_37 |  | 29 | 31 | 0.070489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1024-34_0_6_line_38 |  | 29 | 32 | 0.032966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
39 | LV_1024-34_0_6_line_39 |  | 30 | 41 | 0.055553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1024-34_0_6_line_40 |  | 30 | 42 | 0.026574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
41 | LV_1024-34_0_6_line_41 |  | 31 | 76 | 0.22938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1024-34_0_6_line_42 |  | 32 | 33 | 0.029919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
43 | LV_1024-34_0_6_line_43 |  | 33 | 34 | 0.030467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
44 | LV_1024-34_0_6_line_44 |  | 34 | 62 | 0.025958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1024-34_0_6_line_45 |  | 35 | 36 | 0.042275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1024-34_0_6_line_46 |  | 35 | 37 | 0.056757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1024-34_0_6_line_47 |  | 35 | 38 | 0.024313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1024-34_0_6_line_48 |  | 36 | 44 | 0.020962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1024-34_0_6_line_49 |  | 37 | 45 | 0.036055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1024-34_0_6_line_50 |  | 37 | 46 | 0.075657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1024-34_0_6_line_51 |  | 38 | 39 | 0.020103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1024-34_0_6_line_52 |  | 39 | 40 | 0.020296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1024-34_0_6_line_53 |  | 40 | 49 | 0.013636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1024-34_0_6_line_54 |  | 42 | 43 | 0.004778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1024-34_0_6_line_55 |  | 44 | 77 | 0.029183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1024-34_0_6_line_56 |  | 47 | 48 | 0.014367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1024-34_0_6_line_57 |  | 47 | 49 | 0.010739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1024-34_0_6_line_58 |  | 48 | 50 | 0.079416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1024-34_0_6_line_59 |  | 50 | 51 | 0.039435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1024-34_0_6_line_60 |  | 51 | 67 | 0.065272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1024-34_0_6_line_61 |  | 53 | 54 | 0.040089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1024-34_0_6_line_62 |  | 53 | 55 | 0.027513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1024-34_0_6_line_63 |  | 53 | 56 | 0.040356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1024-34_0_6_line_64 |  | 55 | 57 | 0.010908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1024-34_0_6_line_65 |  | 56 | 83 | 0.0085706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1024-34_0_6_line_66 |  | 57 | 87 | 0.018402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1024-34_0_6_line_67 |  | 58 | 59 | 0.020112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1024-34_0_6_line_68 |  | 58 | 60 | 0.019842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1024-34_0_6_line_69 |  | 58 | 61 | 0.036762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1024-34_0_6_line_70 |  | 60 | 87 | 0.015149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1024-34_0_6_line_71 |  | 61 | 78 | 0.01166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1024-34_0_6_line_72 |  | 61 | 79 | 0.015577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1024-34_0_6_line_73 |  | 62 | 63 | 0.031384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1024-34_0_6_line_74 |  | 63 | 85 | 0.0042542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1024-34_0_6_line_75 |  | 63 | 88 | 0.048637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1024-34_0_6_line_76 |  | 64 | 65 | 0.008575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1024-34_0_6_line_77 |  | 64 | 66 | 0.052623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1024-34_0_6_line_78 |  | 65 | 89 | 0.030557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1024-34_0_6_line_79 |  | 65 | 82 | 0.015812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1024-34_0_6_line_80 |  | 66 | 90 | 0.026806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1024-34_0_6_line_81 |  | 68 | 91 | 0.011432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1024-34_0_6_line_82 |  | 70 | 71 | 0.005297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1024-34_0_6_line_83 |  | 70 | 72 | 0.038158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1024-34_0_6_line_84 |  | 72 | 107 | 0.028349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1024-34_0_6_line_85 |  | 72 | 75 | 0.025599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1024-34_0_6_line_86 |  | 79 | 96 | 0.012767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1024-34_0_6_line_87 |  | 80 | 81 | 0.0036256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1024-34_0_6_line_88 |  | 81 | 109 | 0.017318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1024-34_0_6_line_89 |  | 83 | 112 | 0.044518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1024-34_0_6_line_90 |  | 84 | 85 | 0.044443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1024-34_0_6_line_91 |  | 84 | 86 | 0.013622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1024-34_0_6_line_92 |  | 86 | 95 | 0.014535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1024-34_0_6_line_93 |  | 88 | 109 | 0.0047416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1024-34_0_6_line_94 |  | 89 | 103 | 0.0033592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1024-34_0_6_line_95 |  | 90 | 116 | 0.032793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1024-34_0_6_line_96 |  | 92 | 93 | 0.0069193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1024-34_0_6_line_97 |  | 92 | 94 | 0.035292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1024-34_0_6_line_98 |  | 94 | 117 | 0.011341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1024-34_0_6_line_99 |  | 95 | 96 | 0.0097547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1024-34_0_6_line_100 |  | 97 | 98 | 0.0029445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1024-34_0_6_line_101 |  | 97 | 99 | 0.025558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1024-34_0_6_line_102 |  | 98 | 100 | 0.022306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1024-34_0_6_line_103 |  | 99 | 101 | 0.015493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1024-34_0_6_line_104 |  | 99 | 102 | 0.089173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1024-34_0_6_line_105 |  | 100 | 103 | 0.074565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1024-34_0_6_line_106 |  | 101 | 104 | 0.040094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1024-34_0_6_line_107 |  | 102 | 105 | 0.016351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1024-34_0_6_line_108 |  | 104 | 106 | 0.0057784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1024-34_0_6_line_109 |  | 105 | 107 | 0.017871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1024-34_0_6_line_110 |  | 105 | 108 | 0.003092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1024-34_0_6_line_111 |  | 106 | 114 | 0.025015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1024-34_0_6_line_112 |  | 107 | 115 | 0.002503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1024-34_0_6_line_113 |  | 110 | 111 | 0.00035642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1024-34_0_6_line_114 |  | 110 | 112 | 0.091689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1024-34_0_6_line_115 |  | 112 | 113 | 0.048095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1024-34_0_6_line_116 |  | 116 | 117 | 0.014625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1024-34_0_6_trafo_19 | 0.63 MVA 20/0.4 kV | 118 | 33 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18
0 | 2663132.3693 | 1215199.5346 | 2663132.1762 | 1215199.9093 | 2663139.8883 | 1215204.5383 | 2663136.4483 | 1215209.602
1 | 2663140.5965 | 1215183.5661 | 2663132.3693 | 1215199.5346
2 | 2663128.5616 | 1215220.6839 | 2663131.0245 | 1215217.5858 | 2663136.4483 | 1215209.602
3 | 2663094.748 | 1215196.0442 | 2663128.5616 | 1215220.6839
4 | 2663128.5616 | 1215220.6839 | 2663145.5214 | 1215233.0475
5 | 2663086.5414 | 1215190.0648 | 2663094.748 | 1215196.0442
6 | 2663201.3067 | 1215291.4093 | 2663164.0327 | 1215246.5422 | 2663145.5214 | 1215233.0475
7 | 2663086.5414 | 1215190.0648 | 2663105.5979 | 1215161.0929 | 2663109.2165 | 1215163.6023
8 | 2663086.5414 | 1215190.0648 | 2663072.7505 | 1215180.0109
9 | 2663201.3067 | 1215291.4093 | 2663211.086 | 1215266.3689
10 | 2663212.1712 | 1215262.8973 | 2663211.2047 | 1215266.0651 | 2663211.086 | 1215266.3689
11 | 2663212.1712 | 1215262.8973 | 2663216.7434 | 1215247.9126 | 2663216.8049 | 1215245.9256
12 | 2663207.0427 | 1215234.8041 | 2663216.9396 | 1215241.5774 | 2663216.8049 | 1215245.9256
13 | 2663072.7505 | 1215180.0109 | 2663030.7878 | 1215200.3601
14 | 2663165.2499 | 1215206.2079 | 2663174.252 | 1215212.3626
15 | 2663174.252 | 1215212.3626 | 2663193.5072 | 1215188.3184 | 2663211.0595 | 1215194.5416 | 2663220.578 | 1215199.9792 | 2663230.8183 | 1215204.6573 | 2663247.4583 | 1215219.5541 | 2663261.6109 | 1215220.5159 | 2663270.5982 | 1215222.3346 | 2663270.7685 | 1215217.022 | 2663286.4363 | 1215218.3335 | 2663287.7409 | 1215222.0496 | 2663288.7142 | 1215223.3607 | 2663290.5731 | 1215224.2366 | 2663292.5432 | 1215224.6466 | 2663294.2027 | 1215224.9867 | 2663294.7115 | 1215224.9809 | 2663297.6504 | 1215224.9788 | 2663299.9956 | 1215256.5677 | 2663301.0889 | 1215260.882
16 | 2663174.252 | 1215212.3626 | 2663186.3864 | 1215220.6672
17 | 2663301.0889 | 1215260.882 | 2663306.6812 | 1215260.5856 | 2663303.6968 | 1215224.8318 | 2663302.8074 | 1215214.1935 | 2663313.0015 | 1215213.9238 | 2663312.7296 | 1215211.6417 | 2663312.5968 | 1215210.5619
18 | 2663301.0889 | 1215260.882 | 2663273.7355 | 1215262.3037
19 | 2663186.3864 | 1215220.6672 | 2663207.0427 | 1215234.8041
20 | 2663309.9418 | 1215169.5305 | 2663309.8481 | 1215174.0656 | 2663308.8742 | 1215177.8132 | 2663306.9271 | 1215180.9611 | 2663306.0935 | 1215184.3655 | 2663306.4403 | 1215200.3346 | 2663307.6896 | 1215205.6845 | 2663309.7625 | 1215209.2865 | 2663312.5968 | 1215210.5619
21 | 2663312.5968 | 1215210.5619 | 2663320.4576 | 1215210.8634
22 | 2663309.9418 | 1215169.5305 | 2663308.9357 | 1215158.4352 | 2663308.5951 | 1215157.1811
23 | 2663320.4576 | 1215210.8634 | 2663323.0191 | 1215210.9617 | 2663335.1819 | 1215210.2409
24 | 2663371.2446 | 1215183.5236 | 2663372.6909 | 1215192.4778 | 2663372.4041 | 1215210.1746
25 | 2663372.4041 | 1215210.1746 | 2663365.55 | 1215209.1456 | 2663345.7701 | 1215209.6135 | 2663335.1819 | 1215210.2409
26 | 2663371.2446 | 1215183.5236 | 2663370.4679 | 1215178.7123 | 2663367.3688 | 1215168.5202
27 | 2663355.3718 | 1214974.2921 | 2663348.5217 | 1214985.7264
28 | 2663324.0931 | 1214990.5033 | 2663325.2195 | 1214987.4133 | 2663327.0423 | 1214982.3963 | 2663335.7992 | 1214985.2021 | 2663348.5217 | 1214985.7264
29 | 2663348.5217 | 1214985.7264 | 2663353.2053 | 1214985.9207 | 2663360.1158 | 1214987.384 | 2663373.0071 | 1214992.0349
30 | 2663353.2782 | 1214972.6355 | 2663355.3718 | 1214974.2921
31 | 2663363.6077 | 1214962.5279 | 2663366.1715 | 1214964.9566 | 2663357.4005 | 1214975.6256 | 2663355.3718 | 1214974.2921
32 | 2663324.0931 | 1214990.5033 | 2663322.702 | 1215001.3508 | 2663322.1355 | 1215006.7815 | 2663322.2835 | 1215014.1853
33 | 2663275.0296 | 1214986.6024 | 2663287.3679 | 1214986.1219 | 2663287.6013 | 1214978.4418 | 2663294.9916 | 1214977.6309 | 2663298.1669 | 1214977.5534 | 2663303.8413 | 1214977.4135 | 2663303.7469 | 1214982.0154 | 2663303.7294 | 1214982.9491 | 2663307.2651 | 1214982.5419 | 2663319.5963 | 1214986.3085 | 2663325.2195 | 1214987.4133 | 2663324.0931 | 1214990.5033
34 | 2663324.0931 | 1214990.5033 | 2663325.2195 | 1214987.4133 | 2663327.0423 | 1214982.3963 | 2663331.1301 | 1214977.2031 | 2663340.6806 | 1214956.7808 | 2663337.3819 | 1214954.889
35 | 2663373.0071 | 1214992.0349 | 2663389.7807 | 1215005.1101 | 2663391.8583 | 1215007.2998
36 | 2663280.9276 | 1215044.801 | 2663281.3571 | 1215047.9853 | 2663282.0891 | 1215053.4297 | 2663282.8418 | 1215059.0634 | 2663283.025 | 1215060.4106 | 2663284.5647 | 1215062.7395 | 2663284.6462 | 1215065.0752 | 2663285.9858 | 1215105.5589 | 2663286.0612 | 1215107.7499 | 2663283.5824 | 1215111.626 | 2663283.4831 | 1215114.5379 | 2663290.8427 | 1215110.8804 | 2663295.9539 | 1215107.9884 | 2663300.736 | 1215110.3517 | 2663302.1647 | 1215110.9673 | 2663306.4285 | 1215112.7914 | 2663306.3969 | 1215117.9054 | 2663306.9064 | 1215124.2814 | 2663308.045 | 1215127.1842
37 | 2663280.9276 | 1215044.801 | 2663277.6566 | 1215048.1794 | 2663266.0098 | 1215053.637 | 2663252.8316 | 1215055.9876 | 2663213.2937 | 1215055.8469
38 | 2663280.9276 | 1215044.801 | 2663280.3784 | 1215040.7371 | 2663280.1816 | 1215039.2452 | 2663282.4073 | 1215033.4652 | 2663283.1899 | 1215025.5686 | 2663283.0986 | 1215012.3379
39 | 2663308.045 | 1215127.1842 | 2663314.1296 | 1215122.0233 | 2663320.0141 | 1215119.9734 | 2663329.9955 | 1215116.8664 | 2663343.4581 | 1215113.4628 | 2663360.1286 | 1215110.1175
40 | 2663308.045 | 1215127.1842 | 2663308.984 | 1215129.5845 | 2663309.2355 | 1215130.2098 | 2663307.9574 | 1215132.5755 | 2663306.604 | 1215136.3078 | 2663305.5178 | 1215142.0443 | 2663305.3059 | 1215145.5553 | 2663306.1814 | 1215148.9223 | 2663307.3425 | 1215152.5702
41 | 2662990.2964 | 1215010.2384 | 2662992.3349 | 1215010.6136 | 2663023.3255 | 1215021.5478 | 2663064.6818 | 1215036.1162 | 2663084.0476 | 1215041.8134 | 2663103.5071 | 1215046.5555 | 2663117.8839 | 1215049.3427 | 2663140.9975 | 1215052.5227 | 2663165.7317 | 1215054.697 | 2663202.3622 | 1215055.808 | 2663213.2937 | 1215055.8469
42 | 2663275.0296 | 1214986.6024 | 2663275.1999 | 1214990.5844 | 2663278.4946 | 1214991.4199 | 2663280.6127 | 1214992.9211 | 2663282.2907 | 1214995.8073 | 2663282.9415 | 1214998.8939 | 2663283.0972 | 1215012.126 | 2663283.0986 | 1215012.3379
43 | 2663275.0296 | 1214986.6024 | 2663274.8668 | 1214982.6204 | 2663278.4094 | 1214981.5573 | 2663280.9047 | 1214979.0045 | 2663281.9995 | 1214975.3138 | 2663281.6769 | 1214959.954
44 | 2663281.1319 | 1214934.0013 | 2663281.6769 | 1214959.954
45 | 2663337.3819 | 1214954.889 | 2663340.6806 | 1214956.7808 | 2663347.2781 | 1214942.6755 | 2663347.4366 | 1214936.3399 | 2663340.9611 | 1214921.095
46 | 2663371.2346 | 1214904.4619 | 2663359.2295 | 1214917.1644 | 2663353.7579 | 1214928.9358 | 2663347.4366 | 1214936.3399 | 2663340.9611 | 1214921.095
47 | 2663340.9611 | 1214921.095 | 2663316.6641 | 1214921.9679
48 | 2663337.3819 | 1214954.889 | 2663342.3716 | 1214942.7234 | 2663342.6708 | 1214938.1571 | 2663341.5542 | 1214935.119
49 | 2663371.2346 | 1214904.4619 | 2663396.3115 | 1214930.3678
50 | 2663371.2346 | 1214904.4619 | 2663363.5064 | 1214887.7583 | 2663361.4447 | 1214875.9514 | 2663361.2155 | 1214860.3615 | 2663362.899 | 1214844.1583 | 2663365.5337 | 1214831.0352
51 | 2663297.6557 | 1214918.4225 | 2663304.418 | 1214922.4079 | 2663316.6641 | 1214921.9679
52 | 2663297.6557 | 1214918.4225 | 2663297.0637 | 1214898.1348
53 | 2663296.666 | 1214884.5048 | 2663297.0637 | 1214898.1348
54 | 2663307.3425 | 1215152.5702 | 2663307.3425 | 1215152.5702 | 2663308.5951 | 1215157.1811
55 | 2663317.8629 | 1214927.4648 | 2663323.9428 | 1214927.4516 | 2663338.6629 | 1214927.2522 | 2663341.5542 | 1214935.119
56 | 2663296.3528 | 1214873.77 | 2663297.0332 | 1214859.4193
57 | 2663296.3528 | 1214873.77 | 2663296.666 | 1214884.5048
58 | 2663297.9321 | 1214780.1177 | 2663296.8938 | 1214786.3439 | 2663296.8006 | 1214793.6919 | 2663297.3494 | 1214820.6811 | 2663297.8011 | 1214843.222 | 2663297.0332 | 1214859.4193
59 | 2663297.9321 | 1214780.1177 | 2663303.7886 | 1214764.9928 | 2663321.8917 | 1214779.5272
60 | 2663321.8917 | 1214779.5272 | 2663322.7111 | 1214784.6057 | 2663320.9437 | 1214808.0014 | 2663327.2432 | 1214844.1129
61 | 2663179.5893 | 1214991.8272 | 2663219.5966 | 1214989.2723
62 | 2663179.5893 | 1214991.8272 | 2663178.8015 | 1214980.8898 | 2663174.6047 | 1214973.4519 | 2663182.2105 | 1214975.9562
63 | 2663179.5893 | 1214991.8272 | 2663139.2852 | 1214993.8779
64 | 2663182.2105 | 1214975.9562 | 2663174.4889 | 1214968.252
65 | 2663139.2852 | 1214993.8779 | 2663130.7257 | 1214994.3134
66 | 2663174.4889 | 1214968.252 | 2663168.9092 | 1214962.6849 | 2663161.3586 | 1214955.3595
67 | 2663136.493 | 1214930.7441 | 2663122.4136 | 1214916.3827
68 | 2663136.493 | 1214930.7441 | 2663146.2 | 1214940.653 | 2663150.4857 | 1214944.8109
69 | 2663162.4087 | 1214904.6024 | 2663136.493 | 1214930.7441
70 | 2663161.3586 | 1214955.3595 | 2663150.4857 | 1214944.8109
71 | 2663162.4087 | 1214904.6024 | 2663154.3273 | 1214896.1976
72 | 2663162.4087 | 1214904.6024 | 2663173.5143 | 1214915.5248
73 | 2663249.667 | 1214934.8347 | 2663281.1319 | 1214934.0013
74 | 2663249.667 | 1214934.8347 | 2663245.4134 | 1214934.9036
75 | 2663249.667 | 1214934.8347 | 2663249.9995 | 1214927.8339 | 2663253.0482 | 1214903.907 | 2663249.8342 | 1214899.7592 | 2663244.348 | 1214895.743 | 2663240.1264 | 1214892.2781
76 | 2663507.5377 | 1214860.4623 | 2663515.9991 | 1214858.9292
77 | 2663515.9991 | 1214858.9292 | 2663527.5554 | 1214889.8158 | 2663534.6815 | 1214897.4187 | 2663537.2997 | 1214906.2641
78 | 2663507.5377 | 1214860.4623 | 2663507.4656 | 1214867.2324 | 2663508.7256 | 1214890.9852
79 | 2663507.5377 | 1214860.4623 | 2663502.4596 | 1214854.5156 | 2663497.5761 | 1214848.189
80 | 2663537.2997 | 1214906.2641 | 2663544.908 | 1214931.9676
81 | 2663367.3688 | 1215168.5202 | 2663365.9333 | 1215163.7994 | 2663367.2843 | 1215157.4431
82 | 2663359.256 | 1215025.4095 | 2663360.0661 | 1215030.6435
83 | 2663398.0131 | 1215030.7913 | 2663386.7586 | 1215030.7717 | 2663384.1439 | 1215031.7 | 2663364.5415 | 1215031.8474 | 2663360.0661 | 1215030.6435
84 | 2663419.6404 | 1215031.6218 | 2663409.8187 | 1215040.4005 | 2663398.0131 | 1215030.7913
85 | 2663398.0131 | 1215030.7913 | 2663397.0805 | 1215012.8036 | 2663391.8583 | 1215007.2998
86 | 2663182.6165 | 1214924.4769 | 2663173.5143 | 1214915.5248
87 | 2663220.2722 | 1214875.9828 | 2663223.0748 | 1214878.283
88 | 2663223.0748 | 1214878.283 | 2663236.4612 | 1214889.2699
89 | 2663086.2655 | 1214996.5755 | 2663130.7257 | 1214994.3134
90 | 2663207.9353 | 1214952.0696 | 2663224.7987 | 1214935.2379 | 2663245.4134 | 1214934.9036
91 | 2663207.9353 | 1214952.0696 | 2663204.0576 | 1214947.4812 | 2663203.8222 | 1214945.3329 | 2663199.9342 | 1214941.5091
92 | 2663189.5712 | 1214931.3169 | 2663199.9342 | 1214941.5091
93 | 2663240.1264 | 1214892.2781 | 2663236.4612 | 1214889.2699
94 | 2663508.9035 | 1214894.3397 | 2663508.7256 | 1214890.9852
95 | 2663544.1559 | 1214958.7955 | 2663541.4821 | 1214951.2244 | 2663548.3448 | 1214948.6182 | 2663549.181 | 1214946.4035 | 2663544.908 | 1214931.9676
96 | 2663573.714 | 1215006.6355 | 2663577.0895 | 1215002.7358 | 2663578.6936 | 1215002.0077
97 | 2663573.714 | 1215006.6355 | 2663564.0385 | 1215005.9542 | 2663560.2272 | 1215001.5887 | 2663556.6488 | 1214991.7556 | 2663554.11 | 1214986.9811 | 2663552.8028 | 1214983.2796
98 | 2663549.0261 | 1214972.5856 | 2663552.8028 | 1214983.2796
99 | 2663189.5712 | 1214931.3169 | 2663182.6165 | 1214924.4769
100 | 2663506.1189 | 1214989.5011 | 2663509.0582 | 1214989.3249 | 2663509.0582 | 1214989.3249
101 | 2663480.9747 | 1214988.5699 | 2663482.7859 | 1214989.6454 | 2663487.9628 | 1214990.5899 | 2663506.1189 | 1214989.5011
102 | 2663509.0582 | 1214989.3249 | 2663512.2973 | 1214986.8134 | 2663513.5683 | 1214982.2796 | 2663512.8533 | 1214968.7995
103 | 2663480.9747 | 1214988.5699 | 2663476.6281 | 1214985.9664 | 2663470.6811 | 1214977.4021
104 | 2663480.9747 | 1214988.5699 | 2663483.7073 | 1215002.9634 | 2663486.1181 | 1215015.4746 | 2663487.5709 | 1215022.3943 | 2663487.681 | 1215025.5975 | 2663487.225 | 1215026.3487 | 2663484.0596 | 1215026.9264 | 2663474.7011 | 1215025.715 | 2663472.282 | 1215023.2544 | 2663466.6345 | 1215018.0132 | 2663458.5429 | 1215013.3576 | 2663449.0487 | 1215005.6407 | 2663445.2575 | 1215007.9351 | 2663444.6191 | 1215008.4422
105 | 2663508.9035 | 1214894.3397 | 2663512.8533 | 1214968.7995
106 | 2663470.6811 | 1214977.4021 | 2663459.8438 | 1214961.7951 | 2663447.9524 | 1214944.3735
107 | 2663432.1983 | 1215019.0698 | 2663440.8382 | 1215011.4458 | 2663444.6191 | 1215008.4422
108 | 2663444.6947 | 1214939.6009 | 2663447.9524 | 1214944.3735
109 | 2663432.1983 | 1215019.0698 | 2663426.6239 | 1215026.2149 | 2663419.6404 | 1215031.6218
110 | 2663429.5034 | 1215017.5402 | 2663432.1983 | 1215019.0698
111 | 2663435.4332 | 1214917.0522 | 2663435.6703 | 1214923.3141 | 2663438.218 | 1214930.1121 | 2663444.6947 | 1214939.6009
112 | 2663417.5747 | 1215030.1989 | 2663419.6404 | 1215031.6218
113 | 2663028.6814 | 1214957.5598 | 2663028.6063 | 1214957.2113
114 | 2663086.2655 | 1214996.5755 | 2663037.7582 | 1214999.6757 | 2663028.6814 | 1214957.5598
115 | 2663086.2655 | 1214996.5755 | 2663076.8922 | 1214949.4028
116 | 2663544.1559 | 1214958.7955 | 2663549.0261 | 1214972.5856

## bus_geodata
| x | y | coords
0 | 2663132.3693 | 1215199.5346
1 | 2663136.4483 | 1215209.602
2 | 2663140.5965 | 1215183.5661
3 | 2663128.5616 | 1215220.6839
4 | 2663094.748 | 1215196.0442
5 | 2663145.5214 | 1215233.0475
6 | 2663086.5414 | 1215190.0648
7 | 2663201.3067 | 1215291.4093
8 | 2663211.086 | 1215266.3689
9 | 2663212.1712 | 1215262.8973
10 | 2663216.8049 | 1215245.9256
11 | 2663109.2165 | 1215163.6023
12 | 2663072.7505 | 1215180.0109
13 | 2663030.7878 | 1215200.3601
14 | 2663174.252 | 1215212.3626
15 | 2663165.2499 | 1215206.2079
16 | 2663301.0889 | 1215260.882
17 | 2663186.3864 | 1215220.6672
18 | 2663312.5968 | 1215210.5619
19 | 2663273.7355 | 1215262.3037
20 | 2663309.9418 | 1215169.5305
21 | 2663320.4576 | 1215210.8634
22 | 2663372.4041 | 1215210.1746
23 | 2663371.2446 | 1215183.5236
24 | 2663335.1819 | 1215210.2409
25 | 2663348.5217 | 1214985.7264
26 | 2663355.3718 | 1214974.2921
27 | 2663324.0931 | 1214990.5033
28 | 2663373.0071 | 1214992.0349
29 | 2663280.9276 | 1215044.801
30 | 2663308.045 | 1215127.1842
31 | 2663213.2937 | 1215055.8469
32 | 2663283.0986 | 1215012.3379
33 | 2663275.0296 | 1214986.6024
34 | 2663281.6769 | 1214959.954
35 | 2663340.9611 | 1214921.095
36 | 2663337.3819 | 1214954.889
37 | 2663371.2346 | 1214904.4619
38 | 2663316.6641 | 1214921.9679
39 | 2663297.6557 | 1214918.4225
40 | 2663297.0637 | 1214898.1348
41 | 2663360.1286 | 1215110.1175
42 | 2663307.3425 | 1215152.5702
43 | 2663308.5951 | 1215157.1811
44 | 2663341.5542 | 1214935.119
45 | 2663396.3115 | 1214930.3678
46 | 2663365.5337 | 1214831.0352
47 | 2663296.3528 | 1214873.77
48 | 2663297.0332 | 1214859.4193
49 | 2663296.666 | 1214884.5048
50 | 2663297.9321 | 1214780.1177
51 | 2663321.8917 | 1214779.5272
52 | 2663322.2835 | 1215014.1853
53 | 2663179.5893 | 1214991.8272
54 | 2663219.5966 | 1214989.2723
55 | 2663182.2105 | 1214975.9562
56 | 2663139.2852 | 1214993.8779
57 | 2663174.4889 | 1214968.252
58 | 2663136.493 | 1214930.7441
59 | 2663122.4136 | 1214916.3827
60 | 2663150.4856 | 1214944.8109
61 | 2663162.4087 | 1214904.6024
62 | 2663281.1319 | 1214934.0013
63 | 2663249.667 | 1214934.8347
64 | 2663515.9991 | 1214858.9292
65 | 2663507.5377 | 1214860.4623
66 | 2663537.2997 | 1214906.2641
67 | 2663327.2432 | 1214844.1129
68 | 2663367.3688 | 1215168.5202
69 | 2663207.0427 | 1215234.8041
70 | 2663360.0661 | 1215030.6435
71 | 2663359.256 | 1215025.4095
72 | 2663398.0131 | 1215030.7913
73 | 2663353.2782 | 1214972.6355
74 | 2663363.6077 | 1214962.5279
75 | 2663391.8583 | 1215007.2998
76 | 2662990.2964 | 1215010.2384
77 | 2663317.8629 | 1214927.4648
78 | 2663154.3273 | 1214896.1976
79 | 2663173.5143 | 1214915.5248
80 | 2663220.2722 | 1214875.9828
81 | 2663223.0748 | 1214878.283
82 | 2663497.5761 | 1214848.189
83 | 2663130.7257 | 1214994.3134
84 | 2663207.9353 | 1214952.0696
85 | 2663245.4134 | 1214934.9036
86 | 2663199.9342 | 1214941.5091
87 | 2663161.3586 | 1214955.3595
88 | 2663240.1264 | 1214892.2781
89 | 2663508.7256 | 1214890.9852
90 | 2663544.908 | 1214931.9676
91 | 2663367.2843 | 1215157.4431
92 | 2663573.714 | 1215006.6355
93 | 2663578.6936 | 1215002.0077
94 | 2663552.8028 | 1214983.2796
95 | 2663189.5712 | 1214931.3169
96 | 2663182.6165 | 1214924.4769
97 | 2663506.1189 | 1214989.5011
98 | 2663509.0582 | 1214989.3249
99 | 2663480.9747 | 1214988.5699
100 | 2663512.8533 | 1214968.7995
101 | 2663470.6811 | 1214977.4021
102 | 2663444.6191 | 1215008.4422
103 | 2663508.9035 | 1214894.3397
104 | 2663447.9524 | 1214944.3735
105 | 2663432.1983 | 1215019.0698
106 | 2663444.6947 | 1214939.6009
107 | 2663419.6404 | 1215031.6218
108 | 2663429.5034 | 1215017.5402
109 | 2663236.4612 | 1214889.2699
110 | 2663028.6814 | 1214957.5598
111 | 2663028.6063 | 1214957.2113
112 | 2663086.2655 | 1214996.5755
113 | 2663076.8922 | 1214949.4028
114 | 2663435.4332 | 1214917.0522
115 | 2663417.5747 | 1215030.1989
116 | 2663544.1559 | 1214958.7955
117 | 2663549.0261 | 1214972.5856
118 | 2663287.3679 | 1214986.1219

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97075 | -0.56457 | 0.009505 | 0.0023822
1 | 0.97096 | -0.56051 | 0.00061288 | 0.0001536
2 | 0.97067 | -0.56612 | 0.0046442 | 0.0011639
3 | 0.97115 | -0.55679 | 0 | 0
4 | 0.97066 | -0.56642 | 0 | 0
5 | 0.97168 | -0.54624 | 0.00061282 | 0.00015359
6 | 0.97054 | -0.56875 | 0 | 0
7 | 0.97379 | -0.50457 | 0 | 0
8 | 0.97449 | -0.49082 | 0.0034402 | 0.0008622
9 | 0.9746 | -0.48874 | 0.0018482 | 0.0004632
10 | 0.97514 | -0.47801 | 0.0028234 | 0.00070761
11 | 0.97028 | -0.57401 | 0.007264 | 0.0018205
12 | 0.97046 | -0.5704 | 0.00030765 | 7.7104e-05
13 | 0.97025 | -0.57462 | 0.0048882 | 0.0012251
14 | 0.97719 | -0.43792 | 0 | 0
15 | 0.97715 | -0.43877 | 0.004276 | 0.0010717
16 | 0.98524 | -0.28155 | 0 | 0
17 | 0.97662 | -0.44902 | 0.0015629 | 0.00039169
18 | 0.98824 | -0.22412 | 0 | 0
19 | 0.98516 | -0.28311 | 0.0031642 | 0.00079302
20 | 0.99067 | -0.17759 | 0 | 0
21 | 0.98816 | -0.22554 | 0.0024318 | 0.00060946
22 | 0.98786 | -0.23145 | 0 | 0
23 | 0.98772 | -0.23423 | 0 | 0
24 | 0.98806 | -0.22757 | 0.0018874 | 0.00047302
25 | 0.99158 | -0.1608 | 0 | 0
26 | 0.99137 | -0.16487 | 0 | 0
27 | 0.9938 | -0.11808 | 0 | 0
28 | 0.99013 | -0.18872 | 0.010025 | 0.0025124
29 | 0.99606 | -0.074921 | 0 | 0
30 | 0.99242 | -0.14404 | 0 | 0
31 | 0.99333 | -0.12759 | 0.040627 | 0.010182
32 | 0.99778 | -0.042305 | 0.04906 | 0.012296
33 | 1 | 0 | -0.51774 | -0.13154
34 | 0.99793 | -0.03952 | 0.043441 | 0.010887
35 | 0.98561 | -0.27591 | 0 | 0
36 | 0.98947 | -0.20115 | 0 | 0
37 | 0.98291 | -0.32847 | 0 | 0
38 | 0.98455 | -0.29663 | 0.015042 | 0.0037699
39 | 0.98395 | -0.30836 | 0 | 0
40 | 0.98334 | -0.32021 | 0.0084673 | 0.0021221
41 | 0.99216 | -0.14913 | 0.0051755 | 0.0012971
42 | 0.99162 | -0.15939 | 0.0040001 | 0.0010025
43 | 0.99135 | -0.16457 | 0.0022893 | 0.00057376
44 | 0.98921 | -0.20628 | 0.0098411 | 0.0024664
45 | 0.98136 | -0.35875 | 0.046474 | 0.011648
46 | 0.98256 | -0.3353 | 0.0050006 | 0.0012533
47 | 0.98288 | -0.3291 | 0 | 0
48 | 0.98268 | -0.33312 | 0.011565 | 0.0028984
49 | 0.98304 | -0.3261 | 0.0084673 | 0.0021221
50 | 0.98239 | -0.33874 | 0 | 0
51 | 0.98225 | -0.34153 | 0 | 0
52 | 0.99362 | -0.12156 | 0.0082761 | 0.0020742
53 | 0.98392 | -0.30978 | 0 | 0
54 | 0.98345 | -0.31901 | 0.012781 | 0.0032032
55 | 0.98472 | -0.29428 | 0 | 0
56 | 0.98323 | -0.32326 | 0.0014349 | 0.00035963
57 | 0.98503 | -0.28814 | 0.00031769 | 7.9621e-05
58 | 0.9866 | -0.25765 | 0 | 0
59 | 0.9866 | -0.25775 | 0.00027097 | 6.7911e-05
60 | 0.98601 | -0.26906 | 0.00029793 | 7.4667e-05
61 | 0.9877 | -0.23639 | 0 | 0
62 | 0.99543 | -0.087388 | 0 | 0
63 | 0.9924 | -0.14558 | 0 | 0
64 | 0.98115 | -0.36345 | 0 | 0
65 | 0.98117 | -0.36289 | 0 | 0
66 | 0.98097 | -0.36685 | 0.0005787 | 0.00014504
67 | 0.98201 | -0.34614 | 0.003914 | 0.00098093
68 | 0.98763 | -0.23584 | 0.0017533 | 0.00043942
69 | 0.97569 | -0.46724 | 0.0038318 | 0.00096034
70 | 0.98762 | -0.23732 | 0 | 0
71 | 0.98758 | -0.23799 | 0.0070518 | 0.0017674
72 | 0.98787 | -0.23252 | 0 | 0
73 | 0.99135 | -0.1652 | 0.0070878 | 0.0017764
74 | 0.99118 | -0.16842 | 0.010141 | 0.0025417
75 | 0.98897 | -0.21111 | 0.0048917 | 0.001226
76 | 0.99296 | -0.1348 | 0.0017766 | 0.00044527
77 | 0.9891 | -0.20831 | 0.0039071 | 0.00097922
78 | 0.98767 | -0.23689 | 0.0024183 | 0.00060609
79 | 0.9882 | -0.22672 | 0.00030265 | 7.5851e-05
80 | 0.99133 | -0.16626 | 0.004304 | 0.0010787
81 | 0.99135 | -0.16599 | 0.0026627 | 0.00066735
82 | 0.98107 | -0.36496 | 0.0072122 | 0.0018075
83 | 0.9831 | -0.3259 | 0.0039293 | 0.00098478
84 | 0.99002 | -0.19137 | 0 | 0
85 | 0.99207 | -0.15198 | 0.034982 | 0.0087673
86 | 0.9894 | -0.20348 | 0.014655 | 0.0036728
87 | 0.98557 | -0.27769 | 0.00013206 | 3.3098e-05
88 | 0.9915 | -0.16295 | 0.0095073 | 0.0023828
89 | 0.98148 | -0.35692 | 0.0022015 | 0.00055175
90 | 0.9809 | -0.3683 | 0.00062016 | 0.00015543
91 | 0.98759 | -0.23667 | 0.0040598 | 0.0010175
92 | 0.98077 | -0.37083 | 0 | 0
93 | 0.98077 | -0.37091 | 0.00062085 | 0.0001556
94 | 0.98079 | -0.37044 | 0.00057335 | 0.0001437
95 | 0.98893 | -0.21262 | 0.00010956 | 2.7459e-05
96 | 0.98861 | -0.21873 | 0.00011801 | 2.9576e-05
97 | 0.98299 | -0.32744 | 0.00032521 | 8.1504e-05
98 | 0.98294 | -0.32839 | 0.00031728 | 7.9517e-05
99 | 0.98342 | -0.31902 | 0 | 0
100 | 0.98257 | -0.33549 | 0.002304 | 0.00057743
101 | 0.98327 | -0.32194 | 0.0023682 | 0.00059353
102 | 0.98578 | -0.27296 | 0.0016499 | 0.00041351
103 | 0.98152 | -0.35613 | 0.002329 | 0.00058371
104 | 0.98297 | -0.32779 | 0.0025527 | 0.00063977
105 | 0.98624 | -0.26406 | 0 | 0
106 | 0.98294 | -0.32837 | 0.0024781 | 0.00062106
107 | 0.98682 | -0.2527 | 0 | 0
108 | 0.98622 | -0.26434 | 0.0050991 | 0.0012779
109 | 0.99146 | -0.16385 | 0.0036876 | 0.00092419
110 | 0.98167 | -0.35383 | 0.0047414 | 0.0011883
111 | 0.98167 | -0.35386 | 0.0057297 | 0.001436
112 | 0.98256 | -0.33648 | 0 | 0
113 | 0.98244 | -0.33882 | 0.002693 | 0.00067493
114 | 0.98287 | -0.32975 | 0.0030558 | 0.00076586
115 | 0.98681 | -0.2529 | 0.0043468 | 0.0010894
116 | 0.98083 | -0.36971 | 0.00057004 | 0.00014286
117 | 0.9808 | -0.37019 | 0.00060544 | 0.00015174
118 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.01415 | -0.0035461 | 0.014152 | 0.0035477 | 2.741e-06 | 1.5621e-06 | 0.021689 | 0.021689 | 0.021689 | 0.97075 | -0.56457 | 0.97096 | -0.56051 | 5.9585
1 | 0.0046445 | 0.0011639 | -0.0046442 | -0.0011639 | 3.4143e-07 | -3.5501e-09 | 0.0071193 | 0.0071194 | 0.0071194 | 0.97075 | -0.56457 | 0.97067 | -0.56612 | 1.9559
2 | -0.014765 | -0.0037013 | 0.014768 | 0.0037028 | 2.6132e-06 | 1.5041e-06 | 0.022628 | 0.022628 | 0.022628 | 0.97096 | -0.56051 | 0.97115 | -0.55679 | 6.2166
3 | 0.01247 | 0.0031274 | -0.012464 | -0.0031243 | 5.7177e-06 | 3.1429e-06 | 0.019108 | 0.019108 | 0.019108 | 0.97115 | -0.55679 | 0.97066 | -0.56642 | 5.2495
4 | -0.027238 | -0.0068302 | 0.027252 | 0.0068387 | 1.3709e-05 | 8.5142e-06 | 0.041736 | 0.041736 | 0.041736 | 0.97115 | -0.55679 | 0.97168 | -0.54624 | 11.4659
5 | 0.012464 | 0.0031243 | -0.012463 | -0.0031235 | 1.3877e-06 | 7.6285e-07 | 0.019108 | 0.019108 | 0.019108 | 0.97066 | -0.56642 | 0.97054 | -0.56875 | 5.2495
6 | -0.027864 | -0.0069923 | 0.02792 | 0.0070268 | 5.5478e-05 | 3.4498e-05 | 0.042674 | 0.042674 | 0.042674 | 0.97168 | -0.54624 | 0.97379 | -0.50457 | 11.7237
7 | 0.0072658 | 0.0018212 | -0.007264 | -0.0018205 | 1.8187e-06 | 6.8116e-07 | 0.01114 | 0.01114 | 0.01114 | 0.97054 | -0.56875 | 0.97028 | -0.57401 | 3.0605
8 | 0.0051972 | 0.0013023 | -0.0051968 | -0.0013022 | 4.0635e-07 | 4.9178e-08 | 0.0079682 | 0.0079683 | 0.0079683 | 0.97054 | -0.56875 | 0.97046 | -0.5704 | 2.1891
9 | -0.02792 | -0.0070268 | 0.027938 | 0.0070382 | 1.8358e-05 | 1.1414e-05 | 0.042674 | 0.042674 | 0.042674 | 0.97379 | -0.50457 | 0.97449 | -0.49082 | 11.7236
10 | -0.031378 | -0.0079004 | 0.031382 | 0.0079024 | 3.1338e-06 | 1.9603e-06 | 0.047927 | 0.047927 | 0.047927 | 0.97449 | -0.49082 | 0.9746 | -0.48874 | 13.1668
11 | -0.03323 | -0.0083656 | 0.033247 | 0.0083763 | 1.7051e-05 | 1.0692e-05 | 0.050749 | 0.050749 | 0.050749 | 0.9746 | -0.48874 | 0.97514 | -0.47801 | 13.942
12 | -0.03607 | -0.0090839 | 0.036089 | 0.0090956 | 1.8578e-05 | 1.1686e-05 | 0.055057 | 0.055057 | 0.055057 | 0.97514 | -0.47801 | 0.97569 | -0.46724 | 15.1256
13 | 0.0048892 | 0.0012251 | -0.0048882 | -0.0012251 | 9.8286e-07 | 5.2932e-08 | 0.0074965 | 0.0074967 | 0.0074967 | 0.97046 | -0.5704 | 0.97025 | -0.57462 | 2.0595
14 | 0.0042762 | 0.0010716 | -0.004276 | -0.0010717 | 1.7306e-07 | -2.5586e-08 | 0.0065116 | 0.0065116 | 0.0065116 | 0.97719 | -0.43792 | 0.97715 | -0.43877 | 1.7889
15 | -0.045817 | -0.011555 | 0.046162 | 0.011774 | 0.00034575 | 0.00021889 | 0.069793 | 0.069793 | 0.069793 | 0.97719 | -0.43792 | 0.98524 | -0.28155 | 19.174
16 | 0.04154 | 0.010484 | -0.041518 | -0.01047 | 2.2082e-05 | 1.3948e-05 | 0.063282 | 0.063282 | 0.063282 | 0.97719 | -0.43792 | 0.97662 | -0.44902 | 17.3852
17 | -0.049327 | -0.012567 | 0.049464 | 0.012654 | 0.00013709 | 8.6895e-05 | 0.074572 | 0.074571 | 0.074572 | 0.98524 | -0.28155 | 0.98824 | -0.22412 | 20.4867
18 | 0.0031644 | 0.00079282 | -0.0031642 | -0.00079302 | 2.3461e-07 | -1.9864e-07 | 0.0047791 | 0.0047793 | 0.0047793 | 0.98524 | -0.28155 | 0.98516 | -0.28311 | 1.313
19 | 0.039955 | 0.010078 | -0.039921 | -0.010056 | 3.4814e-05 | 2.1968e-05 | 0.060901 | 0.060901 | 0.060901 | 0.97662 | -0.44902 | 0.97569 | -0.46724 | 16.731
20 | -0.0596 | -0.015194 | 0.059734 | 0.01528 | 0.0001342 | 8.5319e-05 | 0.089834 | 0.089833 | 0.089834 | 0.98824 | -0.22412 | 0.99067 | -0.17759 | 24.6796
21 | 0.010136 | 0.0025404 | -0.010136 | -0.0025401 | 6.8717e-07 | 3.3901e-07 | 0.015262 | 0.015262 | 0.015262 | 0.98824 | -0.22412 | 0.98816 | -0.22554 | 4.193
22 | -0.059734 | -0.01528 | 0.059772 | 0.015303 | 3.7648e-05 | 2.3934e-05 | 0.089833 | 0.089833 | 0.089833 | 0.99067 | -0.17759 | 0.99135 | -0.16457 | 24.6795
23 | 0.0077037 | 0.0019306 | -0.007703 | -0.0019303 | 7.4423e-07 | 2.8741e-07 | 0.011601 | 0.011601 | 0.011601 | 0.98816 | -0.22554 | 0.98806 | -0.22757 | 3.187
24 | 0.0058145 | 0.0014571 | -0.0058138 | -0.001457 | 7.7019e-07 | 1.5019e-07 | 0.0087584 | 0.0087585 | 0.0087585 | 0.98786 | -0.23145 | 0.98772 | -0.23423 | 2.4062
25 | -0.0058145 | -0.0014571 | 0.0058156 | 0.0014573 | 1.0736e-06 | 2.0918e-07 | 0.0087584 | 0.0087582 | 0.0087584 | 0.98786 | -0.23145 | 0.98806 | -0.22757 | 2.4062
26 | 0.0058138 | 0.001457 | -0.0058133 | -0.0014569 | 4.4665e-07 | 8.715e-08 | 0.0087585 | 0.0087586 | 0.0087586 | 0.98772 | -0.23423 | 0.98763 | -0.23584 | 2.4062
27 | 0.017234 | 0.0043209 | -0.017231 | -0.0043189 | 3.3415e-06 | 1.9668e-06 | 0.025863 | 0.025863 | 0.025863 | 0.99158 | -0.1608 | 0.99137 | -0.16487 | 7.1054
28 | -0.079373 | -0.020026 | 0.079535 | 0.02013 | 0.00016269 | 0.00010373 | 0.11916 | 0.11916 | 0.11916 | 0.99158 | -0.1608 | 0.9938 | -0.11808 | 32.7358
29 | 0.062138 | 0.015705 | -0.062055 | -0.015652 | 8.3088e-05 | 5.2849e-05 | 0.093295 | 0.093295 | 0.093295 | 0.99158 | -0.1608 | 0.99013 | -0.18872 | 25.6306
30 | 0.0070879 | 0.0017764 | -0.0070878 | -0.0017764 | 1.1311e-07 | 3.8031e-08 | 0.010639 | 0.010639 | 0.010639 | 0.99137 | -0.16487 | 0.99135 | -0.1652 | 2.9227
31 | 0.010143 | 0.0025425 | -0.010141 | -0.0025417 | 1.7164e-06 | 8.4392e-07 | 0.015225 | 0.015225 | 0.015225 | 0.99137 | -0.16487 | 0.99118 | -0.16842 | 4.1826
32 | 0.0082775 | 0.0020748 | -0.0082761 | -0.0020742 | 1.3711e-06 | 5.6916e-07 | 0.012394 | 0.012394 | 0.012394 | 0.9938 | -0.11808 | 0.99362 | -0.12156 | 3.405
33 | -0.2016 | -0.051147 | 0.20275 | 0.051882 | 0.0011519 | 0.00073549 | 0.30208 | 0.30208 | 0.30208 | 0.9938 | -0.11808 | 1 | 0 | 41.4942
34 | 0.11379 | 0.028942 | -0.11333 | -0.028653 | 0.00045345 | 0.00028967 | 0.17053 | 0.17053 | 0.17053 | 0.9938 | -0.11808 | 0.98947 | -0.20115 | 46.8477
35 | 0.052031 | 0.01314 | -0.051975 | -0.013104 | 5.5736e-05 | 3.5359e-05 | 0.07823 | 0.07823 | 0.07823 | 0.99013 | -0.18872 | 0.98897 | -0.21111 | 21.4917
36 | 0.071542 | 0.018368 | -0.071303 | -0.018218 | 0.00023916 | 0.00015017 | 0.10703 | 0.10703 | 0.10703 | 0.99606 | -0.074921 | 0.99242 | -0.14404 | 14.7024
37 | 0.042511 | 0.010692 | -0.042404 | -0.010625 | 0.00010665 | 6.7344e-05 | 0.06352 | 0.063521 | 0.063521 | 0.99606 | -0.074921 | 0.99333 | -0.12759 | 17.4507
38 | -0.11405 | -0.02906 | 0.11423 | 0.029174 | 0.00017979 | 0.00011421 | 0.17055 | 0.17055 | 0.17055 | 0.99606 | -0.074921 | 0.99778 | -0.042305 | 23.4275
39 | 0.0051767 | 0.0012972 | -0.0051755 | -0.0012971 | 1.2551e-06 | 8.5638e-08 | 0.0077618 | 0.0077621 | 0.0077621 | 0.99242 | -0.14404 | 0.99216 | -0.14913 | 2.1324
40 | 0.066126 | 0.01692 | -0.066077 | -0.01689 | 4.9102e-05 | 3.0739e-05 | 0.099272 | 0.099272 | 0.099272 | 0.99242 | -0.14404 | 0.99162 | -0.15939 | 13.6363
41 | 0.0017772 | 0.00044269 | -0.0017766 | -0.00044527 | 6.095e-07 | -2.5782e-06 | 0.0026614 | 0.0026624 | 0.0026624 | 0.99333 | -0.12759 | 0.99296 | -0.1348 | 0.73143
42 | -0.16329 | -0.04147 | 0.16363 | 0.041682 | 0.00033321 | 0.00021247 | 0.24372 | 0.24372 | 0.24372 | 0.99778 | -0.042305 | 1 | 0 | 33.4776
43 | 0.14971 | 0.037975 | -0.14942 | -0.037794 | 0.00028389 | 0.00018089 | 0.22293 | 0.22293 | 0.22293 | 1 | 0 | 0.99793 | -0.03952 | 30.6221
44 | 0.10598 | 0.026907 | -0.10574 | -0.026751 | 0.00024348 | 0.00015549 | 0.15815 | 0.15815 | 0.15815 | 0.99793 | -0.03952 | 0.99543 | -0.087388 | 43.4489
45 | -0.099226 | -0.024978 | 0.099582 | 0.025205 | 0.00035596 | 0.00022727 | 0.14984 | 0.14984 | 0.14984 | 0.98561 | -0.27591 | 0.98947 | -0.20115 | 41.1662
46 | 0.051673 | 0.013026 | -0.051544 | -0.012943 | 0.00012963 | 8.2239e-05 | 0.07804 | 0.07804 | 0.07804 | 0.98561 | -0.27591 | 0.98291 | -0.32847 | 21.4397
47 | 0.047553 | 0.011952 | -0.047506 | -0.011923 | 4.7008e-05 | 2.9776e-05 | 0.071805 | 0.071805 | 0.071805 | 0.98561 | -0.27591 | 0.98455 | -0.29663 | 19.7266
48 | 0.013752 | 0.0034474 | -0.013749 | -0.0034455 | 3.3621e-06 | 1.8826e-06 | 0.020681 | 0.020681 | 0.020681 | 0.98947 | -0.20115 | 0.98921 | -0.20628 | 5.6817
49 | 0.046541 | 0.01169 | -0.046474 | -0.011648 | 6.7139e-05 | 4.2513e-05 | 0.070468 | 0.070468 | 0.070468 | 0.98291 | -0.32847 | 0.98136 | -0.35875 | 19.3593
50 | 0.0050022 | 0.0012534 | -0.0050006 | -0.0012533 | 1.6271e-06 | 8.2723e-08 | 0.0075727 | 0.007573 | 0.007573 | 0.98291 | -0.32847 | 0.98256 | -0.3353 | 2.0805
51 | 0.032464 | 0.0081527 | -0.032446 | -0.0081413 | 1.8153e-05 | 1.1362e-05 | 0.049071 | 0.049071 | 0.049071 | 0.98455 | -0.29663 | 0.98395 | -0.30836 | 13.4811
52 | 0.032446 | 0.0081413 | -0.032427 | -0.0081298 | 1.8327e-05 | 1.1472e-05 | 0.049071 | 0.049071 | 0.049071 | 0.98395 | -0.30836 | 0.98334 | -0.32021 | 13.4811
53 | 0.02396 | 0.0060077 | -0.023953 | -0.0060036 | 6.7224e-06 | 4.1294e-06 | 0.036258 | 0.036258 | 0.036258 | 0.98334 | -0.32021 | 0.98304 | -0.3261 | 9.9611
54 | 0.062077 | 0.015887 | -0.062061 | -0.015877 | 1.5587e-05 | 9.9141e-06 | 0.09327 | 0.09327 | 0.09327 | 0.99162 | -0.15939 | 0.99135 | -0.16457 | 25.6235
55 | 0.0039075 | 0.00097908 | -0.0039071 | -0.00097922 | 3.7809e-07 | -1.3262e-07 | 0.0058778 | 0.0058779 | 0.0058779 | 0.98921 | -0.20628 | 0.9891 | -0.20831 | 1.6148
56 | 0.015484 | 0.0038802 | -0.015481 | -0.0038785 | 2.9605e-06 | 1.7126e-06 | 0.023441 | 0.023441 | 0.023441 | 0.98288 | -0.3291 | 0.98268 | -0.33312 | 6.44
57 | -0.015484 | -0.0038802 | 0.015486 | 0.0038815 | 2.213e-06 | 1.2802e-06 | 0.023441 | 0.023441 | 0.023441 | 0.98288 | -0.3291 | 0.98304 | -0.3261 | 6.4399
58 | 0.0039164 | 0.00098015 | -0.0039153 | -0.00098049 | 1.0473e-06 | -3.3556e-07 | 0.0059299 | 0.0059302 | 0.0059302 | 0.98268 | -0.33312 | 0.98239 | -0.33874 | 1.6292
59 | 0.0039153 | 0.00098049 | -0.0039148 | -0.00098065 | 5.2008e-07 | -1.6638e-07 | 0.0059302 | 0.0059304 | 0.0059304 | 0.98239 | -0.33874 | 0.98225 | -0.34153 | 1.6292
60 | 0.0039148 | 0.00098065 | -0.003914 | -0.00098093 | 8.6089e-07 | -2.7503e-07 | 0.0059304 | 0.0059307 | 0.0059307 | 0.98225 | -0.34153 | 0.98201 | -0.34614 | 1.6293
61 | 0.012787 | 0.0032063 | -0.012781 | -0.0032032 | 5.622e-06 | 3.0891e-06 | 0.019338 | 0.019338 | 0.019338 | 0.98392 | -0.30978 | 0.98345 | -0.31901 | 5.3127
62 | -0.031345 | -0.007866 | 0.031368 | 0.0078805 | 2.3188e-05 | 1.4491e-05 | 0.047407 | 0.047407 | 0.047407 | 0.98392 | -0.30978 | 0.98472 | -0.29428 | 13.0239
63 | 0.018558 | 0.0046597 | -0.018546 | -0.0046526 | 1.1923e-05 | 7.1187e-06 | 0.028069 | 0.028069 | 0.028069 | 0.98392 | -0.30978 | 0.98323 | -0.32326 | 7.7113
64 | -0.031368 | -0.0078805 | 0.031377 | 0.0078862 | 9.1928e-06 | 5.7446e-06 | 0.047407 | 0.047407 | 0.047407 | 0.98472 | -0.29428 | 0.98503 | -0.28814 | 13.0239
65 | 0.017111 | 0.0042929 | -0.017109 | -0.0042917 | 2.1556e-06 | 1.2709e-06 | 0.025898 | 0.025898 | 0.025898 | 0.98323 | -0.32326 | 0.9831 | -0.3259 | 7.1147
66 | -0.031695 | -0.0079658 | 0.031711 | 0.0079757 | 1.5824e-05 | 9.8933e-06 | 0.047887 | 0.047887 | 0.047887 | 0.98503 | -0.28814 | 0.98557 | -0.27769 | 13.1557
67 | 0.00027097 | 6.7655e-05 | -0.00027097 | -6.7911e-05 | 1.2594e-09 | -2.5602e-07 | 0.00040859 | 0.00040868 | 0.00040868 | 0.9866 | -0.25765 | 0.9866 | -0.25775 | 0.11228
68 | 0.032171 | 0.0081027 | -0.032154 | -0.0080917 | 1.7529e-05 | 1.0965e-05 | 0.048536 | 0.048536 | 0.048536 | 0.9866 | -0.25765 | 0.98601 | -0.26906 | 13.334
69 | -0.032442 | -0.0081703 | 0.032475 | 0.008191 | 3.3024e-05 | 2.0665e-05 | 0.048944 | 0.048944 | 0.048944 | 0.9866 | -0.25765 | 0.9877 | -0.23639 | 13.4462
70 | 0.031856 | 0.008017 | -0.031843 | -0.0080088 | 1.3136e-05 | 8.2138e-06 | 0.048086 | 0.048086 | 0.048086 | 0.98601 | -0.26906 | 0.98557 | -0.27769 | 13.2105
71 | 0.0024184 | 0.00060597 | -0.0024183 | -0.00060609 | 5.804e-08 | -1.1208e-07 | 0.0036433 | 0.0036434 | 0.0036434 | 0.9877 | -0.23639 | 0.98767 | -0.23689 | 1.0009
72 | -0.034894 | -0.008797 | 0.03491 | 0.0088071 | 1.6154e-05 | 1.0139e-05 | 0.052587 | 0.052587 | 0.052587 | 0.9877 | -0.23639 | 0.9882 | -0.22672 | 14.4471
73 | 0.10574 | 0.026751 | -0.10545 | -0.026563 | 0.00029438 | 0.00018799 | 0.15815 | 0.15815 | 0.15815 | 0.99543 | -0.087388 | 0.9924 | -0.14558 | 43.449
74 | 0.085266 | 0.0215 | -0.08524 | -0.021483 | 2.6095e-05 | 1.6646e-05 | 0.12789 | 0.12789 | 0.12789 | 0.9924 | -0.14558 | 0.99207 | -0.15198 | 35.1359
75 | 0.02018 | 0.0050635 | -0.020163 | -0.0050534 | 1.67e-05 | 1.006e-05 | 0.03026 | 0.03026 | 0.03026 | 0.9924 | -0.14558 | 0.9915 | -0.16295 | 8.3131
76 | -0.0035696 | -0.00089273 | 0.0035696 | 0.00089268 | 9.4217e-08 | -4.8e-08 | 0.0054129 | 0.0054129 | 0.0054129 | 0.98115 | -0.36345 | 0.98117 | -0.36289 | 1.4871
77 | 0.0035696 | 0.00089273 | -0.003569 | -0.00089303 | 5.7822e-07 | -2.9441e-07 | 0.0054129 | 0.0054132 | 0.0054132 | 0.98115 | -0.36345 | 0.98097 | -0.36685 | 1.4871
78 | -0.010783 | -0.0027005 | 0.010786 | 0.0027021 | 3.0638e-06 | 1.5748e-06 | 0.016352 | 0.016352 | 0.016352 | 0.98117 | -0.36289 | 0.98148 | -0.35692 | 4.4922
79 | 0.0072129 | 0.0018078 | -0.0072122 | -0.0018075 | 7.0952e-07 | 2.5441e-07 | 0.010939 | 0.010939 | 0.010939 | 0.98117 | -0.36289 | 0.98107 | -0.36496 | 3.0052
80 | 0.0029903 | 0.00074799 | -0.0029901 | -0.0007482 | 2.0677e-07 | -2.0606e-07 | 0.0045354 | 0.0045355 | 0.0045355 | 0.98097 | -0.36685 | 0.9809 | -0.3683 | 1.246
81 | 0.00406 | 0.0010175 | -0.0040598 | -0.0010175 | 1.6042e-07 | -4.3626e-08 | 0.006117 | 0.006117 | 0.006117 | 0.98763 | -0.23584 | 0.98759 | -0.23667 | 1.6805
82 | 0.0070521 | 0.0017674 | -0.0070518 | -0.0017674 | 2.2425e-07 | 7.574e-08 | 0.010625 | 0.010625 | 0.010625 | 0.98762 | -0.23732 | 0.98758 | -0.23799 | 2.919
83 | -0.0070521 | -0.0017674 | 0.0070537 | 0.001768 | 1.6154e-06 | 5.4545e-07 | 0.010625 | 0.010625 | 0.010625 | 0.98762 | -0.23732 | 0.98787 | -0.23252 | 2.919
84 | 0.039981 | 0.01008 | -0.039943 | -0.010056 | 3.8584e-05 | 2.4331e-05 | 0.060245 | 0.060245 | 0.060245 | 0.98787 | -0.23252 | 0.98682 | -0.2527 | 16.5508
85 | -0.047035 | -0.011848 | 0.047083 | 0.011878 | 4.8214e-05 | 3.0529e-05 | 0.07087 | 0.07087 | 0.07087 | 0.98787 | -0.23252 | 0.98897 | -0.21111 | 19.4697
86 | -0.035212 | -0.008883 | 0.035226 | 0.0088914 | 1.347e-05 | 8.4572e-06 | 0.053043 | 0.053043 | 0.053043 | 0.9882 | -0.22672 | 0.98861 | -0.21873 | 14.5723
87 | -0.004304 | -0.0010787 | 0.0043041 | 0.0010787 | 5.6746e-08 | -1.0428e-08 | 0.0064604 | 0.0064604 | 0.0064604 | 0.99133 | -0.16626 | 0.99135 | -0.16599 | 1.7748
88 | -0.0069668 | -0.001746 | 0.0069675 | 0.0017463 | 7.1016e-07 | 2.3119e-07 | 0.010457 | 0.010457 | 0.010457 | 0.99135 | -0.16599 | 0.99146 | -0.16385 | 2.8729
89 | 0.01318 | 0.0033069 | -0.013173 | -0.0033032 | 6.6445e-06 | 3.6883e-06 | 0.01995 | 0.01995 | 0.01995 | 0.9831 | -0.3259 | 0.98256 | -0.33648 | 5.4809
90 | -0.050163 | -0.012656 | 0.050258 | 0.012716 | 9.4813e-05 | 6.0108e-05 | 0.075425 | 0.075425 | 0.075425 | 0.99002 | -0.19137 | 0.99207 | -0.15198 | 20.7212
91 | 0.050163 | 0.012656 | -0.050134 | -0.012637 | 2.906e-05 | 1.8423e-05 | 0.075425 | 0.075425 | 0.075425 | 0.99002 | -0.19137 | 0.9894 | -0.20348 | 20.7212
92 | 0.035479 | 0.0089647 | -0.035464 | -0.008955 | 1.5534e-05 | 9.7555e-06 | 0.053385 | 0.053385 | 0.053385 | 0.9894 | -0.20348 | 0.98893 | -0.21262 | 14.6663
93 | 0.010656 | 0.0026707 | -0.010655 | -0.0026704 | 4.5471e-07 | 2.2986e-07 | 0.015992 | 0.015992 | 0.015992 | 0.9915 | -0.16295 | 0.99146 | -0.16385 | 4.3933
94 | -0.012987 | -0.0032538 | 0.012988 | 0.0032541 | 4.8835e-07 | 2.7009e-07 | 0.019689 | 0.019689 | 0.019689 | 0.98148 | -0.35692 | 0.98152 | -0.35613 | 5.4092
95 | 0.0023699 | 0.00059277 | -0.0023697 | -0.00059308 | 1.5891e-07 | -3.122e-07 | 0.0035947 | 0.0035949 | 0.0035949 | 0.9809 | -0.3683 | 0.98083 | -0.36971 | 0.9876
96 | 0.00062085 | 0.00015551 | -0.00062085 | -0.0001556 | 2.3022e-09 | -8.5845e-08 | 0.00094192 | 0.00094195 | 0.00094195 | 0.98077 | -0.37083 | 0.98077 | -0.37091 | 0.25878
97 | -0.00062085 | -0.00015551 | 0.00062086 | 0.00015508 | 1.174e-08 | -4.3786e-07 | 0.00094192 | 0.00094176 | 0.00094192 | 0.98077 | -0.37083 | 0.98079 | -0.37044 | 0.25877
98 | -0.0011942 | -0.00029877 | 0.0011942 | 0.00029864 | 1.3958e-08 | -1.342e-07 | 0.0018116 | 0.0018116 | 0.0018116 | 0.98079 | -0.37044 | 0.9808 | -0.37019 | 0.4977
99 | 0.035354 | 0.0089275 | -0.035344 | -0.008921 | 1.0361e-05 | 6.506e-06 | 0.053221 | 0.053221 | 0.053221 | 0.98893 | -0.21262 | 0.98861 | -0.21873 | 14.621
100 | 0.01796 | 0.0045075 | -0.017959 | -0.004507 | 8.1628e-07 | 4.8509e-07 | 0.027189 | 0.027189 | 0.027189 | 0.98299 | -0.32744 | 0.98294 | -0.32839 | 7.4696
101 | -0.018285 | -0.004589 | 0.018292 | 0.0045934 | 7.3439e-06 | 4.376e-06 | 0.027682 | 0.027681 | 0.027682 | 0.98299 | -0.32744 | 0.98342 | -0.31902 | 7.6048
102 | 0.017642 | 0.0044275 | -0.017636 | -0.0044239 | 5.9673e-06 | 3.5364e-06 | 0.026709 | 0.026709 | 0.026709 | 0.98294 | -0.32839 | 0.98257 | -0.33549 | 7.3377
103 | 0.010459 | 0.0026217 | -0.010457 | -0.002621 | 1.4551e-06 | 7.3473e-07 | 0.015826 | 0.015826 | 0.015826 | 0.98342 | -0.31902 | 0.98327 | -0.32194 | 4.3477
104 | -0.028751 | -0.0072151 | 0.028815 | 0.0072545 | 6.3296e-05 | 3.9376e-05 | 0.043507 | 0.043507 | 0.043507 | 0.98342 | -0.31902 | 0.98578 | -0.27296 | 11.9525
105 | 0.015332 | 0.0038465 | -0.015317 | -0.0038378 | 1.5076e-05 | 8.7053e-06 | 0.02322 | 0.02322 | 0.02322 | 0.98257 | -0.33549 | 0.98152 | -0.35613 | 6.3792
106 | 0.0080892 | 0.0020275 | -0.008087 | -0.0020265 | 2.2532e-06 | 9.3367e-07 | 0.012242 | 0.012242 | 0.012242 | 0.98327 | -0.32194 | 0.98297 | -0.32779 | 3.3632
107 | -0.030464 | -0.007668 | 0.030477 | 0.0076761 | 1.2973e-05 | 8.0943e-06 | 0.045997 | 0.045997 | 0.045997 | 0.98578 | -0.27296 | 0.98624 | -0.26406 | 12.6366
108 | 0.0055342 | 0.0013868 | -0.0055341 | -0.0013867 | 1.5208e-07 | 2.4088e-08 | 0.0083776 | 0.0083777 | 0.0083777 | 0.98297 | -0.32779 | 0.98294 | -0.32837 | 2.3016
109 | -0.035577 | -0.008954 | 0.035596 | 0.0089661 | 1.9319e-05 | 1.2136e-05 | 0.053691 | 0.05369 | 0.053691 | 0.98624 | -0.26406 | 0.98682 | -0.2527 | 14.7501
110 | 0.0050991 | 0.0012779 | -0.0050991 | -0.0012779 | 6.863e-08 | 4.4676e-09 | 0.0076934 | 0.0076935 | 0.0076935 | 0.98624 | -0.26406 | 0.98622 | -0.26434 | 2.1136
111 | 0.003056 | 0.00076567 | -0.0030558 | -0.00076586 | 2.0077e-07 | -1.8856e-07 | 0.0046262 | 0.0046264 | 0.0046264 | 0.98294 | -0.32837 | 0.98287 | -0.32975 | 1.271
112 | 0.0043469 | 0.0010894 | -0.0043468 | -0.0010894 | 4.0325e-08 | -6.1695e-09 | 0.0065545 | 0.0065546 | 0.0065546 | 0.98682 | -0.2527 | 0.98681 | -0.2529 | 1.8007
113 | 0.0057297 | 0.001436 | -0.0057297 | -0.001436 | 1.0082e-08 | 1.9461e-09 | 0.0086851 | 0.0086851 | 0.0086851 | 0.98167 | -0.35383 | 0.98167 | -0.35386 | 2.386
114 | -0.010471 | -0.0026243 | 0.01048 | 0.0026287 | 8.6618e-06 | 4.3833e-06 | 0.015872 | 0.015872 | 0.015872 | 0.98167 | -0.35383 | 0.98256 | -0.33648 | 4.3605
115 | 0.0026933 | 0.00067452 | -0.002693 | -0.00067493 | 3.0005e-07 | -4.1705e-07 | 0.0040787 | 0.0040789 | 0.0040789 | 0.98256 | -0.33648 | 0.98244 | -0.33882 | 1.1206
116 | 0.0017997 | 0.00045022 | -0.0017997 | -0.00045037 | 4.0877e-08 | -1.5842e-07 | 0.0027301 | 0.0027301 | 0.0027301 | 0.98083 | -0.36971 | 0.9808 | -0.37019 | 0.75003

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.51774 | 0.13154

## res_load
| p_mw | q_mvar
0 | 0.009505 | 0.0023822
1 | 0.00061288 | 0.0001536
2 | 0.0046442 | 0.0011639
3 | 0.00061282 | 0.00015359
4 | 0.0034402 | 0.0008622
5 | 0.0018482 | 0.0004632
6 | 0.0028234 | 0.00070761
7 | 0.007264 | 0.0018205
8 | 0.00030765 | 7.7104e-05
9 | 0.0048882 | 0.0012251
10 | 0.004276 | 0.0010717
11 | 0.0015629 | 0.00039169
12 | 0.0031642 | 0.00079302
13 | 0.0024318 | 0.00060946
14 | 0.0018874 | 0.00047302
15 | 0.010025 | 0.0025124
16 | 0.040627 | 0.010182
17 | 0.04906 | 0.012296
18 | 0.043441 | 0.010887
19 | 0.015042 | 0.0037699
20 | 0.0084673 | 0.0021221
21 | 0.0051755 | 0.0012971
22 | 0.0040001 | 0.0010025
23 | 0.0022893 | 0.00057376
24 | 0.0098411 | 0.0024664
25 | 0.046474 | 0.011648
26 | 0.0050006 | 0.0012533
27 | 0.011565 | 0.0028984
28 | 0.0084673 | 0.0021221
29 | 0.0082761 | 0.0020742
30 | 0.012781 | 0.0032032
31 | 0.0014349 | 0.00035963
32 | 0.00031769 | 7.9621e-05
33 | 0.00027097 | 6.7911e-05
34 | 0.00029793 | 7.4667e-05
35 | 0.0005787 | 0.00014504
36 | 0.003914 | 0.00098093
37 | 0.0017533 | 0.00043942
38 | 0.0038318 | 0.00096034
39 | 0.0070518 | 0.0017674
40 | 0.0070878 | 0.0017764
41 | 0.010141 | 0.0025417
42 | 0.0048917 | 0.001226
43 | 0.0017766 | 0.00044527
44 | 0.0039071 | 0.00097922
45 | 0.0024183 | 0.00060609
46 | 0.00030265 | 7.5851e-05
47 | 0.004304 | 0.0010787
48 | 0.0026627 | 0.00066735
49 | 0.0072122 | 0.0018075
50 | 0.0039293 | 0.00098478
51 | 0.034982 | 0.0087673
52 | 0.014655 | 0.0036728
53 | 0.00013206 | 3.3098e-05
54 | 0.0095073 | 0.0023828
55 | 0.0022015 | 0.00055175
56 | 0.00062016 | 0.00015543
57 | 0.0040598 | 0.0010175
58 | 0.00062085 | 0.0001556
59 | 0.00057335 | 0.0001437
60 | 0.00010956 | 2.7459e-05
61 | 0.00011801 | 2.9576e-05
62 | 0.00032521 | 8.1504e-05
63 | 0.00031728 | 7.9517e-05
64 | 0.002304 | 0.00057743
65 | 0.0023682 | 0.00059353
66 | 0.0016499 | 0.00041351
67 | 0.002329 | 0.00058371
68 | 0.0025527 | 0.00063977
69 | 0.0024781 | 0.00062106
70 | 0.0050991 | 0.0012779
71 | 0.0036876 | 0.00092419
72 | 0.0047414 | 0.0011883
73 | 0.0057297 | 0.001436
74 | 0.002693 | 0.00067493
75 | 0.0030558 | 0.00076586
76 | 0.0043468 | 0.0010894
77 | 0.00057004 | 0.00014286
78 | 0.00060544 | 0.00015174

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1