## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1024-59_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1024-59_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1024-59_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1024-59_0_2_node_9 | 0.4 | n |  | TRUE
4 | bus_LV_1024-59_0_2_node_10 | 0.4 | n |  | TRUE
5 | bus_LV_1024-59_0_2_node_7 | 0.4 | n |  | TRUE
6 | bus_LV_1024-59_0_2_node_3 | 0.4 | n |  | TRUE
7 | bus_LV_1024-59_0_2_node_4 | 0.4 | n |  | TRUE
8 | bus_LV_1024-59_0_2_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_1024-59_0_2_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_1024-59_0_2_node_14 | 0.4 | n |  | TRUE
11 | bus_LV_1024-59_0_2_node_16 | 0.4 | n |  | TRUE
12 | bus_LV_1024-59_0_2_node_15 | 0.4 | n |  | TRUE
13 | bus_LV_1024-59_0_2_node_13 | 0.4 | n |  | TRUE
14 | bus_LV_1024-59_0_2_node_17 | 0.4 | n |  | TRUE
15 | bus_LV_1024-59_0_2_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_1024-59_0_2_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_1024-59_0_2_node_18 | 0.4 | n |  | TRUE
18 | bus_MV_354_1_node_138 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1024-59_0_2_load_0 | 0 | 0.041887 | 0.010498 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1024-59_0_2_load_1 | 1 | 0.019184 | 0.004808 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1024-59_0_2_load_7 | 5 | 0.013307 | 0.0033351 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1024-59_0_2_load_3 | 6 | 0.0018334 | 0.0004595 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1024-59_0_2_load_4 | 7 | 0.001332 | 0.00033384 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1024-59_0_2_load_8 | 8 | 0.022202 | 0.0055644 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1024-59_0_2_load_6 | 9 | 0.065693 | 0.016464 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1024-59_0_2_load_16 | 11 | 0.0092116 | 0.0023086 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1024-59_0_2_load_15 | 12 | 0.0010681 | 0.0002677 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1024-59_0_2_load_13 | 13 | 0.001198 | 0.00030026 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1024-59_0_2_load_17 | 14 | 0.0019982 | 0.00050079 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1024-59_0_2_load_11 | 15 | 0.0037154 | 0.00093116 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1024-59_0_2_load_12 | 16 | 0.017449 | 0.004373 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1024-59_0_2_load_18 | 17 | 0.029841 | 0.0074788 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 5 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1024-59_0_2_line_0 |  | 0 | 1 | 0.050306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1024-59_0_2_line_1 |  | 1 | 2 | 0.0051089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1024-59_0_2_line_2 |  | 2 | 3 | 0.023112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1024-59_0_2_line_3 |  | 3 | 4 | 0.15291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1024-59_0_2_line_4 |  | 3 | 5 | 0.031468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1024-59_0_2_line_5 |  | 4 | 10 | 0.038979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1024-59_0_2_line_6 |  | 4 | 11 | 0.072841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1024-59_0_2_line_7 |  | 5 | 9 | 0.053949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1024-59_0_2_line_8 |  | 6 | 7 | 0.03458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1024-59_0_2_line_9 |  | 6 | 8 | 0.27155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1024-59_0_2_line_10 |  | 8 | 9 | 0.014258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1024-59_0_2_line_11 |  | 10 | 12 | 0.012235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1024-59_0_2_line_12 |  | 10 | 13 | 0.18264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1024-59_0_2_line_13 |  | 11 | 14 | 0.025981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1024-59_0_2_line_14 |  | 13 | 16 | 0.13556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1024-59_0_2_line_15 |  | 14 | 17 | 0.064988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1024-59_0_2_line_16 |  | 15 | 16 | 0.19303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1024-59_0_2_trafo_7 | 0.63 MVA 20/0.4 kV | 18 | 5 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14
0 | 2661929.6781 | 1214776.2149 | 2661890.1548 | 1214790.3277 | 2661885.2156 | 1214797.0465
1 | 2661882.1895 | 1214801.1628 | 2661885.2156 | 1214797.0465
2 | 2661880.9702 | 1214824.2421 | 2661881.8873 | 1214806.8632 | 2661882.1895 | 1214801.1628
3 | 2661788.8524 | 1214873.7176 | 2661789.8375 | 1214868.0688 | 2661803.166 | 1214869.5077 | 2661808.4029 | 1214869.8289 | 2661819.2259 | 1214870.4748 | 2661856.2108 | 1214875.5947 | 2661881.4493 | 1214879.0475 | 2661881.8197 | 1214875.5603 | 2661882.3332 | 1214870.7182 | 2661881.0884 | 1214828.2236 | 2661880.9702 | 1214824.2421
4 | 2661880.9702 | 1214824.2421 | 2661892.2751 | 1214822.3694 | 2661911.7075 | 1214817.6018
5 | 2661764.9623 | 1214900.6423 | 2661775.1431 | 1214897.3012 | 2661781.1366 | 1214892.0267 | 2661787.1898 | 1214883.184 | 2661788.691 | 1214874.6387 | 2661788.8524 | 1214873.7176
6 | 2661788.8524 | 1214873.7176 | 2661791.9221 | 1214874.3053 | 2661801.1722 | 1214875.7576 | 2661811.3649 | 1214877.1307 | 2661822.9213 | 1214878.0956 | 2661830.7511 | 1214878.0989 | 2661842.2345 | 1214878.0402 | 2661851.3237 | 1214878.9016 | 2661861.1346 | 1214880.9751
7 | 2661952.8327 | 1214796.8393 | 2661954.1133 | 1214801.5542 | 2661954.7666 | 1214805.1965 | 2661952.8363 | 1214807.5112 | 2661911.7075 | 1214817.6018
8 | 2662078.709 | 1214544.4634 | 2662057.5755 | 1214530.7408 | 2662049.9664 | 1214525.2518
9 | 2661949.0955 | 1214783.0795 | 2662078.709 | 1214544.4634
10 | 2661949.0955 | 1214783.0795 | 2661952.8327 | 1214796.8393
11 | 2661764.9623 | 1214900.6423 | 2661754.4026 | 1214906.8217
12 | 2661764.9623 | 1214900.6423 | 2661777.6462 | 1214910.0461 | 2661785.3897 | 1214933.0294 | 2661795.3902 | 1214958.7933 | 2661804.8851 | 1214985.6971 | 2661810.4682 | 1214997.2954 | 2661815.1552 | 1215001.5578 | 2661824.7112 | 1215007.1825 | 2661834.9329 | 1215010.8685 | 2661853.1538 | 1215014.304 | 2661873.797 | 1215019.2323 | 2661878.762 | 1215021.6011
13 | 2661861.1346 | 1214880.9751 | 2661862.0008 | 1214881.1582 | 2661886.7012 | 1214885.5933
14 | 2661991.714 | 1215095.0924 | 2661991.714 | 1215095.0924 | 2661978.2418 | 1215082.6892 | 2661954.964 | 1215064.5806 | 2661931.6725 | 1215047.7728 | 2661886.16 | 1215025.1308 | 2661878.762 | 1215021.6011
15 | 2661886.7012 | 1214885.5933 | 2661929.4958 | 1214893.2772 | 2661950.6203 | 1214897.328
16 | 2661970.9054 | 1215206.6716 | 2661987.5339 | 1215190.3299 | 2662003.7845 | 1215175.0672 | 2662023.2926 | 1215159.8384 | 2662043.5765 | 1215148.8871 | 2662050.3495 | 1215143.8767 | 2662054.6815 | 1215138.4406 | 2662055.7518 | 1215133.382 | 2662054.9312 | 1215126.8583 | 2662051.1958 | 1215120.938 | 2662042.9044 | 1215114.9703 | 2662027.9238 | 1215106.6871 | 2662013.7163 | 1215101.4695 | 2661996.2386 | 1215097.4297 | 2661991.714 | 1215095.0924

## bus_geodata
| x | y | coords
0 | 2661929.6781 | 1214776.2149
1 | 2661885.2156 | 1214797.0465
2 | 2661882.1895 | 1214801.1628
3 | 2661880.9702 | 1214824.2421
4 | 2661788.8524 | 1214873.7176
5 | 2661911.7075 | 1214817.6018
6 | 2662078.709 | 1214544.4634
7 | 2662049.9664 | 1214525.2518
8 | 2661949.0955 | 1214783.0795
9 | 2661952.8327 | 1214796.8393
10 | 2661764.9623 | 1214900.6423
11 | 2661861.1346 | 1214880.9751
12 | 2661754.4026 | 1214906.8217
13 | 2661878.762 | 1215021.6011
14 | 2661886.7012 | 1214885.5933
15 | 2661970.9054 | 1215206.6716
16 | 2661991.714 | 1215095.0924
17 | 2661950.6203 | 1214897.328
18 | 2661933.9697 | 1214812.14

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99287 | -0.13662 | 0.041887 | 0.010498
1 | 0.9948 | -0.099436 | 0.019184 | 0.004808
2 | 0.99508 | -0.093943 | 0 | 0
3 | 0.99637 | -0.069129 | 0 | 0
4 | 0.98725 | -0.24391 | 0 | 0
5 | 1 | 0 | -0.22011 | -0.055454
6 | 0.99441 | -0.10755 | 0.0018334 | 0.0004595
7 | 0.99437 | -0.10836 | 0.001332 | 0.00033384
8 | 0.9952 | -0.092385 | 0.022202 | 0.0055644
9 | 0.99552 | -0.086019 | 0.065693 | 0.016464
10 | 0.98641 | -0.26026 | 0 | 0
11 | 0.98449 | -0.29753 | 0.0092116 | 0.0023086
12 | 0.9864 | -0.2605 | 0.0010681 | 0.0002677
13 | 0.98263 | -0.33375 | 0.001198 | 0.00030026
14 | 0.98373 | -0.31242 | 0.0019982 | 0.00050079
15 | 0.97931 | -0.39873 | 0.0037154 | 0.00093116
16 | 0.97998 | -0.3857 | 0.017449 | 0.004373
17 | 0.98194 | -0.34741 | 0.029841 | 0.0074788
18 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.041887 | -0.010498 | 0.041962 | 0.010545 | 7.4344e-05 | 4.6928e-05 | 0.062776 | 0.062776 | 0.062776 | 0.99287 | -0.13662 | 0.9948 | -0.099436 | 17.2463
1 | -0.061146 | -0.015353 | 0.061162 | 0.015363 | 1.603e-05 | 1.0193e-05 | 0.091472 | 0.091472 | 0.091472 | 0.9948 | -0.099436 | 0.99508 | -0.093943 | 25.1297
2 | -0.061162 | -0.015363 | 0.061234 | 0.015409 | 7.2516e-05 | 4.611e-05 | 0.091472 | 0.091472 | 0.091472 | 0.99508 | -0.093943 | 0.99637 | -0.069129 | 25.1297
3 | 0.065359 | 0.016711 | -0.064811 | -0.016363 | 0.00054765 | 0.00034853 | 0.097727 | 0.097728 | 0.097728 | 0.99637 | -0.069129 | 0.98725 | -0.24391 | 26.8483
4 | -0.12659 | -0.03212 | 0.12702 | 0.03239 | 0.00042241 | 0.00026993 | 0.1892 | 0.1892 | 0.1892 | 0.99637 | -0.069129 | 1 | 0 | 51.9776
5 | 0.023582 | 0.0059625 | -0.023564 | -0.0059512 | 1.8486e-05 | 1.1333e-05 | 0.035563 | 0.035563 | 0.035563 | 0.98725 | -0.24391 | 0.98641 | -0.26026 | 9.77
6 | 0.041229 | 0.0104 | -0.041123 | -0.010334 | 0.00010556 | 6.663e-05 | 0.062165 | 0.062165 | 0.062165 | 0.98725 | -0.24391 | 0.98449 | -0.29753 | 17.0784
7 | 0.091445 | 0.023063 | -0.09107 | -0.022824 | 0.00037486 | 0.00023921 | 0.13612 | 0.13612 | 0.13612 | 1 | 0 | 0.99552 | -0.086019 | 37.3965
8 | 0.0013321 | 0.00033342 | -0.001332 | -0.00033384 | 5.1519e-08 | -4.1562e-07 | 0.0019931 | 0.0019933 | 0.0019933 | 0.99441 | -0.10755 | 0.99437 | -0.10836 | 0.54761
9 | -0.0031655 | -0.00079292 | 0.0031678 | 0.00079085 | 2.284e-06 | -2.0638e-06 | 0.0047366 | 0.0047354 | 0.0047366 | 0.99441 | -0.10755 | 0.9952 | -0.092385 | 1.3013
10 | -0.02537 | -0.0063552 | 0.025378 | 0.00636 | 7.6933e-06 | 4.7384e-06 | 0.037932 | 0.037932 | 0.037932 | 0.9952 | -0.092385 | 0.99552 | -0.086019 | 10.4209
11 | 0.0010681 | 0.00026755 | -0.0010681 | -0.0002677 | 1.1912e-08 | -1.4855e-07 | 0.0016113 | 0.0016113 | 0.0016113 | 0.98641 | -0.26026 | 0.9864 | -0.2605 | 0.44267
12 | 0.022496 | 0.0056836 | -0.022417 | -0.0056354 | 7.895e-05 | 4.8206e-05 | 0.033952 | 0.033952 | 0.033952 | 0.98641 | -0.26026 | 0.98263 | -0.33375 | 9.3276
13 | 0.031912 | 0.0080249 | -0.031889 | -0.0080107 | 2.2675e-05 | 1.4182e-05 | 0.048242 | 0.048243 | 0.048243 | 0.98449 | -0.29753 | 0.98373 | -0.31242 | 13.2535
14 | 0.021219 | 0.0053351 | -0.021166 | -0.0053032 | 5.2506e-05 | 3.1891e-05 | 0.032138 | 0.032139 | 0.032139 | 0.98263 | -0.33375 | 0.97998 | -0.3857 | 8.8294
15 | 0.029891 | 0.0075099 | -0.029841 | -0.0074788 | 4.9835e-05 | 3.1071e-05 | 0.04522 | 0.04522 | 0.04522 | 0.98373 | -0.31242 | 0.98194 | -0.34741 | 12.4232
16 | -0.0037154 | -0.00093116 | 0.0037177 | 0.0009302 | 2.3066e-06 | -9.5416e-07 | 0.0056453 | 0.0056445 | 0.0056453 | 0.97931 | -0.39873 | 0.97998 | -0.3857 | 1.5509

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.23342 | 0.058789

## res_load
| p_mw | q_mvar
0 | 0.041887 | 0.010498
1 | 0.019184 | 0.004808
2 | 0.013307 | 0.0033351
3 | 0.0018334 | 0.0004595
4 | 0.001332 | 0.00033384
5 | 0.022202 | 0.0055644
6 | 0.065693 | 0.016464
7 | 0.0092116 | 0.0023086
8 | 0.0010681 | 0.0002677
9 | 0.001198 | 0.00030026
10 | 0.0019982 | 0.00050079
11 | 0.0037154 | 0.00093116
12 | 0.017449 | 0.004373
13 | 0.029841 | 0.0074788

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1