## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1024-60_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1024-60_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1024-60_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1024-60_0_3_node_13 | 0.4 | n |  | TRUE
4 | bus_LV_1024-60_0_3_node_14 | 0.4 | n |  | TRUE
5 | bus_LV_1024-60_0_3_node_3 | 0.4 | n |  | TRUE
6 | bus_LV_1024-60_0_3_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_1024-60_0_3_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_1024-60_0_3_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_1024-60_0_3_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_1024-60_0_3_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_1024-60_0_3_node_15 | 0.4 | n |  | TRUE
12 | bus_LV_1024-60_0_3_node_20 | 0.4 | n |  | TRUE
13 | bus_LV_1024-60_0_3_node_17 | 0.4 | n |  | TRUE
14 | bus_LV_1024-60_0_3_node_16 | 0.4 | n |  | TRUE
15 | bus_LV_1024-60_0_3_node_26 | 0.4 | n |  | TRUE
16 | bus_LV_1024-60_0_3_node_18 | 0.4 | n |  | TRUE
17 | bus_LV_1024-60_0_3_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_1024-60_0_3_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_1024-60_0_3_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_1024-60_0_3_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_1024-60_0_3_node_24 | 0.4 | n |  | TRUE
22 | bus_LV_1024-60_0_3_node_25 | 0.4 | n |  | TRUE
23 | bus_LV_1024-60_0_3_node_22 | 0.4 | n |  | TRUE
24 | bus_LV_1024-60_0_3_node_23 | 0.4 | n |  | TRUE
25 | bus_LV_1024-60_0_3_node_19 | 0.4 | n |  | TRUE
26 | bus_MV_354_1_node_147 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1024-60_0_3_load_0 | 0 | 0.00010793 | 2.7049e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1024-60_0_3_load_1 | 1 | 0.00020004 | 5.0134e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1024-60_0_3_load_2 | 2 | 0.000202 | 5.0626e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1024-60_0_3_load_13 | 3 | 0.00092482 | 0.00023178 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1024-60_0_3_load_3 | 5 | 0.00055622 | 0.0001394 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1024-60_0_3_load_4 | 6 | 0.00043883 | 0.00010998 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1024-60_0_3_load_5 | 7 | 0.00018767 | 4.7034e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1024-60_0_3_load_15 | 11 | 0.00029421 | 7.3737e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1024-60_0_3_load_20 | 12 | 0.0010631 | 0.00026643 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1024-60_0_3_load_17 | 13 | 0.00011749 | 2.9446e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1024-60_0_3_load_16 | 14 | 0.0005189 | 0.00013005 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1024-60_0_3_load_26 | 15 | 8.1861e-05 | 2.0516e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1024-60_0_3_load_18 | 16 | 0.000323 | 8.0951e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1024-60_0_3_load_9 | 17 | 0.048912 | 0.012259 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1024-60_0_3_load_11 | 19 | 0.059421 | 0.014892 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1024-60_0_3_load_12 | 20 | 0.028838 | 0.0072276 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1024-60_0_3_load_22 | 23 | 0.021964 | 0.0055047 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1024-60_0_3_load_23 | 24 | 0.02093 | 0.0052456 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1024-60_0_3_load_19 | 25 | 0.0011841 | 0.00029677 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 23 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1024-60_0_3_line_0 |  | 0 | 1 | 0.0044272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1024-60_0_3_line_1 |  | 1 | 2 | 0.050492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1024-60_0_3_line_2 |  | 2 | 5 | 0.0020297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1024-60_0_3_line_3 |  | 2 | 3 | 0.19632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1024-60_0_3_line_4 |  | 3 | 4 | 0.071838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1024-60_0_3_line_5 |  | 4 | 11 | 0.01115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1024-60_0_3_line_6 |  | 6 | 7 | 0.014567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1024-60_0_3_line_7 |  | 6 | 8 | 0.041519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1024-60_0_3_line_8 |  | 7 | 9 | 0.012134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1024-60_0_3_line_9 |  | 8 | 10 | 0.031738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1024-60_0_3_line_10 |  | 9 | 11 | 0.02017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1024-60_0_3_line_11 |  | 9 | 12 | 0.049795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1024-60_0_3_line_12 |  | 9 | 13 | 0.039604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1024-60_0_3_line_13 |  | 10 | 14 | 0.028836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1024-60_0_3_line_14 |  | 12 | 15 | 0.085432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1024-60_0_3_line_15 |  | 13 | 16 | 0.029617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1024-60_0_3_line_16 |  | 15 | 22 | 0.055913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1024-60_0_3_line_17 |  | 16 | 25 | 0.022996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1024-60_0_3_line_18 |  | 17 | 18 | 0.023235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1024-60_0_3_line_19 |  | 18 | 19 | 0.0046987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1024-60_0_3_line_20 |  | 18 | 20 | 0.02639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1024-60_0_3_line_21 |  | 19 | 24 | 0.00083052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1024-60_0_3_line_22 |  | 21 | 22 | 0.020729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1024-60_0_3_line_23 |  | 21 | 23 | 0.48845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1024-60_0_3_line_24 |  | 23 | 24 | 0.007665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1024-60_0_3_trafo_22 | 0.63 MVA 20/0.4 kV | 26 | 23 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14
0 | 2660893.4451 | 1214599.5029 | 2660895.6882 | 1214595.6861
1 | 2660895.6882 | 1214595.6861 | 2660897.4564 | 1214592.6772 | 2660897.9651 | 1214589.725 | 2660897.8012 | 1214587.1773 | 2660895.4047 | 1214580.1486 | 2660895.1921 | 1214577.9117 | 2660895.2508 | 1214575.1439 | 2660896.9384 | 1214567.5565 | 2660897.9174 | 1214563.1638 | 2660897.9405 | 1214560.9071 | 2660896.9424 | 1214556.761 | 2660896.0735 | 1214554.0838 | 2660894.397 | 1214551.6652 | 2660892.1745 | 1214549.9081 | 2660890.7081 | 1214549.205
2 | 2660888.8779 | 1214548.3274 | 2660890.7081 | 1214549.205
3 | 2661030.5676 | 1214411.4298 | 2660890.7081 | 1214549.205
4 | 2661045.202 | 1214345.2801 | 2661025.7217 | 1214383.015 | 2661025.7765 | 1214399.9148 | 2661030.5676 | 1214411.4298
5 | 2661045.202 | 1214345.2801 | 2661050.325 | 1214338.9731 | 2661052.8387 | 1214337.2911
6 | 2661061.5718 | 1214319.1021 | 2661057.6981 | 1214315.4119 | 2661050.5356 | 1214309.6104
7 | 2661018.272 | 1214283.4777 | 2661050.5356 | 1214309.6104
8 | 2661070.3572 | 1214327.4711 | 2661061.5718 | 1214319.1021
9 | 2661018.272 | 1214283.4777 | 2661013.7703 | 1214283.9987 | 2661009.909 | 1214285.0376 | 2661003.2477 | 1214288.038 | 2660997.1121 | 1214291.6219 | 2660990.0169 | 1214296.9415
10 | 2661070.3572 | 1214327.4711 | 2661062.5992 | 1214330.7603 | 2661052.8387 | 1214337.2911
11 | 2661070.3572 | 1214327.4711 | 2661094.3545 | 1214360.3926 | 2661100.8647 | 1214366.687
12 | 2661070.3572 | 1214327.4711 | 2661095.0657 | 1214311.014 | 2661101.6731 | 1214303.62
13 | 2660990.0169 | 1214296.9415 | 2661014.0204 | 1214312.9215
14 | 2661100.8647 | 1214366.687 | 2661185.6383 | 1214356.1034
15 | 2661101.6731 | 1214303.62 | 2661106.3678 | 1214298.3665 | 2661111.346 | 1214292.8474 | 2661118.9249 | 1214279.7418
16 | 2661187.956 | 1214411.4833 | 2661190.2037 | 1214403.3792 | 2661185.6383 | 1214356.1034
17 | 2661128.2061 | 1214258.7439 | 2661127.4509 | 1214259.9478 | 2661120.3773 | 1214277.2304 | 2661118.9249 | 1214279.7418
18 | 2661694.089 | 1214528.8356 | 2661708.9549 | 1214546.6923
19 | 2661694.089 | 1214528.8356 | 2661691.0839 | 1214525.2235
20 | 2661694.089 | 1214528.8356 | 2661709.0557 | 1214507.0999
21 | 2661691.0839 | 1214525.2235 | 2661690.5527 | 1214524.585
22 | 2661207.7049 | 1214417.9566 | 2661201.756 | 1214415.9277 | 2661187.956 | 1214411.4833
23 | 2661207.7049 | 1214417.9566 | 2661685.6506 | 1214518.6926
24 | 2661685.6506 | 1214518.6926 | 2661690.5527 | 1214524.585

## bus_geodata
| x | y | coords
0 | 2660893.4451 | 1214599.5029
1 | 2660895.6882 | 1214595.6861
2 | 2660890.7081 | 1214549.205
3 | 2661030.5676 | 1214411.4298
4 | 2661045.202 | 1214345.2801
5 | 2660888.8779 | 1214548.3274
6 | 2661050.5356 | 1214309.6104
7 | 2661061.5718 | 1214319.1021
8 | 2661018.272 | 1214283.4777
9 | 2661070.3572 | 1214327.4711
10 | 2660990.0169 | 1214296.9415
11 | 2661052.8387 | 1214337.2911
12 | 2661100.8647 | 1214366.687
13 | 2661101.6731 | 1214303.62
14 | 2661014.0204 | 1214312.9215
15 | 2661185.6383 | 1214356.1034
16 | 2661118.9249 | 1214279.7418
17 | 2661708.9549 | 1214546.6923
18 | 2661694.089 | 1214528.8356
19 | 2661691.0839 | 1214525.2235
20 | 2661709.0557 | 1214507.0999
21 | 2661207.7049 | 1214417.9566
22 | 2661187.956 | 1214411.4833
23 | 2661685.6506 | 1214518.6926
24 | 2661690.5527 | 1214524.585
25 | 2661128.2061 | 1214258.7439
26 | 2661685.6506 | 1214518.6926

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99571 | -0.082946 | 0.00010793 | 2.7049e-05
1 | 0.99571 | -0.082937 | 0.00020004 | 5.0134e-05
2 | 0.99573 | -0.082663 | 0.000202 | 5.0626e-05
3 | 0.99592 | -0.078966 | 0.00092482 | 0.00023178
4 | 0.99605 | -0.076441 | 0 | 0
5 | 0.99573 | -0.082683 | 0.00055622 | 0.0001394
6 | 0.99608 | -0.075726 | 0.00043883 | 0.00010998
7 | 0.9961 | -0.07548 | 0.00018767 | 4.7034e-05
8 | 0.99606 | -0.076107 | 0 | 0
9 | 0.99611 | -0.075235 | 0 | 0
10 | 0.99605 | -0.076397 | 0 | 0
11 | 0.99607 | -0.076049 | 0.00029421 | 7.3737e-05
12 | 0.99634 | -0.070797 | 0.0010631 | 0.00026643
13 | 0.99605 | -0.076367 | 0.00011749 | 2.9446e-05
14 | 0.99604 | -0.07666 | 0.0005189 | 0.00013005
15 | 0.99681 | -0.06159 | 8.1861e-05 | 2.0516e-05
16 | 0.99601 | -0.077152 | 0.000323 | 8.0951e-05
17 | 0.99798 | -0.038801 | 0.048912 | 0.012259
18 | 0.99901 | -0.018933 | 0 | 0
19 | 0.99935 | -0.012555 | 0.059421 | 0.014892
20 | 0.99832 | -0.032233 | 0.028838 | 0.0072276
21 | 0.99725 | -0.053225 | 0 | 0
22 | 0.99713 | -0.055487 | 0 | 0
23 | 1 | 0 | -0.16616 | -0.041291
24 | 0.99945 | -0.010567 | 0.02093 | 0.0052456
25 | 0.99599 | -0.077631 | 0.0011841 | 0.00029677
26 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.00010793 | -2.7049e-05 | 0.00010793 | 2.6991e-05 | 4.3194e-11 | -5.7557e-08 | 0.00016129 | 0.00016127 | 0.00016129 | 0.99571 | -0.082946 | 0.99571 | -0.082937 | 0.04431
1 | -0.00030796 | -7.7125e-05 | 0.00030797 | 7.6471e-05 | 4.0081e-09 | -6.5419e-07 | 0.0004602 | 0.00045997 | 0.0004602 | 0.99571 | -0.082937 | 0.99573 | -0.082663 | 0.12643
2 | 0.00055622 | 0.00013938 | -0.00055622 | -0.0001394 | 5.2589e-10 | -2.6065e-08 | 0.00083121 | 0.00083122 | 0.00083122 | 0.99573 | -0.082663 | 0.99573 | -0.082683 | 0.22836
3 | -0.0010662 | -0.00026647 | 0.0010664 | 0.00026404 | 1.8673e-07 | -2.4346e-06 | 0.0015931 | 0.0015922 | 0.0015931 | 0.99573 | -0.082663 | 0.99592 | -0.078966 | 0.43765
4 | -0.0019912 | -0.00049582 | 0.0019914 | 0.00049504 | 2.3823e-07 | -7.8244e-07 | 0.0029739 | 0.0029736 | 0.0029739 | 0.99592 | -0.078966 | 0.99605 | -0.076441 | 0.81702
5 | -0.0019914 | -0.00049504 | 0.0019915 | 0.00049492 | 3.6972e-08 | -1.2147e-07 | 0.0029736 | 0.0029736 | 0.0029736 | 0.99605 | -0.076441 | 0.99607 | -0.076049 | 0.81693
6 | -0.00095774 | -0.00023871 | 0.00095776 | 0.00023853 | 1.1175e-08 | -1.8247e-07 | 0.0014303 | 0.0014302 | 0.0014303 | 0.99608 | -0.075726 | 0.9961 | -0.07548 | 0.39293
7 | 0.00051892 | 0.00012873 | -0.00051891 | -0.00012927 | 9.3474e-09 | -5.3445e-07 | 0.00077473 | 0.00077492 | 0.00077492 | 0.99608 | -0.075726 | 0.99606 | -0.076107 | 0.21289
8 | -0.0011454 | -0.00028557 | 0.0011454 | 0.00028542 | 1.3313e-08 | -1.4942e-07 | 0.0017106 | 0.0017105 | 0.0017106 | 0.9961 | -0.07548 | 0.99611 | -0.075235 | 0.46993
9 | 0.00051891 | 0.00012927 | -0.0005189 | -0.00012968 | 7.1484e-09 | -4.0853e-07 | 0.00077492 | 0.00077507 | 0.00077507 | 0.99606 | -0.076107 | 0.99605 | -0.076397 | 0.21293
10 | 0.0022858 | 0.00056845 | -0.0022857 | -0.00056865 | 8.811e-08 | -2.0616e-07 | 0.003413 | 0.0034131 | 0.0034131 | 0.99611 | -0.075235 | 0.99607 | -0.076049 | 0.93766
11 | -0.005056 | -0.0012599 | 0.0050571 | 0.00126 | 1.0645e-06 | 3.29e-08 | 0.0075503 | 0.00755 | 0.0075503 | 0.99611 | -0.075235 | 0.99634 | -0.070797 | 2.0742
12 | 0.0016248 | 0.00040608 | -0.0016247 | -0.00040654 | 8.7468e-08 | -4.5953e-07 | 0.0024268 | 0.0024269 | 0.0024269 | 0.99611 | -0.075235 | 0.99605 | -0.076367 | 0.66674
13 | 0.0005189 | 0.00012968 | -0.0005189 | -0.00013005 | 6.4971e-09 | -3.7116e-07 | 0.00077507 | 0.0007752 | 0.0007752 | 0.99605 | -0.076397 | 0.99604 | -0.07666 | 0.21297
14 | -0.0061201 | -0.0015264 | 0.0061228 | 0.001527 | 2.6749e-06 | 5.9879e-07 | 0.0091377 | 0.0091373 | 0.0091377 | 0.99634 | -0.070797 | 0.99681 | -0.06159 | 2.5104
15 | 0.0015072 | 0.00037709 | -0.0015072 | -0.00037744 | 5.6301e-08 | -3.4945e-07 | 0.0022514 | 0.0022516 | 0.0022516 | 0.99605 | -0.076367 | 0.99601 | -0.077152 | 0.61856
16 | -0.0062047 | -0.0015475 | 0.0062065 | 0.0015479 | 1.7977e-06 | 4.214e-07 | 0.0092595 | 0.0092593 | 0.0092595 | 0.99681 | -0.06159 | 0.99713 | -0.055487 | 2.5438
17 | 0.0011842 | 0.00029649 | -0.0011841 | -0.00029677 | 2.6988e-08 | -2.8202e-07 | 0.001769 | 0.0017691 | 0.0017691 | 0.99601 | -0.077152 | 0.99599 | -0.077631 | 0.48602
18 | -0.048912 | -0.012259 | 0.048958 | 0.012288 | 4.6342e-05 | 2.9355e-05 | 0.072929 | 0.072929 | 0.072929 | 0.99798 | -0.038801 | 0.99901 | -0.018933 | 20.0355
19 | -0.077815 | -0.019527 | 0.077839 | 0.019542 | 2.3674e-05 | 1.509e-05 | 0.11591 | 0.11591 | 0.11591 | 0.99901 | -0.018933 | 0.99935 | -0.012555 | 31.8442
20 | 0.028857 | 0.0072389 | -0.028838 | -0.0072276 | 1.8285e-05 | 1.1357e-05 | 0.042984 | 0.042984 | 0.042984 | 0.99901 | -0.018933 | 0.99832 | -0.032233 | 11.8088
21 | -0.13726 | -0.034434 | 0.13727 | 0.034442 | 1.3011e-05 | 8.316e-06 | 0.20439 | 0.20439 | 0.20439 | 0.99935 | -0.012555 | 0.99945 | -0.010567 | 56.151
22 | 0.0062071 | 0.0015481 | -0.0062065 | -0.0015479 | 6.6643e-07 | 1.561e-07 | 0.0092592 | 0.0092593 | 0.0092593 | 0.99725 | -0.053225 | 0.99713 | -0.055487 | 2.5438
23 | -0.0062071 | -0.0015481 | 0.0062228 | 0.0015518 | 1.57e-05 | 3.6573e-06 | 0.0092592 | 0.0092569 | 0.0092592 | 0.99725 | -0.053225 | 1 | 0 | 2.5437
24 | 0.15828 | 0.039739 | -0.1582 | -0.039688 | 7.9741e-05 | 5.0833e-05 | 0.23555 | 0.23555 | 0.23555 | 1 | 0 | 0.99945 | -0.010567 | 32.356

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -6.4999e-16 | 2.4266e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 7.2519e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.18812 | 0.046796

## res_load
| p_mw | q_mvar
0 | 0.00010793 | 2.7049e-05
1 | 0.00020004 | 5.0134e-05
2 | 0.000202 | 5.0626e-05
3 | 0.00092482 | 0.00023178
4 | 0.00055622 | 0.0001394
5 | 0.00043883 | 0.00010998
6 | 0.00018767 | 4.7034e-05
7 | 0.00029421 | 7.3737e-05
8 | 0.0010631 | 0.00026643
9 | 0.00011749 | 2.9446e-05
10 | 0.0005189 | 0.00013005
11 | 8.1861e-05 | 2.0516e-05
12 | 0.000323 | 8.0951e-05
13 | 0.048912 | 0.012259
14 | 0.059421 | 0.014892
15 | 0.028838 | 0.0072276
16 | 0.021964 | 0.0055047
17 | 0.02093 | 0.0052456
18 | 0.0011841 | 0.00029677

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1