## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1024-6_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1024-6_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1024-6_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1024-6_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1024-6_0_6_node_56 | 0.4 | n |  | TRUE
5 | bus_LV_1024-6_0_6_node_14 | 0.4 | n |  | TRUE
6 | bus_LV_1024-6_0_6_node_11 | 0.4 | n |  | TRUE
7 | bus_LV_1024-6_0_6_node_61 | 0.4 | n |  | TRUE
8 | bus_LV_1024-6_0_6_node_57 | 0.4 | n |  | TRUE
9 | bus_LV_1024-6_0_6_node_29 | 0.4 | n |  | TRUE
10 | bus_LV_1024-6_0_6_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_1024-6_0_6_node_30 | 0.4 | n |  | TRUE
12 | bus_LV_1024-6_0_6_node_4 | 0.4 | n |  | TRUE
13 | bus_LV_1024-6_0_6_node_5 | 0.4 | n |  | TRUE
14 | bus_LV_1024-6_0_6_node_6 | 0.4 | n |  | TRUE
15 | bus_LV_1024-6_0_6_node_7 | 0.4 | n |  | TRUE
16 | bus_LV_1024-6_0_6_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_1024-6_0_6_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_1024-6_0_6_node_22 | 0.4 | n |  | TRUE
19 | bus_LV_1024-6_0_6_node_15 | 0.4 | n |  | TRUE
20 | bus_LV_1024-6_0_6_node_18 | 0.4 | n |  | TRUE
21 | bus_LV_1024-6_0_6_node_48 | 0.4 | n |  | TRUE
22 | bus_LV_1024-6_0_6_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_1024-6_0_6_node_20 | 0.4 | n |  | TRUE
24 | bus_LV_1024-6_0_6_node_27 | 0.4 | n |  | TRUE
25 | bus_LV_1024-6_0_6_node_23 | 0.4 | n |  | TRUE
26 | bus_LV_1024-6_0_6_node_55 | 0.4 | n |  | TRUE
27 | bus_LV_1024-6_0_6_node_19 | 0.4 | n |  | TRUE
28 | bus_LV_1024-6_0_6_node_53 | 0.4 | n |  | TRUE
29 | bus_LV_1024-6_0_6_node_21 | 0.4 | n |  | TRUE
30 | bus_LV_1024-6_0_6_node_25 | 0.4 | n |  | TRUE
31 | bus_LV_1024-6_0_6_node_24 | 0.4 | n |  | TRUE
32 | bus_LV_1024-6_0_6_node_58 | 0.4 | n |  | TRUE
33 | bus_LV_1024-6_0_6_node_59 | 0.4 | n |  | TRUE
34 | bus_LV_1024-6_0_6_node_10 | 0.4 | n |  | TRUE
35 | bus_LV_1024-6_0_6_node_12 | 0.4 | n |  | TRUE
36 | bus_LV_1024-6_0_6_node_52 | 0.4 | n |  | TRUE
37 | bus_LV_1024-6_0_6_node_54 | 0.4 | n |  | TRUE
38 | bus_LV_1024-6_0_6_node_50 | 0.4 | n |  | TRUE
39 | bus_LV_1024-6_0_6_node_51 | 0.4 | n |  | TRUE
40 | bus_LV_1024-6_0_6_node_46 | 0.4 | n |  | TRUE
41 | bus_LV_1024-6_0_6_node_26 | 0.4 | n |  | TRUE
42 | bus_LV_1024-6_0_6_node_45 | 0.4 | n |  | TRUE
43 | bus_LV_1024-6_0_6_node_28 | 0.4 | n |  | TRUE
44 | bus_LV_1024-6_0_6_node_43 | 0.4 | n |  | TRUE
45 | bus_LV_1024-6_0_6_node_39 | 0.4 | n |  | TRUE
46 | bus_LV_1024-6_0_6_node_40 | 0.4 | n |  | TRUE
47 | bus_LV_1024-6_0_6_node_38 | 0.4 | n |  | TRUE
48 | bus_LV_1024-6_0_6_node_41 | 0.4 | n |  | TRUE
49 | bus_LV_1024-6_0_6_node_34 | 0.4 | n |  | TRUE
50 | bus_LV_1024-6_0_6_node_47 | 0.4 | n |  | TRUE
51 | bus_LV_1024-6_0_6_node_44 | 0.4 | n |  | TRUE
52 | bus_LV_1024-6_0_6_node_49 | 0.4 | n |  | TRUE
53 | bus_LV_1024-6_0_6_node_60 | 0.4 | n |  | TRUE
54 | bus_LV_1024-6_0_6_node_31 | 0.4 | n |  | TRUE
55 | bus_LV_1024-6_0_6_node_32 | 0.4 | n |  | TRUE
56 | bus_LV_1024-6_0_6_node_42 | 0.4 | n |  | TRUE
57 | bus_MV_490_0_node_30 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1024-6_0_6_load_0 | 0 | 0.0079358 | 0.0019889 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1024-6_0_6_load_1 | 1 | 0.00099201 | 0.00024862 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1024-6_0_6_load_2 | 2 | 0.0011289 | 0.00028292 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1024-6_0_6_load_3 | 3 | 0.0041884 | 0.0010497 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1024-6_0_6_load_56 | 4 | 0.010291 | 0.0025793 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1024-6_0_6_load_11 | 6 | 0.0013487 | 0.00033803 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1024-6_0_6_load_61 | 7 | 0.0095507 | 0.0023936 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1024-6_0_6_load_29 | 9 | 0.0087102 | 0.002183 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1024-6_0_6_load_9 | 10 | 0.016514 | 0.0041389 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1024-6_0_6_load_30 | 11 | 0.013027 | 0.0032649 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1024-6_0_6_load_4 | 12 | 0.041253 | 0.010339 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1024-6_0_6_load_5 | 13 | 0.00095703 | 0.00023985 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1024-6_0_6_load_6 | 14 | 0.01298 | 0.0032531 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1024-6_0_6_load_7 | 15 | 0.0048635 | 0.0012189 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1024-6_0_6_load_13 | 17 | 0.0038706 | 0.00097007 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1024-6_0_6_load_48 | 21 | 0.015453 | 0.003873 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1024-6_0_6_load_55 | 26 | 0.0077342 | 0.0019384 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1024-6_0_6_load_53 | 28 | 0.026277 | 0.0065856 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1024-6_0_6_load_25 | 30 | 0.044922 | 0.011258 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1024-6_0_6_load_24 | 31 | 0.0017124 | 0.00042916 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1024-6_0_6_load_58 | 32 | 0.012271 | 0.0030754 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1024-6_0_6_load_10 | 34 | 0.0010245 | 0.00025677 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1024-6_0_6_load_12 | 35 | 0.009332 | 0.0023388 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1024-6_0_6_load_52 | 36 | 0.0088652 | 0.0022218 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1024-6_0_6_load_54 | 37 | 0.0082917 | 0.0020781 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1024-6_0_6_load_50 | 38 | 0.040392 | 0.010123 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1024-6_0_6_load_51 | 39 | 0.021621 | 0.0054188 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1024-6_0_6_load_46 | 40 | 0.020562 | 0.0051534 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1024-6_0_6_load_45 | 42 | 0.051236 | 0.012841 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1024-6_0_6_load_43 | 44 | 0.018744 | 0.0046976 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1024-6_0_6_load_39 | 45 | 0.0038442 | 0.00096345 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1024-6_0_6_load_38 | 47 | 0.0044711 | 0.0011206 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1024-6_0_6_load_41 | 48 | 0.0071349 | 0.0017882 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1024-6_0_6_load_47 | 50 | 0.0090238 | 0.0022616 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1024-6_0_6_load_44 | 51 | 0.0049264 | 0.0012347 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1024-6_0_6_load_49 | 52 | 0.0085469 | 0.002142 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1024-6_0_6_load_60 | 53 | 0.0097448 | 0.0024423 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1024-6_0_6_load_31 | 54 | 0.013663 | 0.0034243 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1024-6_0_6_load_32 | 55 | 0.0040686 | 0.0010197 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1024-6_0_6_load_42 | 56 | 0.017851 | 0.004474 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 35 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1024-6_0_6_line_0 |  | 0 | 1 | 0.0074034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1024-6_0_6_line_1 |  | 0 | 2 | 0.0098447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1024-6_0_6_line_2 |  | 1 | 3 | 0.0072381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1024-6_0_6_line_3 |  | 3 | 6 | 0.012176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1024-6_0_6_line_4 |  | 4 | 5 | 0.004574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1024-6_0_6_line_5 |  | 5 | 8 | 0.013015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1024-6_0_6_line_6 |  | 6 | 9 | 0.05653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_1024-6_0_6_line_7 |  | 6 | 10 | 0.018556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_1024-6_0_6_line_8 |  | 7 | 8 | 0.004522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1024-6_0_6_line_9 |  | 8 | 33 | 0.014659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1024-6_0_6_line_10 |  | 9 | 11 | 0.0032647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_1024-6_0_6_line_11 |  | 10 | 34 | 0.0013935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_1024-6_0_6_line_12 |  | 11 | 30 | 0.025952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_1024-6_0_6_line_13 |  | 12 | 13 | 0.00047048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1024-6_0_6_line_14 |  | 12 | 14 | 0.016125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1024-6_0_6_line_15 |  | 13 | 15 | 0.042884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1024-6_0_6_line_16 |  | 15 | 16 | 0.024817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1024-6_0_6_line_17 |  | 16 | 17 | 0.0077259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1024-6_0_6_line_18 |  | 17 | 18 | 0.012173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1024-6_0_6_line_19 |  | 18 | 31 | 0.055338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1024-6_0_6_line_20 |  | 19 | 20 | 0.015612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1024-6_0_6_line_21 |  | 19 | 21 | 0.040833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1024-6_0_6_line_22 |  | 20 | 25 | 0.058898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1024-6_0_6_line_23 |  | 20 | 26 | 0.033774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1024-6_0_6_line_24 |  | 21 | 50 | 0.02325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1024-6_0_6_line_25 |  | 22 | 23 | 0.077476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_1024-6_0_6_line_26 |  | 22 | 24 | 0.07933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_1024-6_0_6_line_27 |  | 23 | 27 | 0.01281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_1024-6_0_6_line_28 |  | 24 | 45 | 0.10532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
29 | LV_1024-6_0_6_line_29 |  | 25 | 32 | 0.004008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1024-6_0_6_line_30 |  | 25 | 33 | 0.013353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1024-6_0_6_line_31 |  | 26 | 37 | 0.016827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1024-6_0_6_line_32 |  | 27 | 28 | 0.014122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_1024-6_0_6_line_33 |  | 28 | 39 | 0.02404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
34 | LV_1024-6_0_6_line_34 |  | 28 | 40 | 0.018353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1024-6_0_6_line_35 |  | 29 | 30 | 0.12882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
36 | LV_1024-6_0_6_line_36 |  | 29 | 31 | 0.16609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1024-6_0_6_line_37 |  | 33 | 53 | 0.004742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1024-6_0_6_line_38 |  | 34 | 35 | 0.01653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
39 | LV_1024-6_0_6_line_39 |  | 35 | 38 | 0.033349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
40 | LV_1024-6_0_6_line_40 |  | 36 | 37 | 0.024291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1024-6_0_6_line_41 |  | 36 | 38 | 0.0216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1024-6_0_6_line_42 |  | 38 | 39 | 0.024307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
43 | LV_1024-6_0_6_line_43 |  | 41 | 42 | 0.031331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1024-6_0_6_line_44 |  | 41 | 43 | 0.023527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1024-6_0_6_line_45 |  | 41 | 44 | 0.015781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1024-6_0_6_line_46 |  | 43 | 46 | 0.063577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1024-6_0_6_line_47 |  | 43 | 47 | 0.026608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1024-6_0_6_line_48 |  | 44 | 51 | 0.030907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1024-6_0_6_line_49 |  | 45 | 47 | 0.016213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1024-6_0_6_line_50 |  | 46 | 48 | 0.022286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1024-6_0_6_line_51 |  | 46 | 49 | 0.028805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1024-6_0_6_line_52 |  | 49 | 56 | 0.0036638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1024-6_0_6_line_53 |  | 49 | 55 | 0.024971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1024-6_0_6_line_54 |  | 50 | 52 | 0.020308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1024-6_0_6_line_55 |  | 54 | 55 | 0.017232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1024-6_0_6_trafo_12 | 0.63 MVA 20/0.4 kV | 57 | 35 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14
0 | 2663541.8993 | 1214084.542 | 2663549.2737 | 1214085.1971
1 | 2663541.8993 | 1214084.542 | 2663532.0932 | 1214083.6709
2 | 2663549.2737 | 1214085.1971 | 2663556.4834 | 1214085.8376
3 | 2663568.6112 | 1214086.915 | 2663556.4834 | 1214085.8376
4 | 2663523.0994 | 1214146.9982 | 2663524.6038 | 1214142.6782
5 | 2663523.0994 | 1214146.9982 | 2663535.6705 | 1214150.5009
6 | 2663593.3011 | 1214036.0617 | 2663568.6112 | 1214086.915
7 | 2663568.6112 | 1214086.915 | 2663587.0941 | 1214088.557
8 | 2663536.9245 | 1214146.156 | 2663535.6705 | 1214150.5009
9 | 2663549.911 | 1214154.1437 | 2663535.6705 | 1214150.5009
10 | 2663594.9248 | 1214033.2294 | 2663593.3011 | 1214036.0617
11 | 2663588.4821 | 1214088.6803 | 2663587.0941 | 1214088.557
12 | 2663607.8319 | 1214010.7152 | 2663594.9248 | 1214033.2294
13 | 2663499.2283 | 1213974.3686 | 2663498.7602 | 1213974.3213
14 | 2663499.2283 | 1213974.3686 | 2663515.2716 | 1213975.9905
15 | 2663498.7602 | 1213974.3213 | 2663456.0942 | 1213970.0078
16 | 2663431.4033 | 1213967.5116 | 2663456.0942 | 1213970.0078
17 | 2663431.4033 | 1213967.5116 | 2663432.0544 | 1213959.8132
18 | 2663433.0803 | 1213947.6839 | 2663432.0544 | 1213959.8132
19 | 2663433.0803 | 1213947.6839 | 2663441.4256 | 1213947.9061 | 2663488.3745 | 1213949.8744
20 | 2663591.1028 | 1214186.7251 | 2663593.8469 | 1214187.944 | 2663598.4127 | 1214189.9828 | 2663599.0553 | 1214190.2676 | 2663600.7336 | 1214191.0082 | 2663604.3545 | 1214192.6256 | 2663605.3675 | 1214193.07
21 | 2663605.3675 | 1214193.07 | 2663608.059 | 1214184.9826 | 2663609.6561 | 1214179.8075 | 2663613.8637 | 1214168.4454 | 2663620.8948 | 1214155.4484
22 | 2663562.1002 | 1214159.2657 | 2663565.6009 | 1214161.4821 | 2663561.6184 | 1214171.6904 | 2663562.5852 | 1214180.0281 | 2663590.4024 | 1214191.8541 | 2663591.1028 | 1214186.7251
23 | 2663591.1028 | 1214186.7251 | 2663594.2692 | 1214181.1109 | 2663595.0614 | 1214179.4739 | 2663598.8107 | 1214171.1866 | 2663602.381 | 1214163.3198 | 2663603.8868 | 1214161.0011 | 2663605.7494 | 1214158.7084 | 2663607.2255 | 1214157.2775
24 | 2663631.4771 | 1214134.7474 | 2663630.0309 | 1214137.4542 | 2663621.7514 | 1214153.8649 | 2663620.8948 | 1214155.4484
25 | 2663713.7953 | 1213993.0036 | 2663707.132 | 1213989.6304 | 2663674.6666 | 1214051.6554
26 | 2663713.7953 | 1213993.0036 | 2663713.7842 | 1213977.6941 | 2663715.0899 | 1213977.7636 | 2663718.7185 | 1213977.958 | 2663723.1517 | 1213978.2055 | 2663724.1918 | 1213978.2611 | 2663723.846 | 1213982.8936 | 2663725.2008 | 1214004.666 | 2663726.773 | 1214021.7267 | 2663727.293 | 1214022.1102 | 2663731.9886 | 1214025.5181 | 2663734.0688 | 1214027.0301 | 2663734.8678 | 1214027.6057
27 | 2663663.2751 | 1214045.7968 | 2663664.3327 | 1214046.3418 | 2663670.7158 | 1214049.623 | 2663673.8659 | 1214051.2466 | 2663674.6666 | 1214051.6554
28 | 2663734.8678 | 1214027.6057 | 2663731.8192 | 1214032.1203 | 2663725.8932 | 1214043.6308 | 2663710.2344 | 1214081.7092 | 2663704.6602 | 1214097.2593 | 2663703.3329 | 1214104.1828 | 2663702.6117 | 1214111.2572 | 2663702.8684 | 1214119.932 | 2663703.3614 | 1214126.312
29 | 2663562.1002 | 1214159.2657 | 2663564.278 | 1214155.8979
30 | 2663562.1002 | 1214159.2657 | 2663556.7965 | 1214155.9071 | 2663549.911 | 1214154.1437
31 | 2663607.2255 | 1214157.2775 | 2663610.6842 | 1214153.9247 | 2663616.4327 | 1214143.3794
32 | 2663663.2751 | 1214045.7968 | 2663657.1057 | 1214058.0608 | 2663656.9279 | 1214058.4123
33 | 2663647.0114 | 1214080.2905 | 2663650.879 | 1214072.1363 | 2663653.9243 | 1214064.3529 | 2663656.9279 | 1214058.4123
34 | 2663656.9279 | 1214058.4123 | 2663639.1153 | 1214053.9927
35 | 2663637.1823 | 1213888.7437 | 2663633.1772 | 1213966.5045 | 2663607.8319 | 1214010.7152
36 | 2663637.1823 | 1213888.7437 | 2663633.0714 | 1213888.1773 | 2663627.8605 | 1213888.1995 | 2663622.3439 | 1213889.1079 | 2663607.1388 | 1213891.8029 | 2663601.7894 | 1213893.4135 | 2663588.4087 | 1213900.2529 | 2663583.8858 | 1213903.4289 | 2663555.6826 | 1213927.6766 | 2663546.0297 | 1213934.6892 | 2663537.3543 | 1213939.0661 | 2663523.501 | 1213944.6554 | 2663505.8138 | 1213949.3588 | 2663495.103 | 1213950.1564 | 2663488.3745 | 1213949.8744
37 | 2663549.911 | 1214154.1437 | 2663551.6367 | 1214149.7261
38 | 2663588.4821 | 1214088.6803 | 2663604.9468 | 1214090.143
39 | 2663636.1121 | 1214102.0124 | 2663604.9468 | 1214090.143
40 | 2663626.0409 | 1214121.1132 | 2663620.1995 | 1214134.1696 | 2663618.2222 | 1214140.0966 | 2663616.4327 | 1214143.3794
41 | 2663636.1121 | 1214102.0124 | 2663635.0821 | 1214103.9875 | 2663627.1946 | 1214118.5345 | 2663626.0409 | 1214121.1132
42 | 2663636.1121 | 1214102.0124 | 2663642.7045 | 1214089.3709 | 2663647.0114 | 1214080.2905
43 | 2663694.8432 | 1214155.1791 | 2663687.39 | 1214154.6659 | 2663682.8773 | 1214178.0953
44 | 2663694.8432 | 1214155.1791 | 2663700.1558 | 1214155.5694 | 2663698.375 | 1214167.9803 | 2663703.3105 | 1214168.8336 | 2663703.9549 | 1214168.9405
45 | 2663694.8432 | 1214155.1791 | 2663695.0137 | 1214146.3311 | 2663694.5195 | 1214139.4179
46 | 2663703.9549 | 1214168.9405 | 2663703.3527 | 1214172.7031 | 2663700.5721 | 1214184.136 | 2663701.7398 | 1214183.6148 | 2663702.6757 | 1214182.7465 | 2663705.0217 | 1214179.2805 | 2663712.4521 | 1214161.3154 | 2663720.6974 | 1214150.9638 | 2663727.1833 | 1214145.3407
47 | 2663703.9549 | 1214168.9405 | 2663705.3384 | 1214160.3055 | 2663705.4641 | 1214153.5249 | 2663704.6104 | 1214142.4772
48 | 2663694.5195 | 1214139.4179 | 2663693.4014 | 1214123.7777 | 2663692.8196 | 1214108.5621
49 | 2663704.6104 | 1214142.4772 | 2663703.3614 | 1214126.312
50 | 2663727.1833 | 1214145.3407 | 2663731.6683 | 1214141.4418 | 2663738.707 | 1214138.8154 | 2663747.251 | 1214136.5857
51 | 2663727.1833 | 1214145.3407 | 2663747.917 | 1214165.3969
52 | 2663747.917 | 1214165.3969 | 2663750.5498 | 1214167.9448
53 | 2663747.917 | 1214165.3969 | 2663735.5743 | 1214178.9067 | 2663735.503 | 1214185.5785
54 | 2663631.4771 | 1214134.7474 | 2663638.7964 | 1214121.0487 | 2663641.0686 | 1214116.8469
55 | 2663746.7368 | 1214197.9954 | 2663735.4851 | 1214187.2553 | 2663735.503 | 1214185.5785

## bus_geodata
| x | y | coords
0 | 2663541.8993 | 1214084.542
1 | 2663549.2737 | 1214085.1971
2 | 2663532.0932 | 1214083.6709
3 | 2663556.4834 | 1214085.8376
4 | 2663524.6038 | 1214142.6782
5 | 2663523.0994 | 1214146.9982
6 | 2663568.6112 | 1214086.915
7 | 2663536.9245 | 1214146.156
8 | 2663535.6705 | 1214150.5009
9 | 2663593.3011 | 1214036.0617
10 | 2663587.0941 | 1214088.557
11 | 2663594.9248 | 1214033.2294
12 | 2663499.2283 | 1213974.3686
13 | 2663498.7602 | 1213974.3213
14 | 2663515.2716 | 1213975.9905
15 | 2663456.0942 | 1213970.0078
16 | 2663431.4033 | 1213967.5116
17 | 2663432.0544 | 1213959.8132
18 | 2663433.0803 | 1213947.6839
19 | 2663605.3675 | 1214193.07
20 | 2663591.1028 | 1214186.7251
21 | 2663620.8948 | 1214155.4484
22 | 2663713.7953 | 1213993.0036
23 | 2663674.6666 | 1214051.6554
24 | 2663734.8678 | 1214027.6057
25 | 2663562.1002 | 1214159.2657
26 | 2663607.2255 | 1214157.2775
27 | 2663663.2751 | 1214045.7968
28 | 2663656.9279 | 1214058.4123
29 | 2663637.1823 | 1213888.7437
30 | 2663607.8319 | 1214010.7152
31 | 2663488.3745 | 1213949.8744
32 | 2663564.278 | 1214155.8979
33 | 2663549.911 | 1214154.1437
34 | 2663588.4821 | 1214088.6803
35 | 2663604.9468 | 1214090.143
36 | 2663626.0409 | 1214121.1132
37 | 2663616.4327 | 1214143.3794
38 | 2663636.1121 | 1214102.0124
39 | 2663647.0114 | 1214080.2905
40 | 2663639.1153 | 1214053.9927
41 | 2663694.8432 | 1214155.1791
42 | 2663682.8773 | 1214178.0953
43 | 2663703.9549 | 1214168.9405
44 | 2663694.5195 | 1214139.4179
45 | 2663703.3614 | 1214126.312
46 | 2663727.1833 | 1214145.3407
47 | 2663704.6104 | 1214142.4772
48 | 2663747.251 | 1214136.5857
49 | 2663747.917 | 1214165.3969
50 | 2663631.4771 | 1214134.7474
51 | 2663692.8196 | 1214108.5621
52 | 2663641.0686 | 1214116.8469
53 | 2663551.6367 | 1214149.7261
54 | 2663746.7368 | 1214197.9954
55 | 2663735.503 | 1214185.5785
56 | 2663750.5498 | 1214167.9448
57 | 2663525.4895 | 1214083.0842

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99796 | -0.038708 | 0.0079358 | 0.0019889
1 | 0.99803 | -0.037534 | 0.00099201 | 0.00024862
2 | 0.99795 | -0.038903 | 0.0011289 | 0.00028292
3 | 0.99809 | -0.03626 | 0.0041884 | 0.0010497
4 | 0.9859 | -0.27112 | 0.010291 | 0.0025793
5 | 0.98594 | -0.27027 | 0 | 0
6 | 0.99825 | -0.033226 | 0.0013487 | 0.00033803
7 | 0.98602 | -0.26864 | 0.0095507 | 0.0023936
8 | 0.98606 | -0.26787 | 0 | 0
9 | 0.99595 | -0.076937 | 0.0087102 | 0.002183
10 | 0.99909 | -0.017237 | 0.016514 | 0.0041389
11 | 0.99583 | -0.079301 | 0.013027 | 0.0032649
12 | 0.97275 | -0.52463 | 0.041253 | 0.010339
13 | 0.97278 | -0.52416 | 0.00095703 | 0.00023985
14 | 0.97256 | -0.52849 | 0.01298 | 0.0032531
15 | 0.97498 | -0.48067 | 0.0048635 | 0.0012189
16 | 0.97637 | -0.45338 | 0 | 0
17 | 0.9768 | -0.4449 | 0.0038706 | 0.00097007
18 | 0.97753 | -0.4307 | 0 | 0
19 | 0.98849 | -0.22074 | 0 | 0
20 | 0.98896 | -0.21154 | 0 | 0
21 | 0.98725 | -0.24482 | 0.015453 | 0.003873
22 | 0.98973 | -0.19483 | 0 | 0
23 | 0.99277 | -0.13713 | 0 | 0
24 | 0.98663 | -0.25428 | 0 | 0
25 | 0.98669 | -0.25558 | 0 | 0
26 | 0.99129 | -0.16658 | 0.0077342 | 0.0019384
27 | 0.99327 | -0.12762 | 0 | 0
28 | 0.99383 | -0.11715 | 0.026277 | 0.0065856
29 | 0.991 | -0.17088 | 0 | 0
30 | 0.99494 | -0.096128 | 0.044922 | 0.011258
31 | 0.98083 | -0.36639 | 0.0017124 | 0.00042916
32 | 0.98665 | -0.25646 | 0.012271 | 0.0030754
33 | 0.98633 | -0.26266 | 0 | 0
34 | 0.99916 | -0.015903 | 0.0010245 | 0.00025677
35 | 1 | 0 | -0.50841 | -0.12961
36 | 0.99459 | -0.10296 | 0.0088652 | 0.0022218
37 | 0.99256 | -0.14195 | 0.0082917 | 0.0020781
38 | 0.99657 | -0.065055 | 0.040392 | 0.010123
39 | 0.99511 | -0.092744 | 0.021621 | 0.0054188
40 | 0.99348 | -0.12381 | 0.020562 | 0.0051534
41 | 0.97403 | -0.49922 | 0 | 0
42 | 0.97254 | -0.52875 | 0.051236 | 0.012841
43 | 0.97568 | -0.4669 | 0 | 0
44 | 0.97369 | -0.50608 | 0.018744 | 0.0046976
45 | 0.98044 | -0.3738 | 0.0038442 | 0.00096345
46 | 0.97314 | -0.51676 | 0 | 0
47 | 0.97859 | -0.40976 | 0.0044711 | 0.0011206
48 | 0.97299 | -0.51968 | 0.0071349 | 0.0017882
49 | 0.97219 | -0.53564 | 0 | 0
50 | 0.98687 | -0.25213 | 0.0090238 | 0.0022616
51 | 0.97354 | -0.50888 | 0.0049264 | 0.0012347
52 | 0.98671 | -0.25524 | 0.0085469 | 0.002142
53 | 0.98629 | -0.26349 | 0.0097448 | 0.0024423
54 | 0.97155 | -0.54815 | 0.013663 | 0.0034243
55 | 0.97177 | -0.54381 | 0.0040686 | 0.0010197
56 | 0.97212 | -0.53685 | 0.017851 | 0.004474
57 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0090647 | -0.0022717 | 0.0090652 | 0.0022719 | 5.0716e-07 | 2.2785e-07 | 0.013516 | 0.013516 | 0.013516 | 0.99796 | -0.038708 | 0.99803 | -0.037534 | 3.7131
1 | 0.0011289 | 0.0002828 | -0.0011289 | -0.00028292 | 1.046e-08 | -1.2193e-07 | 0.0016832 | 0.0016832 | 0.0016832 | 0.99796 | -0.038708 | 0.99795 | -0.038903 | 0.46243
2 | -0.010057 | -0.0025205 | 0.010058 | 0.0025208 | 6.1029e-07 | 2.96e-07 | 0.014995 | 0.014995 | 0.014995 | 0.99803 | -0.037534 | 0.99809 | -0.03626 | 4.1195
3 | -0.014246 | -0.0035706 | 0.014248 | 0.0035717 | 2.0597e-06 | 1.159e-06 | 0.021239 | 0.021239 | 0.021239 | 0.99809 | -0.03626 | 0.99825 | -0.033226 | 5.835
4 | -0.010291 | -0.0025793 | 0.010292 | 0.0025795 | 4.1383e-07 | 2.0652e-07 | 0.015533 | 0.015533 | 0.015533 | 0.9859 | -0.27112 | 0.98594 | -0.27027 | 4.2672
5 | -0.010292 | -0.0025795 | 0.010293 | 0.00258 | 1.1775e-06 | 5.8761e-07 | 0.015533 | 0.015533 | 0.015533 | 0.98594 | -0.27027 | 0.98606 | -0.26787 | 4.2672
6 | 0.13402 | 0.034247 | -0.13373 | -0.034069 | 0.00028266 | 0.00017869 | 0.2 | 0.2 | 0.2 | 0.99825 | -0.033226 | 0.99595 | -0.076937 | 18.3154
7 | -0.14961 | -0.038157 | 0.14973 | 0.03823 | 0.00011561 | 7.326e-05 | 0.22325 | 0.22325 | 0.22325 | 0.99825 | -0.033226 | 0.99909 | -0.017237 | 20.4444
8 | -0.0095507 | -0.0023936 | 0.009551 | 0.0023938 | 3.5227e-07 | 1.6777e-07 | 0.014413 | 0.014413 | 0.014413 | 0.98602 | -0.26864 | 0.98606 | -0.26787 | 3.9596
9 | -0.019844 | -0.0049738 | 0.019849 | 0.0049768 | 4.9295e-06 | 2.9678e-06 | 0.029946 | 0.029946 | 0.029946 | 0.98606 | -0.26787 | 0.98633 | -0.26266 | 8.2268
10 | 0.12502 | 0.031886 | -0.12501 | -0.031877 | 1.4269e-05 | 9.0047e-06 | 0.18699 | 0.18699 | 0.18699 | 0.99595 | -0.076937 | 0.99583 | -0.079301 | 17.1237
11 | -0.16624 | -0.042369 | 0.16626 | 0.042376 | 1.07e-05 | 6.7934e-06 | 0.24785 | 0.24785 | 0.24785 | 0.99909 | -0.017237 | 0.99916 | -0.015903 | 22.6968
12 | 0.11198 | 0.028612 | -0.11189 | -0.028555 | 9.104e-05 | 5.7254e-05 | 0.16753 | 0.16753 | 0.16753 | 0.99583 | -0.079301 | 0.99494 | -0.096128 | 15.3412
13 | -0.054235 | -0.013593 | 0.054237 | 0.013594 | 1.2144e-06 | 7.7136e-07 | 0.082964 | 0.082964 | 0.082964 | 0.97275 | -0.52463 | 0.97278 | -0.52416 | 22.7923
14 | 0.012983 | 0.0032545 | -0.01298 | -0.0032531 | 2.385e-06 | 1.3262e-06 | 0.01986 | 0.01986 | 0.01986 | 0.97275 | -0.52463 | 0.97256 | -0.52849 | 5.456
15 | -0.055194 | -0.013834 | 0.055308 | 0.013907 | 0.00011463 | 7.2829e-05 | 0.084428 | 0.084428 | 0.084428 | 0.97278 | -0.52416 | 0.97498 | -0.48067 | 23.1945
16 | -0.060172 | -0.015126 | 0.06025 | 0.015176 | 7.8512e-05 | 4.9938e-05 | 0.091851 | 0.09185 | 0.091851 | 0.97498 | -0.48067 | 0.97637 | -0.45338 | 25.2337
17 | -0.06025 | -0.015176 | 0.060275 | 0.015191 | 2.4442e-05 | 1.5546e-05 | 0.09185 | 0.09185 | 0.09185 | 0.97637 | -0.45338 | 0.9768 | -0.4449 | 25.2336
18 | -0.064145 | -0.016161 | 0.064189 | 0.016189 | 4.3613e-05 | 2.776e-05 | 0.097747 | 0.097747 | 0.097747 | 0.9768 | -0.4449 | 0.97753 | -0.4307 | 26.8535
19 | -0.064189 | -0.016189 | 0.064387 | 0.016315 | 0.00019827 | 0.0001262 | 0.097747 | 0.097746 | 0.097747 | 0.97753 | -0.4307 | 0.98083 | -0.36639 | 26.8535
20 | -0.033069 | -0.0083046 | 0.033084 | 0.0083136 | 1.4512e-05 | 9.0874e-06 | 0.049787 | 0.049787 | 0.049787 | 0.98849 | -0.22074 | 0.98896 | -0.21154 | 13.6777
21 | 0.033069 | 0.0083046 | -0.033031 | -0.0082808 | 3.7955e-05 | 2.3768e-05 | 0.049787 | 0.049787 | 0.049787 | 0.98849 | -0.22074 | 0.98725 | -0.24482 | 13.6778
22 | 0.041964 | 0.010557 | -0.041875 | -0.010501 | 8.809e-05 | 5.5624e-05 | 0.063154 | 0.063154 | 0.063154 | 0.98896 | -0.21154 | 0.98669 | -0.25558 | 17.3499
23 | -0.075047 | -0.01887 | 0.075209 | 0.018973 | 0.00016155 | 0.00010296 | 0.11294 | 0.11294 | 0.11294 | 0.98896 | -0.21154 | 0.99129 | -0.16658 | 31.0275
24 | 0.017578 | 0.0044078 | -0.017572 | -0.0044042 | 6.1206e-06 | 3.62e-06 | 0.026495 | 0.026495 | 0.026495 | 0.98725 | -0.24482 | 0.98687 | -0.25213 | 7.2789
25 | -0.12792 | -0.03282 | 0.12828 | 0.033046 | 0.0003592 | 0.00022689 | 0.19259 | 0.19259 | 0.19259 | 0.98973 | -0.19483 | 0.99277 | -0.13713 | 17.6364
26 | 0.12792 | 0.03282 | -0.12755 | -0.032587 | 0.0003678 | 0.00023234 | 0.19259 | 0.19259 | 0.19259 | 0.98973 | -0.19483 | 0.98663 | -0.25428 | 17.6365
27 | -0.12828 | -0.033046 | 0.12834 | 0.033084 | 5.939e-05 | 3.7512e-05 | 0.19259 | 0.19259 | 0.19259 | 0.99277 | -0.13713 | 0.99327 | -0.12762 | 17.6363
28 | 0.12755 | 0.032587 | -0.12682 | -0.032121 | 0.00073249 | 0.00046612 | 0.19259 | 0.19259 | 0.19259 | 0.98663 | -0.25428 | 0.98044 | -0.3738 | 26.4549
29 | 0.012271 | 0.0030756 | -0.012271 | -0.0030754 | 5.1475e-07 | 2.7825e-07 | 0.018506 | 0.018506 | 0.018506 | 0.98669 | -0.25558 | 0.98665 | -0.25646 | 5.0841
30 | 0.029604 | 0.0074255 | -0.029594 | -0.0074193 | 9.9817e-06 | 6.2178e-06 | 0.044648 | 0.044648 | 0.044648 | 0.98669 | -0.25558 | 0.98633 | -0.26266 | 12.2658
31 | -0.082943 | -0.020912 | 0.083041 | 0.020974 | 9.7889e-05 | 6.2432e-05 | 0.12455 | 0.12455 | 0.12455 | 0.99129 | -0.16658 | 0.99256 | -0.14195 | 34.217
32 | -0.12834 | -0.033084 | 0.1284 | 0.033125 | 6.5474e-05 | 4.1355e-05 | 0.19259 | 0.19259 | 0.19259 | 0.99327 | -0.12762 | 0.99383 | -0.11715 | 17.6363
33 | -0.17525 | -0.044868 | 0.17545 | 0.045 | 0.00020742 | 0.00013181 | 0.26273 | 0.26273 | 0.26273 | 0.99383 | -0.11715 | 0.99511 | -0.092744 | 24.0593
34 | 0.020569 | 0.0051574 | -0.020562 | -0.0051534 | 6.5279e-06 | 3.9401e-06 | 0.030798 | 0.030798 | 0.030798 | 0.99383 | -0.11715 | 0.99348 | -0.12381 | 8.461
35 | -0.066727 | -0.017144 | 0.06697 | 0.017296 | 0.00024321 | 0.00015232 | 0.10034 | 0.10034 | 0.10034 | 0.991 | -0.17088 | 0.99494 | -0.096128 | 13.7834
36 | 0.066727 | 0.017144 | -0.0661 | -0.016744 | 0.00062713 | 0.00039925 | 0.10034 | 0.10034 | 0.10034 | 0.991 | -0.17088 | 0.98083 | -0.36639 | 27.5671
37 | 0.0097452 | 0.0024425 | -0.0097448 | -0.0024423 | 3.8437e-07 | 1.8547e-07 | 0.014702 | 0.014702 | 0.014702 | 0.98633 | -0.26266 | 0.98629 | -0.26349 | 4.039
38 | -0.16728 | -0.042633 | 0.16741 | 0.042714 | 0.00012849 | 8.1584e-05 | 0.24937 | 0.24937 | 0.24937 | 0.99916 | -0.015903 | 1 | 0 | 22.8365
39 | 0.33935 | 0.086891 | -0.33828 | -0.08621 | 0.0010657 | 0.00068072 | 0.50561 | 0.50561 | 0.50561 | 1 | 0 | 0.99657 | -0.065055 | 46.3013
40 | 0.091504 | 0.023161 | -0.091333 | -0.023052 | 0.00017092 | 0.00010907 | 0.13698 | 0.13698 | 0.13698 | 0.99459 | -0.10296 | 0.99256 | -0.14195 | 37.632
41 | -0.10037 | -0.025383 | 0.10055 | 0.0255 | 0.00018284 | 0.00011674 | 0.15024 | 0.15024 | 0.15024 | 0.99459 | -0.10296 | 0.99657 | -0.065055 | 41.2757
42 | 0.19734 | 0.050587 | -0.19708 | -0.050419 | 0.00026452 | 0.00016834 | 0.29506 | 0.29506 | 0.29506 | 0.99657 | -0.065055 | 0.99511 | -0.092744 | 27.02
43 | 0.051308 | 0.012887 | -0.051236 | -0.012841 | 7.2203e-05 | 4.5821e-05 | 0.078393 | 0.078393 | 0.078393 | 0.97403 | -0.49922 | 0.97254 | -0.52875 | 21.5365
44 | -0.074987 | -0.018824 | 0.075103 | 0.018898 | 0.0001158 | 7.382e-05 | 0.11457 | 0.11457 | 0.11457 | 0.97403 | -0.49922 | 0.97568 | -0.4669 | 31.4745
45 | 0.023678 | 0.0059371 | -0.023671 | -0.0059323 | 7.7438e-06 | 4.7597e-06 | 0.036174 | 0.036174 | 0.036174 | 0.97403 | -0.49922 | 0.97369 | -0.50608 | 9.938
46 | 0.042864 | 0.010797 | -0.042762 | -0.010733 | 0.00010195 | 6.4454e-05 | 0.065392 | 0.065392 | 0.065392 | 0.97568 | -0.4669 | 0.97314 | -0.51676 | 17.9649
47 | -0.11797 | -0.029695 | 0.11829 | 0.029902 | 0.00032313 | 0.00020647 | 0.17996 | 0.17996 | 0.17996 | 0.97568 | -0.4669 | 0.97859 | -0.40976 | 49.4392
48 | 0.004927 | 0.0012347 | -0.0049264 | -0.0012347 | 6.571e-07 | 3.6186e-08 | 0.0075296 | 0.0075297 | 0.0075297 | 0.97369 | -0.50608 | 0.97354 | -0.50888 | 2.0686
49 | 0.12297 | 0.031158 | -0.12276 | -0.031022 | 0.00021206 | 0.00013551 | 0.18676 | 0.18676 | 0.18676 | 0.98044 | -0.3738 | 0.97859 | -0.40976 | 51.3069
50 | 0.0071359 | 0.0017885 | -0.0071349 | -0.0017882 | 9.95e-07 | 3.5997e-07 | 0.010911 | 0.010912 | 0.010912 | 0.97314 | -0.51676 | 0.97299 | -0.51968 | 2.9977
51 | 0.035626 | 0.0089444 | -0.035594 | -0.0089243 | 3.2062e-05 | 2.0162e-05 | 0.054481 | 0.054481 | 0.054481 | 0.97314 | -0.51676 | 0.97219 | -0.53564 | 14.9673
52 | 0.017853 | 0.0044746 | -0.017851 | -0.004474 | 1.0258e-06 | 6.1111e-07 | 0.027325 | 0.027325 | 0.027325 | 0.97219 | -0.53564 | 0.97212 | -0.53685 | 7.5069
53 | 0.017741 | 0.0044497 | -0.017734 | -0.0044455 | 6.9056e-06 | 4.1101e-06 | 0.027156 | 0.027156 | 0.027156 | 0.97219 | -0.53564 | 0.97177 | -0.54381 | 7.4604
54 | 0.0085481 | 0.0021426 | -0.0085469 | -0.002142 | 1.2652e-06 | 5.5027e-07 | 0.012889 | 0.012889 | 0.012889 | 0.98687 | -0.25213 | 0.98671 | -0.25524 | 3.541
55 | -0.013663 | -0.0034243 | 0.013666 | 0.0034259 | 2.8296e-06 | 1.5975e-06 | 0.020926 | 0.020926 | 0.020926 | 0.97155 | -0.54815 | 0.97177 | -0.54381 | 5.7489

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.51774 | 0.13194

## res_load
| p_mw | q_mvar
0 | 0.0079358 | 0.0019889
1 | 0.00099201 | 0.00024862
2 | 0.0011289 | 0.00028292
3 | 0.0041884 | 0.0010497
4 | 0.010291 | 0.0025793
5 | 0.0013487 | 0.00033803
6 | 0.0095507 | 0.0023936
7 | 0.0087102 | 0.002183
8 | 0.016514 | 0.0041389
9 | 0.013027 | 0.0032649
10 | 0.041253 | 0.010339
11 | 0.00095703 | 0.00023985
12 | 0.01298 | 0.0032531
13 | 0.0048635 | 0.0012189
14 | 0.0038706 | 0.00097007
15 | 0.015453 | 0.003873
16 | 0.0077342 | 0.0019384
17 | 0.026277 | 0.0065856
18 | 0.044922 | 0.011258
19 | 0.0017124 | 0.00042916
20 | 0.012271 | 0.0030754
21 | 0.0010245 | 0.00025677
22 | 0.009332 | 0.0023388
23 | 0.0088652 | 0.0022218
24 | 0.0082917 | 0.0020781
25 | 0.040392 | 0.010123
26 | 0.021621 | 0.0054188
27 | 0.020562 | 0.0051534
28 | 0.051236 | 0.012841
29 | 0.018744 | 0.0046976
30 | 0.0038442 | 0.00096345
31 | 0.0044711 | 0.0011206
32 | 0.0071349 | 0.0017882
33 | 0.0090238 | 0.0022616
34 | 0.0049264 | 0.0012347
35 | 0.0085469 | 0.002142
36 | 0.0097448 | 0.0024423
37 | 0.013663 | 0.0034243
38 | 0.0040686 | 0.0010197
39 | 0.017851 | 0.004474

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1