## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1024-7_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1024-7_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1024-7_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1024-7_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1024-7_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1024-7_0_4_node_8 | 0.4 | n |  | TRUE
6 | bus_LV_1024-7_0_4_node_21 | 0.4 | n |  | TRUE
7 | bus_LV_1024-7_0_4_node_9 | 0.4 | n |  | TRUE
8 | bus_LV_1024-7_0_4_node_38 | 0.4 | n |  | TRUE
9 | bus_LV_1024-7_0_4_node_19 | 0.4 | n |  | TRUE
10 | bus_LV_1024-7_0_4_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_1024-7_0_4_node_13 | 0.4 | n |  | TRUE
12 | bus_LV_1024-7_0_4_node_39 | 0.4 | n |  | TRUE
13 | bus_LV_1024-7_0_4_node_17 | 0.4 | n |  | TRUE
14 | bus_LV_1024-7_0_4_node_12 | 0.4 | n |  | TRUE
15 | bus_LV_1024-7_0_4_node_16 | 0.4 | n |  | TRUE
16 | bus_LV_1024-7_0_4_node_37 | 0.4 | n |  | TRUE
17 | bus_LV_1024-7_0_4_node_36 | 0.4 | n |  | TRUE
18 | bus_LV_1024-7_0_4_node_5 | 0.4 | n |  | TRUE
19 | bus_LV_1024-7_0_4_node_33 | 0.4 | n |  | TRUE
20 | bus_LV_1024-7_0_4_node_10 | 0.4 | n |  | TRUE
21 | bus_LV_1024-7_0_4_node_35 | 0.4 | n |  | TRUE
22 | bus_LV_1024-7_0_4_node_30 | 0.4 | n |  | TRUE
23 | bus_LV_1024-7_0_4_node_32 | 0.4 | n |  | TRUE
24 | bus_LV_1024-7_0_4_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_1024-7_0_4_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_1024-7_0_4_node_28 | 0.4 | n |  | TRUE
27 | bus_LV_1024-7_0_4_node_31 | 0.4 | n |  | TRUE
28 | bus_LV_1024-7_0_4_node_27 | 0.4 | n |  | TRUE
29 | bus_LV_1024-7_0_4_node_23 | 0.4 | n |  | TRUE
30 | bus_LV_1024-7_0_4_node_29 | 0.4 | n |  | TRUE
31 | bus_LV_1024-7_0_4_node_22 | 0.4 | n |  | TRUE
32 | bus_LV_1024-7_0_4_node_11 | 0.4 | n |  | TRUE
33 | bus_LV_1024-7_0_4_node_40 | 0.4 | n |  | TRUE
34 | bus_LV_1024-7_0_4_node_14 | 0.4 | n |  | TRUE
35 | bus_LV_1024-7_0_4_node_34 | 0.4 | n |  | TRUE
36 | bus_LV_1024-7_0_4_node_26 | 0.4 | n |  | TRUE
37 | bus_LV_1024-7_0_4_node_24 | 0.4 | n |  | TRUE
38 | bus_LV_1024-7_0_4_node_25 | 0.4 | n |  | TRUE
39 | bus_MV_490_0_node_47 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1024-7_0_4_load_0 | 0 | 0.0016438 | 0.00041197 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1024-7_0_4_load_1 | 1 | 0.0043902 | 0.0011003 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1024-7_0_4_load_4 | 4 | 0.027497 | 0.0068913 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1024-7_0_4_load_21 | 6 | 0.0025425 | 0.0006372 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1024-7_0_4_load_38 | 8 | 0.011065 | 0.0027731 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1024-7_0_4_load_39 | 12 | 0.0070664 | 0.001771 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1024-7_0_4_load_37 | 16 | 0.011534 | 0.0028907 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1024-7_0_4_load_36 | 17 | 0.036518 | 0.0091522 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1024-7_0_4_load_5 | 18 | 0.053354 | 0.013372 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1024-7_0_4_load_33 | 19 | 0.027334 | 0.0068506 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1024-7_0_4_load_35 | 21 | 0.0031652 | 0.00079328 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1024-7_0_4_load_30 | 22 | 0.0019952 | 0.00050005 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1024-7_0_4_load_32 | 23 | 0.0026797 | 0.0006716 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1024-7_0_4_load_28 | 26 | 0.017469 | 0.004378 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1024-7_0_4_load_31 | 27 | 0.01573 | 0.0039423 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1024-7_0_4_load_27 | 28 | 0.035993 | 0.0090208 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1024-7_0_4_load_23 | 29 | 0.0026117 | 0.00065456 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1024-7_0_4_load_29 | 30 | 0.0032889 | 0.00082429 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1024-7_0_4_load_22 | 31 | 0.061597 | 0.015438 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1024-7_0_4_load_40 | 33 | 0.0030862 | 0.00077347 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1024-7_0_4_load_34 | 35 | 0.011457 | 0.0028714 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1024-7_0_4_load_26 | 36 | 0.01255 | 0.0031452 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1024-7_0_4_load_24 | 37 | 0.010355 | 0.0025951 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1024-7_0_4_load_25 | 38 | 0.012135 | 0.0030412 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 35 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1024-7_0_4_line_0 |  | 0 | 1 | 0.0068451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1024-7_0_4_line_1 |  | 0 | 2 | 0.014815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1024-7_0_4_line_2 |  | 1 | 3 | 0.04236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1024-7_0_4_line_3 |  | 2 | 4 | 0.023316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1024-7_0_4_line_4 |  | 3 | 5 | 0.13121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1024-7_0_4_line_5 |  | 4 | 6 | 0.0021241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1024-7_0_4_line_6 |  | 5 | 19 | 0.019135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
7 | LV_1024-7_0_4_line_7 |  | 5 | 10 | 0.156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_1024-7_0_4_line_8 |  | 6 | 31 | 0.028178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1024-7_0_4_line_9 |  | 7 | 8 | 0.036986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1024-7_0_4_line_10 |  | 7 | 9 | 0.023505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_1024-7_0_4_line_11 |  | 7 | 10 | 0.066875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
12 | LV_1024-7_0_4_line_12 |  | 9 | 30 | 0.010472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1024-7_0_4_line_13 |  | 9 | 14 | 0.021422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
14 | LV_1024-7_0_4_line_14 |  | 10 | 18 | 0.01802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1024-7_0_4_line_15 |  | 11 | 12 | 0.034121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1024-7_0_4_line_16 |  | 11 | 13 | 0.099621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1024-7_0_4_line_17 |  | 12 | 34 | 0.005514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1024-7_0_4_line_18 |  | 13 | 28 | 0.09735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1024-7_0_4_line_19 |  | 14 | 15 | 0.019795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1024-7_0_4_line_20 |  | 14 | 16 | 0.03087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_1024-7_0_4_line_21 |  | 15 | 17 | 0.019848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1024-7_0_4_line_22 |  | 16 | 36 | 0.029753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_1024-7_0_4_line_23 |  | 19 | 35 | 0.049764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_1024-7_0_4_line_24 |  | 20 | 21 | 0.022813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1024-7_0_4_line_25 |  | 20 | 22 | 0.034463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1024-7_0_4_line_26 |  | 20 | 23 | 0.021378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1024-7_0_4_line_27 |  | 22 | 30 | 0.025326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1024-7_0_4_line_28 |  | 24 | 25 | 0.049549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
29 | LV_1024-7_0_4_line_29 |  | 24 | 26 | 0.0089498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1024-7_0_4_line_30 |  | 24 | 27 | 0.043064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1024-7_0_4_line_31 |  | 25 | 29 | 0.02636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
32 | LV_1024-7_0_4_line_32 |  | 26 | 28 | 0.0069054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1024-7_0_4_line_33 |  | 29 | 37 | 0.031589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
34 | LV_1024-7_0_4_line_34 |  | 32 | 33 | 0.031132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1024-7_0_4_line_35 |  | 32 | 34 | 0.003969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1024-7_0_4_line_36 |  | 36 | 38 | 0.02514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
37 | LV_1024-7_0_4_line_37 |  | 37 | 38 | 0.024476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1024-7_0_4_trafo_34 | 0.63 MVA 20/0.4 kV | 39 | 35 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17
0 | 2663762.5848 | 1213617.4521 | 2663756.0673 | 1213615.36
1 | 2663776.6912 | 1213621.9801 | 2663762.5848 | 1213617.4521
2 | 2663726.0266 | 1213626.8306 | 2663735.101 | 1213608.6274 | 2663747.0239 | 1213612.4572 | 2663756.0673 | 1213615.36
3 | 2663776.6912 | 1213621.9801 | 2663771.0233 | 1213642.6879 | 2663770.4745 | 1213644.4514
4 | 2663671.3418 | 1213745.6533 | 2663684.1244 | 1213726.5891 | 2663697.0642 | 1213697.7872 | 2663716.4632 | 1213646.0069 | 2663726.0266 | 1213626.8306
5 | 2663769.8433 | 1213646.4795 | 2663770.4745 | 1213644.4514
6 | 2663671.3418 | 1213745.6533 | 2663688.1871 | 1213754.7296
7 | 2663671.3418 | 1213745.6533 | 2663662.8876 | 1213754.1905 | 2663649.6408 | 1213769.7921 | 2663639.6416 | 1213790.7094 | 2663692.1573 | 1213814.3734 | 2663705.5753 | 1213820.4204 | 2663703.4804 | 1213824.545 | 2663700.3945 | 1213833.2619 | 2663695.7247 | 1213846.6092
8 | 2663762.7486 | 1213673.4628 | 2663762.2679 | 1213670.8227 | 2663769.8433 | 1213646.4795
9 | 2663734.8346 | 1213850.2514 | 2663723.119 | 1213885.3368
10 | 2663743.8547 | 1213884.6912 | 2663740.2746 | 1213889.1891 | 2663738.6834 | 1213889.539 | 2663737.1597 | 1213889.2559 | 2663723.119 | 1213885.3368
11 | 2663695.7247 | 1213846.6092 | 2663691.5684 | 1213858.8279 | 2663687.5608 | 1213869.9253 | 2663686.5203 | 1213873.4719 | 2663723.119 | 1213885.3368
12 | 2663743.8547 | 1213884.6912 | 2663751.2172 | 1213877.2449
13 | 2663743.8547 | 1213884.6912 | 2663744.7137 | 1213885.3453 | 2663752.2179 | 1213891.0623 | 2663752.9713 | 1213891.6374 | 2663753.6871 | 1213892.1787 | 2663760.1365 | 1213897.0951 | 2663760.8975 | 1213897.6703
14 | 2663695.7247 | 1213846.6092 | 2663712.9273 | 1213851.9748
15 | 2663819.9403 | 1213590.3343 | 2663828.2735 | 1213593.1474 | 2663836.4476 | 1213595.2139 | 2663851.425 | 1213603.2125
16 | 2663935.4712 | 1213653.9551 | 2663934.2462 | 1213651.3181 | 2663930.4809 | 1213647.5532 | 2663918.3155 | 1213642.9756 | 2663907.4653 | 1213631.9192 | 2663892.7457 | 1213622.5557 | 2663864.5788 | 1213608.4343 | 2663851.425 | 1213603.2125
17 | 2663819.9403 | 1213590.3343 | 2663820.2785 | 1213589.2483 | 2663821.5842 | 1213585.0708
18 | 2663935.4712 | 1213653.9551 | 2663931.8077 | 1213661.9541 | 2663919.0648 | 1213689.2788 | 2663911.7633 | 1213705.7441 | 2663902.7434 | 1213723.7808 | 2663894.4203 | 1213737.7558 | 2663892.302 | 1213741.0997
19 | 2663756.0614 | 1213915.2072 | 2663756.5406 | 1213914.4341 | 2663759.4698 | 1213909.718 | 2663760.0417 | 1213908.8013 | 2663758.6644 | 1213906.8966 | 2663758.2165 | 1213904.0344 | 2663758.578 | 1213902.1927 | 2663758.8027 | 1213901.0722 | 2663760.8975 | 1213897.6703
20 | 2663760.8975 | 1213897.6703 | 2663772.0237 | 1213884.3254 | 2663781.9247 | 1213875.1547
21 | 2663756.0614 | 1213915.2072 | 2663773.7148 | 1213924.2801
22 | 2663781.9247 | 1213875.1547 | 2663783.8306 | 1213873.3894 | 2663797.6204 | 1213861.7074 | 2663801.338 | 1213858.5674 | 2663804.5295 | 1213855.812
23 | 2663730.2559 | 1213781.1821 | 2663725.4927 | 1213777.6846 | 2663704.414 | 1213763.4729 | 2663688.1871 | 1213754.7296
24 | 2663775.6142 | 1213831.9982 | 2663796.7807 | 1213839.3846 | 2663797.0962 | 1213839.7104
25 | 2663797.0962 | 1213839.7104 | 2663788.4808 | 1213846.9783 | 2663782.0023 | 1213851.8788 | 2663773.0187 | 1213855.9297 | 2663770.9533 | 1213857.2862 | 2663769.0253 | 1213859.2369
26 | 2663797.0962 | 1213839.7104 | 2663799.25 | 1213837.899 | 2663813.4786 | 1213825.9762
27 | 2663751.2172 | 1213877.2449 | 2663758.1373 | 1213870.2461 | 2663767.8434 | 1213860.4327 | 2663769.0253 | 1213859.2369
28 | 2663883.6006 | 1213754.3502 | 2663884.2265 | 1213754.7794 | 2663888.6531 | 1213757.7842 | 2663889.2564 | 1213758.1909 | 2663890.8543 | 1213759.3532 | 2663895.8063 | 1213762.9418 | 2663896.3942 | 1213763.3706 | 2663894.8625 | 1213766.6673 | 2663894.5489 | 1213768.2872 | 2663895.1537 | 1213770.684 | 2663895.9482 | 1213772.3825 | 2663897.4463 | 1213773.6437 | 2663896.7745 | 1213774.6594 | 2663890.8225 | 1213783.5789 | 2663889.8344 | 1213785.0581 | 2663889.8311 | 1213785.3694 | 2663889.6679 | 1213792.7945 | 2663889.6513 | 1213793.6392
29 | 2663883.6006 | 1213754.3502 | 2663887.3196 | 1213748.9645 | 2663888.6065 | 1213746.933
30 | 2663883.6006 | 1213754.3502 | 2663879.3107 | 1213760.5636 | 2663868.2784 | 1213774.3207 | 2663856.7479 | 1213787.0718 | 2663856.2652 | 1213787.5615
31 | 2663889.6513 | 1213793.6392 | 2663884.1342 | 1213793.8692 | 2663878.9055 | 1213794.836 | 2663871.0425 | 1213797.787 | 2663865.3971 | 1213802.1295
32 | 2663888.6065 | 1213746.933 | 2663892.302 | 1213741.0997
33 | 2663865.3971 | 1213802.1295 | 2663864.5707 | 1213802.7652 | 2663850.1762 | 1213816.9754 | 2663842.2582 | 1213823.5928
34 | 2663793.5922 | 1213570.1845 | 2663806.8549 | 1213575.1738 | 2663822.7642 | 1213581.2811
35 | 2663822.7642 | 1213581.2811 | 2663822.5282 | 1213582.0346 | 2663821.5842 | 1213585.0708
36 | 2663804.5295 | 1213855.812 | 2663823.5584 | 1213839.3833
37 | 2663823.5584 | 1213839.3833 | 2663829.4363 | 1213834.3086 | 2663842.2582 | 1213823.5928

## bus_geodata
| x | y | coords
0 | 2663762.5848 | 1213617.4521
1 | 2663756.0673 | 1213615.36
2 | 2663776.6912 | 1213621.9801
3 | 2663726.0266 | 1213626.8306
4 | 2663770.4745 | 1213644.4514
5 | 2663671.3418 | 1213745.6533
6 | 2663769.8433 | 1213646.4795
7 | 2663723.119 | 1213885.3368
8 | 2663734.8346 | 1213850.2514
9 | 2663743.8547 | 1213884.6912
10 | 2663695.7247 | 1213846.6092
11 | 2663851.425 | 1213603.2125
12 | 2663819.9403 | 1213590.3343
13 | 2663935.4712 | 1213653.9551
14 | 2663760.8975 | 1213897.6703
15 | 2663756.0614 | 1213915.2072
16 | 2663781.9247 | 1213875.1547
17 | 2663773.7148 | 1213924.2801
18 | 2663712.9273 | 1213851.9748
19 | 2663688.1871 | 1213754.7296
20 | 2663797.0962 | 1213839.7104
21 | 2663775.6142 | 1213831.9982
22 | 2663769.0253 | 1213859.2369
23 | 2663813.4786 | 1213825.9762
24 | 2663883.6006 | 1213754.3502
25 | 2663889.6513 | 1213793.6392
26 | 2663888.6065 | 1213746.933
27 | 2663856.2652 | 1213787.5615
28 | 2663892.302 | 1213741.0997
29 | 2663865.3971 | 1213802.1295
30 | 2663751.2172 | 1213877.2449
31 | 2663762.7486 | 1213673.4628
32 | 2663822.7642 | 1213581.2811
33 | 2663793.5922 | 1213570.1845
34 | 2663821.5842 | 1213585.0708
35 | 2663730.2559 | 1213781.1821
36 | 2663804.5295 | 1213855.812
37 | 2663842.2582 | 1213823.5928
38 | 2663823.5584 | 1213839.3833
39 | 2663671.3418 | 1213745.6533

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97787 | -0.42348 | 0.0016438 | 0.00041197
1 | 0.97847 | -0.41185 | 0.0043902 | 0.0011003
2 | 0.97661 | -0.44826 | 0 | 0
3 | 0.98232 | -0.33683 | 0 | 0
4 | 0.97462 | -0.48739 | 0.027497 | 0.0068913
5 | 0.99427 | -0.10813 | 0 | 0
6 | 0.97449 | -0.48989 | 0.0025425 | 0.0006372
7 | 0.98267 | -0.33142 | 0 | 0
8 | 0.98229 | -0.33881 | 0.011065 | 0.0027731
9 | 0.98171 | -0.35013 | 0 | 0
10 | 0.98558 | -0.27506 | 0 | 0
11 | 0.97241 | -0.53259 | 0 | 0
12 | 0.97209 | -0.53898 | 0.0070664 | 0.001771
13 | 0.97335 | -0.51396 | 0 | 0
14 | 0.98089 | -0.36613 | 0 | 0
15 | 0.98022 | -0.37923 | 0 | 0
16 | 0.97997 | -0.38412 | 0.011534 | 0.0028907
17 | 0.97955 | -0.39239 | 0.036518 | 0.0091522
18 | 0.98469 | -0.29233 | 0.053354 | 0.013372
19 | 0.99578 | -0.079632 | 0.027334 | 0.0068506
20 | 0.98123 | -0.35947 | 0 | 0
21 | 0.98116 | -0.36078 | 0.0031652 | 0.00079328
22 | 0.98142 | -0.35583 | 0.0019952 | 0.00050005
23 | 0.98118 | -0.36051 | 0.0026797 | 0.0006716
24 | 0.9751 | -0.47948 | 0 | 0
25 | 0.97693 | -0.44351 | 0 | 0
26 | 0.97457 | -0.48993 | 0.017469 | 0.004378
27 | 0.97447 | -0.49191 | 0.01573 | 0.0039423
28 | 0.97427 | -0.49578 | 0.035993 | 0.0090208
29 | 0.97742 | -0.43397 | 0.0026117 | 0.00065456
30 | 0.9816 | -0.35223 | 0.0032889 | 0.00082429
31 | 0.97288 | -0.5218 | 0.061597 | 0.015438
32 | 0.97206 | -0.53952 | 0 | 0
33 | 0.97197 | -0.54129 | 0.0030862 | 0.00077347
34 | 0.97207 | -0.53929 | 0 | 0
35 | 1 | 0 | -0.3745 | -0.096231
36 | 0.97916 | -0.39993 | 0.01255 | 0.0031452
37 | 0.97802 | -0.42216 | 0.010355 | 0.0025951
38 | 0.97855 | -0.41187 | 0.012135 | 0.0030412
39 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.093662 | -0.023622 | 0.093714 | 0.023655 | 5.218e-05 | 3.3309e-05 | 0.14258 | 0.14258 | 0.14258 | 0.97787 | -0.42348 | 0.97847 | -0.41185 | 39.1694
1 | 0.092018 | 0.02321 | -0.091909 | -0.02314 | 0.00010901 | 6.958e-05 | 0.14008 | 0.14008 | 0.14008 | 0.97787 | -0.42348 | 0.97661 | -0.44826 | 38.4822
2 | -0.098104 | -0.024755 | 0.098458 | 0.024981 | 0.00035386 | 0.00022594 | 0.14925 | 0.14925 | 0.14925 | 0.97847 | -0.41185 | 0.98232 | -0.33683 | 41.0035
3 | 0.091909 | 0.02314 | -0.091737 | -0.023031 | 0.00017156 | 0.00010951 | 0.14008 | 0.14008 | 0.14008 | 0.97661 | -0.44826 | 0.97462 | -0.48739 | 38.4822
4 | -0.098458 | -0.024981 | 0.099554 | 0.025681 | 0.0010961 | 0.00069979 | 0.14925 | 0.14925 | 0.14925 | 0.98232 | -0.33683 | 0.99427 | -0.10813 | 41.0035
5 | 0.064241 | 0.016139 | -0.064233 | -0.016134 | 7.6646e-06 | 4.8789e-06 | 0.098094 | 0.098094 | 0.098094 | 0.97462 | -0.48739 | 0.97449 | -0.48989 | 26.949
6 | -0.3436 | -0.088157 | 0.34407 | 0.08846 | 0.00047569 | 0.00030345 | 0.51495 | 0.51495 | 0.51495 | 0.99427 | -0.10813 | 0.99578 | -0.079632 | 35.3675
7 | 0.24404 | 0.062476 | -0.24209 | -0.061232 | 0.0019559 | 0.0012437 | 0.3657 | 0.3657 | 0.3657 | 0.99427 | -0.10813 | 0.98558 | -0.27506 | 25.1169
8 | 0.06169 | 0.015497 | -0.061597 | -0.015438 | 9.3791e-05 | 5.9676e-05 | 0.094212 | 0.094212 | 0.094212 | 0.97449 | -0.48989 | 0.97288 | -0.5218 | 25.8825
9 | 0.011069 | 0.0027752 | -0.011065 | -0.0027731 | 3.8967e-06 | 2.0255e-06 | 0.016761 | 0.016762 | 0.016762 | 0.98267 | -0.33142 | 0.98229 | -0.33881 | 4.6048
10 | 0.17711 | 0.044734 | -0.17695 | -0.044634 | 0.00015865 | 0.00010034 | 0.26832 | 0.26832 | 0.26832 | 0.98267 | -0.33142 | 0.98171 | -0.35013 | 18.4283
11 | -0.18818 | -0.047509 | 0.18869 | 0.047832 | 0.00050952 | 0.00032269 | 0.28508 | 0.28508 | 0.28508 | 0.98267 | -0.33142 | 0.98558 | -0.27506 | 19.5795
12 | 0.011133 | 0.0027902 | -0.011132 | -0.0027896 | 1.1182e-06 | 5.8326e-07 | 0.016875 | 0.016875 | 0.016875 | 0.98171 | -0.35013 | 0.9816 | -0.35223 | 4.6359
13 | 0.16582 | 0.041844 | -0.16569 | -0.041763 | 0.00012697 | 8.018e-05 | 0.25144 | 0.25144 | 0.25144 | 0.98171 | -0.35013 | 0.98089 | -0.36613 | 17.2694
14 | 0.053398 | 0.0134 | -0.053354 | -0.013372 | 4.3928e-05 | 2.7885e-05 | 0.080627 | 0.080627 | 0.080627 | 0.98558 | -0.27506 | 0.98469 | -0.29233 | 22.1502
15 | 0.010156 | 0.0025457 | -0.010153 | -0.0025442 | 3.0905e-06 | 1.5548e-06 | 0.015541 | 0.015541 | 0.015541 | 0.97241 | -0.53259 | 0.97209 | -0.53898 | 4.2696
16 | -0.010156 | -0.0025457 | 0.010165 | 0.0025503 | 9.0228e-06 | 4.5375e-06 | 0.015541 | 0.015541 | 0.015541 | 0.97241 | -0.53259 | 0.97335 | -0.51396 | 4.2696
17 | 0.0030865 | 0.00077318 | -0.0030865 | -0.00077322 | 4.6155e-08 | -3.8817e-08 | 0.0047245 | 0.0047246 | 0.0047246 | 0.97209 | -0.53898 | 0.97207 | -0.53929 | 1.298
18 | -0.010165 | -0.0025503 | 0.010174 | 0.0025547 | 8.8166e-06 | 4.4315e-06 | 0.015541 | 0.01554 | 0.015541 | 0.97335 | -0.51396 | 0.97427 | -0.49578 | 4.2694
19 | 0.036563 | 0.009181 | -0.036541 | -0.0091666 | 2.2843e-05 | 1.437e-05 | 0.055473 | 0.055473 | 0.055473 | 0.98089 | -0.36613 | 0.98022 | -0.37923 | 15.2399
20 | 0.12913 | 0.032582 | -0.12902 | -0.032513 | 0.00011114 | 6.9575e-05 | 0.19597 | 0.19597 | 0.19597 | 0.98089 | -0.36613 | 0.97997 | -0.38412 | 13.4594
21 | 0.036541 | 0.0091666 | -0.036518 | -0.0091522 | 2.2905e-05 | 1.4409e-05 | 0.055473 | 0.055473 | 0.055473 | 0.98022 | -0.37923 | 0.97955 | -0.39239 | 15.24
22 | 0.11748 | 0.029622 | -0.11739 | -0.029567 | 8.8832e-05 | 5.5354e-05 | 0.17846 | 0.17846 | 0.17846 | 0.97997 | -0.38412 | 0.97916 | -0.39993 | 12.2566
23 | -0.37141 | -0.095311 | 0.37285 | 0.09623 | 0.0014412 | 0.00091975 | 0.5558 | 0.5558 | 0.5558 | 0.99578 | -0.079632 | 1 | 0 | 38.1729
24 | 0.0031654 | 0.00079312 | -0.0031652 | -0.00079328 | 1.9713e-07 | -1.6198e-07 | 0.0048002 | 0.0048004 | 0.0048004 | 0.98123 | -0.35947 | 0.98116 | -0.36078 | 1.3188
25 | -0.0058453 | -0.0014645 | 0.0058463 | 0.0014648 | 1.0154e-06 | 2.1447e-07 | 0.0088641 | 0.008864 | 0.0088641 | 0.98123 | -0.35947 | 0.98142 | -0.35583 | 2.4352
26 | 0.0026799 | 0.00067142 | -0.0026797 | -0.0006716 | 1.324e-07 | -1.8528e-07 | 0.0040639 | 0.004064 | 0.004064 | 0.98123 | -0.35947 | 0.98118 | -0.36051 | 1.1165
27 | -0.0078415 | -0.0019648 | 0.0078429 | 0.0019653 | 1.3424e-06 | 5.3907e-07 | 0.011889 | 0.011889 | 0.011889 | 0.98142 | -0.35583 | 0.9816 | -0.35223 | 3.2662
28 | -0.07942 | -0.01993 | 0.079556 | 0.020016 | 0.00013648 | 8.6109e-05 | 0.1212 | 0.1212 | 0.1212 | 0.9751 | -0.47948 | 0.97693 | -0.44351 | 16.6489
29 | 0.06368 | 0.015982 | -0.063649 | -0.015962 | 3.1699e-05 | 2.0175e-05 | 0.097185 | 0.097185 | 0.097185 | 0.9751 | -0.47948 | 0.97457 | -0.48993 | 26.6991
30 | 0.015739 | 0.0039477 | -0.01573 | -0.0039423 | 9.3169e-06 | 5.426e-06 | 0.024019 | 0.02402 | 0.02402 | 0.9751 | -0.47948 | 0.97447 | -0.49191 | 6.5988
31 | -0.079556 | -0.020016 | 0.079592 | 0.020038 | 3.6303e-05 | 2.1913e-05 | 0.1212 | 0.1212 | 0.1212 | 0.97693 | -0.44351 | 0.97742 | -0.43397 | 8.3244
32 | 0.04618 | 0.011584 | -0.046167 | -0.011575 | 1.2875e-05 | 8.1542e-06 | 0.070513 | 0.070513 | 0.070513 | 0.97457 | -0.48993 | 0.97427 | -0.49578 | 19.3717
33 | -0.082204 | -0.020692 | 0.08225 | 0.02072 | 4.6405e-05 | 2.8115e-05 | 0.12518 | 0.12518 | 0.12518 | 0.97742 | -0.43397 | 0.97802 | -0.42216 | 8.5975
34 | 0.0030864 | 0.00077325 | -0.0030862 | -0.00077347 | 2.606e-07 | -2.191e-07 | 0.0047246 | 0.0047247 | 0.0047247 | 0.97206 | -0.53952 | 0.97197 | -0.54129 | 1.298
35 | -0.0030864 | -0.00077325 | 0.0030865 | 0.00077322 | 3.3223e-08 | -2.7939e-08 | 0.0047246 | 0.0047246 | 0.0047246 | 0.97206 | -0.53952 | 0.97207 | -0.53929 | 1.298
36 | 0.10485 | 0.026422 | -0.10479 | -0.026385 | 5.9872e-05 | 3.7054e-05 | 0.15938 | 0.15938 | 0.15938 | 0.97916 | -0.39993 | 0.97855 | -0.41187 | 10.9468
37 | -0.092605 | -0.023315 | 0.092651 | 0.023343 | 4.5575e-05 | 2.7939e-05 | 0.14093 | 0.14093 | 0.14093 | 0.97802 | -0.42216 | 0.97855 | -0.41187 | 9.6795

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.38596 | 0.099102

## res_load
| p_mw | q_mvar
0 | 0.0016438 | 0.00041197
1 | 0.0043902 | 0.0011003
2 | 0.027497 | 0.0068913
3 | 0.0025425 | 0.0006372
4 | 0.011065 | 0.0027731
5 | 0.0070664 | 0.001771
6 | 0.011534 | 0.0028907
7 | 0.036518 | 0.0091522
8 | 0.053354 | 0.013372
9 | 0.027334 | 0.0068506
10 | 0.0031652 | 0.00079328
11 | 0.0019952 | 0.00050005
12 | 0.0026797 | 0.0006716
13 | 0.017469 | 0.004378
14 | 0.01573 | 0.0039423
15 | 0.035993 | 0.0090208
16 | 0.0026117 | 0.00065456
17 | 0.0032889 | 0.00082429
18 | 0.061597 | 0.015438
19 | 0.0030862 | 0.00077347
20 | 0.011457 | 0.0028714
21 | 0.01255 | 0.0031452
22 | 0.010355 | 0.0025951
23 | 0.012135 | 0.0030412

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1