## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1024-8_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1024-8_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1024-8_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1024-8_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1024-8_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1024-8_0_6_node_19 | 0.4 | n |  | TRUE
6 | bus_LV_1024-8_0_6_node_16 | 0.4 | n |  | TRUE
7 | bus_LV_1024-8_0_6_node_27 | 0.4 | n |  | TRUE
8 | bus_LV_1024-8_0_6_node_24 | 0.4 | n |  | TRUE
9 | bus_LV_1024-8_0_6_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_1024-8_0_6_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_1024-8_0_6_node_50 | 0.4 | n |  | TRUE
12 | bus_LV_1024-8_0_6_node_11 | 0.4 | n |  | TRUE
13 | bus_LV_1024-8_0_6_node_51 | 0.4 | n |  | TRUE
14 | bus_LV_1024-8_0_6_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_1024-8_0_6_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_1024-8_0_6_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_1024-8_0_6_node_23 | 0.4 | n |  | TRUE
18 | bus_LV_1024-8_0_6_node_55 | 0.4 | n |  | TRUE
19 | bus_LV_1024-8_0_6_node_17 | 0.4 | n |  | TRUE
20 | bus_LV_1024-8_0_6_node_53 | 0.4 | n |  | TRUE
21 | bus_LV_1024-8_0_6_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_1024-8_0_6_node_52 | 0.4 | n |  | TRUE
23 | bus_LV_1024-8_0_6_node_18 | 0.4 | n |  | TRUE
24 | bus_LV_1024-8_0_6_node_13 | 0.4 | n |  | TRUE
25 | bus_LV_1024-8_0_6_node_45 | 0.4 | n |  | TRUE
26 | bus_LV_1024-8_0_6_node_42 | 0.4 | n |  | TRUE
27 | bus_LV_1024-8_0_6_node_15 | 0.4 | n |  | TRUE
28 | bus_LV_1024-8_0_6_node_36 | 0.4 | n |  | TRUE
29 | bus_LV_1024-8_0_6_node_54 | 0.4 | n |  | TRUE
30 | bus_LV_1024-8_0_6_node_44 | 0.4 | n |  | TRUE
31 | bus_LV_1024-8_0_6_node_46 | 0.4 | n |  | TRUE
32 | bus_LV_1024-8_0_6_node_34 | 0.4 | n |  | TRUE
33 | bus_LV_1024-8_0_6_node_33 | 0.4 | n |  | TRUE
34 | bus_LV_1024-8_0_6_node_21 | 0.4 | n |  | TRUE
35 | bus_LV_1024-8_0_6_node_35 | 0.4 | n |  | TRUE
36 | bus_LV_1024-8_0_6_node_26 | 0.4 | n |  | TRUE
37 | bus_LV_1024-8_0_6_node_22 | 0.4 | n |  | TRUE
38 | bus_LV_1024-8_0_6_node_25 | 0.4 | n |  | TRUE
39 | bus_LV_1024-8_0_6_node_43 | 0.4 | n |  | TRUE
40 | bus_LV_1024-8_0_6_node_48 | 0.4 | n |  | TRUE
41 | bus_LV_1024-8_0_6_node_47 | 0.4 | n |  | TRUE
42 | bus_LV_1024-8_0_6_node_49 | 0.4 | n |  | TRUE
43 | bus_LV_1024-8_0_6_node_39 | 0.4 | n |  | TRUE
44 | bus_LV_1024-8_0_6_node_31 | 0.4 | n |  | TRUE
45 | bus_LV_1024-8_0_6_node_40 | 0.4 | n |  | TRUE
46 | bus_LV_1024-8_0_6_node_28 | 0.4 | n |  | TRUE
47 | bus_LV_1024-8_0_6_node_29 | 0.4 | n |  | TRUE
48 | bus_LV_1024-8_0_6_node_37 | 0.4 | n |  | TRUE
49 | bus_LV_1024-8_0_6_node_38 | 0.4 | n |  | TRUE
50 | bus_LV_1024-8_0_6_node_41 | 0.4 | n |  | TRUE
51 | bus_MV_218_0_node_100 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1024-8_0_6_load_0 | 0 | 0.037572 | 0.0094163 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1024-8_0_6_load_27 | 7 | 0.079537 | 0.019934 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1024-8_0_6_load_24 | 8 | 0.046341 | 0.011614 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1024-8_0_6_load_50 | 11 | 0.078663 | 0.019715 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1024-8_0_6_load_51 | 13 | 0.027897 | 0.0069915 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1024-8_0_6_load_23 | 17 | 0.042893 | 0.01075 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1024-8_0_6_load_55 | 18 | 0.019122 | 0.0047925 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1024-8_0_6_load_53 | 20 | 0.011074 | 0.0027754 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1024-8_0_6_load_52 | 22 | 0.013021 | 0.0032634 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1024-8_0_6_load_45 | 25 | 0.0053666 | 0.001345 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1024-8_0_6_load_42 | 26 | 0.0080751 | 0.0020238 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1024-8_0_6_load_36 | 28 | 0.011368 | 0.0028491 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1024-8_0_6_load_54 | 29 | 0.0081684 | 0.0020472 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1024-8_0_6_load_46 | 31 | 0.010947 | 0.0027435 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1024-8_0_6_load_33 | 33 | 0.0040173 | 0.0010068 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1024-8_0_6_load_35 | 35 | 0.0066417 | 0.0016646 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1024-8_0_6_load_26 | 36 | 0.012096 | 0.0030315 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1024-8_0_6_load_25 | 38 | 0.020971 | 0.0052559 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1024-8_0_6_load_48 | 40 | 0.013515 | 0.0033872 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1024-8_0_6_load_47 | 41 | 0.013513 | 0.0033867 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1024-8_0_6_load_49 | 42 | 0.010942 | 0.0027422 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1024-8_0_6_load_39 | 43 | 0.0020054 | 0.0005026 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1024-8_0_6_load_31 | 44 | 0.0049052 | 0.0012293 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1024-8_0_6_load_40 | 45 | 0.0054102 | 0.0013559 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1024-8_0_6_load_28 | 46 | 0.0015722 | 0.00039402 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1024-8_0_6_load_29 | 47 | 0.0067537 | 0.0016926 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1024-8_0_6_load_37 | 48 | 0.00338 | 0.00084711 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1024-8_0_6_load_38 | 49 | 0.0019866 | 0.0004979 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 3 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1024-8_0_6_line_0 |  | 0 | 1 | 0.037127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1024-8_0_6_line_1 |  | 0 | 2 | 0.059812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1024-8_0_6_line_2 |  | 1 | 3 | 0.005966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
3 | LV_1024-8_0_6_line_3 |  | 1 | 4 | 0.018699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
4 | LV_1024-8_0_6_line_4 |  | 2 | 5 | 0.09676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1024-8_0_6_line_5 |  | 3 | 6 | 0.032512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1024-8_0_6_line_6 |  | 3 | 7 | 0.012725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_1024-8_0_6_line_7 |  | 4 | 8 | 0.004582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_1024-8_0_6_line_8 |  | 5 | 32 | 0.096942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1024-8_0_6_line_9 |  | 5 | 33 | 0.081706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1024-8_0_6_line_10 |  | 6 | 27 | 0.028012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1024-8_0_6_line_11 |  | 7 | 37 | 0.017631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1024-8_0_6_line_12 |  | 8 | 14 | 0.020097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1024-8_0_6_line_13 |  | 8 | 15 | 0.022278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1024-8_0_6_line_14 |  | 9 | 10 | 0.013107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1024-8_0_6_line_15 |  | 9 | 11 | 0.010905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1024-8_0_6_line_16 |  | 9 | 12 | 0.15759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1024-8_0_6_line_17 |  | 10 | 13 | 0.011668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1024-8_0_6_line_18 |  | 10 | 14 | 0.060539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1024-8_0_6_line_19 |  | 12 | 19 | 0.10541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1024-8_0_6_line_20 |  | 12 | 20 | 0.006638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1024-8_0_6_line_21 |  | 15 | 16 | 0.019082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1024-8_0_6_line_22 |  | 15 | 17 | 0.016767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1024-8_0_6_line_23 |  | 16 | 18 | 0.038761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1024-8_0_6_line_24 |  | 19 | 29 | 0.014391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1024-8_0_6_line_25 |  | 21 | 22 | 0.005813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1024-8_0_6_line_26 |  | 21 | 23 | 0.03833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1024-8_0_6_line_27 |  | 23 | 30 | 0.034644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1024-8_0_6_line_28 |  | 23 | 31 | 0.0088583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1024-8_0_6_line_29 |  | 24 | 25 | 0.0033373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1024-8_0_6_line_30 |  | 24 | 26 | 0.029539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1024-8_0_6_line_31 |  | 26 | 39 | 0.0052049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1024-8_0_6_line_32 |  | 27 | 28 | 0.027077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1024-8_0_6_line_33 |  | 30 | 42 | 0.016968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1024-8_0_6_line_34 |  | 30 | 39 | 0.022021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1024-8_0_6_line_35 |  | 32 | 43 | 0.048824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1024-8_0_6_line_36 |  | 33 | 44 | 0.034144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1024-8_0_6_line_37 |  | 34 | 35 | 0.022859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1024-8_0_6_line_38 |  | 34 | 36 | 0.018726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1024-8_0_6_line_39 |  | 35 | 45 | 0.0049215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1024-8_0_6_line_40 |  | 36 | 38 | 0.032186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1024-8_0_6_line_41 |  | 37 | 38 | 0.027803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1024-8_0_6_line_42 |  | 39 | 50 | 0.017481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1024-8_0_6_line_43 |  | 40 | 41 | 0.021615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1024-8_0_6_line_44 |  | 41 | 50 | 0.026178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1024-8_0_6_line_45 |  | 43 | 49 | 0.0072886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1024-8_0_6_line_46 |  | 44 | 47 | 0.030278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1024-8_0_6_line_47 |  | 45 | 50 | 0.010384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1024-8_0_6_line_48 |  | 46 | 47 | 0.021488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1024-8_0_6_line_49 |  | 48 | 49 | 0.022467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1024-8_0_6_trafo_3 | 0.63 MVA 20/0.4 kV | 51 | 3 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18
0 | 2664242.6481 | 1213762.5334 | 2664235.8377 | 1213765.7621 | 2664222.2737 | 1213767.6616 | 2664206.416 | 1213768.728
1 | 2664146.7384 | 1213772.7409 | 2664206.416 | 1213768.728
2 | 2664246.082 | 1213767.4179 | 2664245.4386 | 1213766.4993 | 2664242.6481 | 1213762.5334
3 | 2664242.6481 | 1213762.5334 | 2664239.5058 | 1213758.0746 | 2664239.0495 | 1213757.4248 | 2664239.606 | 1213754.4179 | 2664238.8175 | 1213750.0511 | 2664239.5214 | 1213749.5806 | 2664242.9488 | 1213747.3161
4 | 2664070.5656 | 1213811.0015 | 2664068.4673 | 1213805.52 | 2664075.0009 | 1213799.7644 | 2664096.7852 | 1213786.4013 | 2664100.6006 | 1213779.8271 | 2664103.4488 | 1213774.9102 | 2664132.876 | 1213773.4367 | 2664146.7384 | 1213772.7409
5 | 2664246.082 | 1213767.4179 | 2664248.1711 | 1213767.3959 | 2664249.7198 | 1213768.1797 | 2664251.2867 | 1213770.0978 | 2664253.4907 | 1213772.801 | 2664267.8777 | 1213790.3891
6 | 2664246.082 | 1213767.4179 | 2664237.7872 | 1213769.5298 | 2664233.6727 | 1213770.1814
7 | 2664242.9488 | 1213747.3161 | 2664246.2768 | 1213745.1062 | 2664246.7741 | 1213744.778
8 | 2664070.5656 | 1213811.0015 | 2664069.8948 | 1213818.2877 | 2664080.3888 | 1213834.8662 | 2664102.5878 | 1213866.9912 | 2664106.3262 | 1213874.6472 | 2664106.3335 | 1213880.3175 | 2664103.1949 | 1213887.5326 | 2664098.9476 | 1213895.4141
9 | 2664070.5656 | 1213811.0015 | 2664079.2898 | 1213820.5122 | 2664118.6897 | 1213870.6332 | 2664122.1926 | 1213874.2665
10 | 2664267.8777 | 1213790.3891 | 2664275.3246 | 1213799.9752 | 2664285.9145 | 1213811.8411
11 | 2664216.1433 | 1213771.9427 | 2664218.9707 | 1213771.7842 | 2664228.3218 | 1213771.0288 | 2664233.6727 | 1213770.1814
12 | 2664246.7741 | 1213744.778 | 2664258.1334 | 1213761.3773
13 | 2664246.7741 | 1213744.778 | 2664238.0097 | 1213731.9646 | 2664234.0736 | 1213726.4521
14 | 2664305.0439 | 1213779.872 | 2664294.5673 | 1213787.7862
15 | 2664296.4651 | 1213773.1087 | 2664305.0439 | 1213779.872
16 | 2664305.0439 | 1213779.872 | 2664319.1238 | 1213763.2468 | 2664320.6983 | 1213753.1909 | 2664317.2699 | 1213744.9822 | 2664310.2904 | 1213733.6111 | 2664308.1256 | 1213730.0856 | 2664311.045 | 1213728.4382 | 2664303.6361 | 1213717.4293 | 2664300.6214 | 1213712.416 | 2664323.4361 | 1213688.8251 | 2664335.2995 | 1213702.3392 | 2664336.8241 | 1213703.9566 | 2664340.2318 | 1213700.7025 | 2664346.2755 | 1213693.2186 | 2664345.1907 | 1213691.6726 | 2664344.6175 | 1213689.8876 | 2664344.6151 | 1213687.9975 | 2664345.189 | 1213686.2026 | 2664346.2842 | 1213684.669
17 | 2664294.5673 | 1213787.7862 | 2664303.9336 | 1213794.7803
18 | 2664258.1334 | 1213761.3773 | 2664260.1894 | 1213764.4346 | 2664263.9722 | 1213770.0678 | 2664268.3425 | 1213776.1631 | 2664281.6523 | 1213792.9057 | 2664286.3444 | 1213798.7376 | 2664289.1334 | 1213795.0988 | 2664294.5673 | 1213787.7862
19 | 2664298.8586 | 1213646.2672 | 2664300.0018 | 1213656.4747 | 2664295.548 | 1213669.3903 | 2664300.8315 | 1213672.5158 | 2664331.4097 | 1213704.5097 | 2664333.8851 | 1213706.7044 | 2664336.8241 | 1213703.9566 | 2664340.2318 | 1213700.7025 | 2664346.2755 | 1213693.2186 | 2664345.1907 | 1213691.6726 | 2664344.6175 | 1213689.8876 | 2664344.6151 | 1213687.9975 | 2664345.189 | 1213686.2026 | 2664346.2842 | 1213684.669
20 | 2664342.4919 | 1213679.2136 | 2664346.2842 | 1213684.669
21 | 2664234.0736 | 1213726.4521 | 2664229.5615 | 1213720.1218 | 2664238.2532 | 1213712.8887
22 | 2664234.0736 | 1213726.4521 | 2664234.7846 | 1213722.5018 | 2664235.9163 | 1213718.9896 | 2664242.6505 | 1213712.9233
23 | 2664238.2532 | 1213712.8887 | 2664220.0529 | 1213688.9447 | 2664226.9845 | 1213683.6382
24 | 2664286.6818 | 1213638.5423 | 2664298.8586 | 1213646.2672
25 | 2664299.9628 | 1213855.1749 | 2664296.4867 | 1213859.8403
26 | 2664264.7556 | 1213846.0676 | 2664269.5551 | 1213844.763 | 2664273.0435 | 1213842.4658 | 2664296.4867 | 1213859.8403
27 | 2664264.7556 | 1213846.0676 | 2664247.4842 | 1213841.0007 | 2664244.2955 | 1213840.8551 | 2664235.0739 | 1213850.7508
28 | 2664264.7556 | 1213846.0676 | 2664266.1742 | 1213851.8754 | 2664268.1947 | 1213853.9274
29 | 2664236.8682 | 1213898.5219 | 2664237.9303 | 1213901.6857
30 | 2664236.8682 | 1213898.5219 | 2664223.3118 | 1213872.2777
31 | 2664220.9231 | 1213867.6533 | 2664223.3118 | 1213872.2777
32 | 2664285.9145 | 1213811.8411 | 2664278.5024 | 1213820.1553 | 2664268.9383 | 1213832.9058
33 | 2664235.0739 | 1213850.7508 | 2664246.7831 | 1213863.0623
34 | 2664235.0739 | 1213850.7508 | 2664220.9231 | 1213867.6533
35 | 2664098.9476 | 1213895.4141 | 2664125.5824 | 1213936.3332
36 | 2664122.1926 | 1213874.2665 | 2664144.7937 | 1213897.7083 | 2664145.8105 | 1213898.9194
37 | 2664186.1515 | 1213824.4413 | 2664194.7499 | 1213832.2053 | 2664201.6126 | 1213841.1494
38 | 2664186.1515 | 1213824.4413 | 2664196.7468 | 1213809.0013
39 | 2664201.6126 | 1213841.1494 | 2664204.6086 | 1213845.054
40 | 2664196.7468 | 1213809.0013 | 2664196.7468 | 1213809.0013 | 2664188.899 | 1213802.7686 | 2664190.9746 | 1213797.6544 | 2664201.4236 | 1213793.6977 | 2664206.8441 | 1213792.9483
41 | 2664216.1433 | 1213771.9427 | 2664216.8282 | 1213788.0378 | 2664216.0761 | 1213789.4639 | 2664213.3963 | 1213791.4363 | 2664210.3012 | 1213792.4703 | 2664206.8441 | 1213792.9483
42 | 2664220.9231 | 1213867.6533 | 2664210.9298 | 1213853.2924
43 | 2664227.4348 | 1213832.9736 | 2664241.0631 | 1213816.1961
44 | 2664210.9298 | 1213853.2924 | 2664227.4348 | 1213832.9736
45 | 2664125.5824 | 1213936.3332 | 2664129.5585 | 1213942.4417
46 | 2664161.1902 | 1213924.9164 | 2664148.7685 | 1213902.4429 | 2664145.8105 | 1213898.9194
47 | 2664210.9298 | 1213853.2924 | 2664204.6086 | 1213845.054
48 | 2664161.1902 | 1213924.9164 | 2664164.7427 | 1213931.3437 | 2664171.0399 | 1213944.0083
49 | 2664141.8149 | 1213961.2713 | 2664129.5585 | 1213942.4417

## bus_geodata
| x | y | coords
0 | 2664206.416 | 1213768.728
1 | 2664242.6481 | 1213762.5334
2 | 2664146.7384 | 1213772.7409
3 | 2664246.082 | 1213767.4179
4 | 2664242.9488 | 1213747.3161
5 | 2664070.5656 | 1213811.0015
6 | 2664267.8777 | 1213790.3891
7 | 2664233.6727 | 1213770.1814
8 | 2664246.7741 | 1213744.778
9 | 2664305.0439 | 1213779.872
10 | 2664294.5673 | 1213787.7862
11 | 2664296.4651 | 1213773.1087
12 | 2664346.2842 | 1213684.669
13 | 2664303.9336 | 1213794.7803
14 | 2664258.1334 | 1213761.3773
15 | 2664234.0736 | 1213726.4521
16 | 2664238.2532 | 1213712.8887
17 | 2664242.6505 | 1213712.9233
18 | 2664226.9845 | 1213683.6382
19 | 2664298.8586 | 1213646.2672
20 | 2664342.4919 | 1213679.2136
21 | 2664296.4867 | 1213859.8403
22 | 2664299.9628 | 1213855.1749
23 | 2664264.7556 | 1213846.0676
24 | 2664236.8682 | 1213898.5219
25 | 2664237.9303 | 1213901.6857
26 | 2664223.3118 | 1213872.2777
27 | 2664285.9145 | 1213811.8411
28 | 2664268.9383 | 1213832.9058
29 | 2664286.6818 | 1213638.5423
30 | 2664235.0739 | 1213850.7508
31 | 2664268.1947 | 1213853.9274
32 | 2664098.9476 | 1213895.4141
33 | 2664122.1926 | 1213874.2665
34 | 2664186.1515 | 1213824.4413
35 | 2664201.6126 | 1213841.1494
36 | 2664196.7468 | 1213809.0013
37 | 2664216.1433 | 1213771.9427
38 | 2664206.8441 | 1213792.9483
39 | 2664220.9231 | 1213867.6533
40 | 2664241.0631 | 1213816.1961
41 | 2664227.4348 | 1213832.9736
42 | 2664246.7831 | 1213863.0623
43 | 2664125.5824 | 1213936.3332
44 | 2664145.8105 | 1213898.9194
45 | 2664204.6086 | 1213845.054
46 | 2664171.0399 | 1213944.0083
47 | 2664161.1902 | 1213924.9164
48 | 2664141.8149 | 1213961.2713
49 | 2664129.5585 | 1213942.4417
50 | 2664210.9298 | 1213853.2924
51 | 2664242.6481 | 1213762.5334

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99736 | -0.050662 | 0.037572 | 0.0094163
1 | 0.99946 | -0.010279 | 0 | 0
2 | 0.99601 | -0.076516 | 0 | 0
3 | 1 | 0 | -0.51313 | -0.12962
4 | 0.99812 | -0.03578 | 0 | 0
5 | 0.99383 | -0.11848 | 0 | 0
6 | 0.99966 | -0.0064454 | 0 | 0
7 | 0.99884 | -0.02221 | 0.079537 | 0.019934
8 | 0.99763 | -0.045171 | 0.046341 | 0.011614
9 | 0.98712 | -0.24744 | 0 | 0
10 | 0.9883 | -0.22451 | 0 | 0
11 | 0.98633 | -0.2628 | 0.078663 | 0.019715
12 | 0.98433 | -0.30185 | 0 | 0
13 | 0.988 | -0.23032 | 0.027897 | 0.0069915
14 | 0.99531 | -0.089554 | 0 | 0
15 | 0.99638 | -0.069397 | 0 | 0
16 | 0.99604 | -0.075806 | 0 | 0
17 | 0.99572 | -0.082032 | 0.042893 | 0.01075
18 | 0.99537 | -0.088836 | 0.019122 | 0.0047925
19 | 0.98353 | -0.31736 | 0 | 0
20 | 0.98426 | -0.30318 | 0.011074 | 0.0027754
21 | 0.98371 | -0.31382 | 0 | 0
22 | 0.98364 | -0.31518 | 0.013021 | 0.0032634
23 | 0.98417 | -0.30483 | 0 | 0
24 | 0.98543 | -0.2802 | 0 | 0
25 | 0.98542 | -0.28052 | 0.0053666 | 0.001345
26 | 0.98558 | -0.27735 | 0.0080751 | 0.0020238
27 | 0.99938 | -0.012002 | 0 | 0
28 | 0.9991 | -0.017375 | 0.011368 | 0.0028491
29 | 0.98343 | -0.31948 | 0.0081684 | 0.0020472
30 | 0.98494 | -0.2899 | 0 | 0
31 | 0.98408 | -0.30658 | 0.010947 | 0.0027435
32 | 0.99318 | -0.13111 | 0 | 0
33 | 0.99255 | -0.14339 | 0.0040173 | 0.0010068
34 | 0.98935 | -0.20416 | 0 | 0
35 | 0.98751 | -0.23982 | 0.0066417 | 0.0016646
36 | 0.99086 | -0.17505 | 0.012096 | 0.0030315
37 | 0.99688 | -0.059402 | 0 | 0
38 | 0.9938 | -0.11835 | 0.020971 | 0.0052559
39 | 0.98564 | -0.2761 | 0 | 0
40 | 0.9855 | -0.27887 | 0.013515 | 0.0033872
41 | 0.98577 | -0.27363 | 0.013513 | 0.0033867
42 | 0.98477 | -0.29324 | 0.010942 | 0.0027422
43 | 0.99285 | -0.13748 | 0.0020054 | 0.0005026
44 | 0.99213 | -0.15139 | 0.0049052 | 0.0012293
45 | 0.98714 | -0.24693 | 0.0054102 | 0.0013559
46 | 0.99187 | -0.15645 | 0.0015722 | 0.00039402
47 | 0.9919 | -0.15585 | 0.0067537 | 0.0016926
48 | 0.99275 | -0.13951 | 0.00338 | 0.00084711
49 | 0.99282 | -0.13817 | 0.0019866 | 0.0004979
50 | 0.98642 | -0.26094 | 0 | 0
51 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.062306 | -0.015654 | 0.062427 | 0.01573 | 0.00012034 | 7.6534e-05 | 0.092972 | 0.092972 | 0.092972 | 0.99736 | -0.050662 | 0.99946 | -0.010279 | 25.5417
1 | 0.024735 | 0.0062372 | -0.024704 | -0.0062184 | 3.0568e-05 | 1.8784e-05 | 0.036917 | 0.036917 | 0.036917 | 0.99736 | -0.050662 | 0.99601 | -0.076516 | 10.142
2 | -0.29842 | -0.07558 | 0.29856 | 0.075674 | 0.00014739 | 9.4094e-05 | 0.44457 | 0.44457 | 0.44457 | 0.99946 | -0.010279 | 1 | 0 | 40.7111
3 | 0.23599 | 0.05985 | -0.2357 | -0.059666 | 0.00028894 | 0.00018419 | 0.35159 | 0.35159 | 0.35159 | 0.99946 | -0.010279 | 0.99812 | -0.03578 | 32.1973
4 | 0.024704 | 0.0062184 | -0.024655 | -0.006188 | 4.9452e-05 | 3.0393e-05 | 0.036917 | 0.036917 | 0.036917 | 0.99601 | -0.076516 | 0.99383 | -0.11848 | 10.1421
5 | 0.011377 | 0.002854 | -0.011374 | -0.0028521 | 3.4948e-06 | 1.8103e-06 | 0.016931 | 0.016931 | 0.016931 | 1 | 0 | 0.99966 | -0.0064454 | 4.6513
6 | 0.20154 | 0.051092 | -0.20133 | -0.050954 | 0.00021488 | 0.00013719 | 0.3001 | 0.3001 | 0.3001 | 1 | 0 | 0.99884 | -0.02221 | 41.2225
7 | 0.2357 | 0.059666 | -0.23559 | -0.059598 | 0.0001062 | 6.7851e-05 | 0.35159 | 0.35159 | 0.35159 | 0.99812 | -0.03578 | 0.99763 | -0.045171 | 48.2959
8 | 0.0073791 | 0.0018499 | -0.0073747 | -0.0018483 | 4.4378e-06 | 1.5848e-06 | 0.011049 | 0.011049 | 0.011049 | 0.99383 | -0.11848 | 0.99318 | -0.13111 | 3.0354
9 | 0.017276 | 0.0043382 | -0.017255 | -0.0043261 | 2.0504e-05 | 1.2065e-05 | 0.025869 | 0.025869 | 0.025869 | 0.99383 | -0.11848 | 0.99255 | -0.14339 | 7.1069
10 | 0.011374 | 0.0028521 | -0.011371 | -0.0028506 | 3.0111e-06 | 1.56e-06 | 0.016931 | 0.016931 | 0.016931 | 0.99966 | -0.0064454 | 0.99938 | -0.012002 | 4.6513
11 | 0.12179 | 0.03102 | -0.12157 | -0.030881 | 0.00021807 | 0.00013933 | 0.18161 | 0.18161 | 0.18161 | 0.99884 | -0.02221 | 0.99688 | -0.059402 | 49.8928
12 | 0.12712 | 0.032368 | -0.12685 | -0.032195 | 0.00027146 | 0.00017347 | 0.18979 | 0.18979 | 0.18979 | 0.99763 | -0.045171 | 0.99531 | -0.089554 | 52.1396
13 | 0.062131 | 0.015615 | -0.062059 | -0.015569 | 7.1769e-05 | 4.5642e-05 | 0.092686 | 0.092686 | 0.092686 | 0.99763 | -0.045171 | 0.99638 | -0.069397 | 25.4633
14 | -0.098021 | -0.024607 | 0.098128 | 0.024676 | 0.00010733 | 6.8525e-05 | 0.14777 | 0.14777 | 0.14777 | 0.98712 | -0.24744 | 0.9883 | -0.22451 | 40.5972
15 | 0.078721 | 0.019752 | -0.078663 | -0.019715 | 5.7592e-05 | 3.672e-05 | 0.11867 | 0.11867 | 0.11867 | 0.98712 | -0.24744 | 0.98633 | -0.2628 | 32.6027
16 | 0.0193 | 0.0048559 | -0.01925 | -0.0048259 | 5.0045e-05 | 3.002e-05 | 0.0291 | 0.029101 | 0.029101 | 0.98712 | -0.24744 | 0.98433 | -0.30185 | 7.9948
17 | 0.027904 | 0.0069963 | -0.027897 | -0.0069915 | 7.7237e-06 | 4.7937e-06 | 0.042014 | 0.042015 | 0.042015 | 0.9883 | -0.22451 | 0.988 | -0.23032 | 11.5424
18 | -0.12603 | -0.031672 | 0.12685 | 0.032195 | 0.00081772 | 0.00052256 | 0.18979 | 0.18979 | 0.18979 | 0.9883 | -0.22451 | 0.99531 | -0.089554 | 52.1396
19 | 0.0081753 | 0.0020501 | -0.0081692 | -0.0020475 | 6.0383e-06 | 2.5256e-06 | 0.012359 | 0.01236 | 0.01236 | 0.98433 | -0.30185 | 0.98353 | -0.31736 | 3.3955
20 | 0.011075 | 0.0027758 | -0.011074 | -0.0027754 | 6.9772e-07 | 3.6217e-07 | 0.016742 | 0.016742 | 0.016742 | 0.98433 | -0.30185 | 0.98426 | -0.30318 | 4.5995
21 | 0.01914 | 0.0048031 | -0.019134 | -0.0047996 | 5.8474e-06 | 3.4939e-06 | 0.028586 | 0.028586 | 0.028586 | 0.99638 | -0.069397 | 0.99604 | -0.075806 | 7.8534
22 | 0.042919 | 0.010766 | -0.042893 | -0.01075 | 2.5835e-05 | 1.6316e-05 | 0.0641 | 0.0641 | 0.0641 | 0.99638 | -0.069397 | 0.99572 | -0.082032 | 17.61
23 | 0.019134 | 0.0047996 | -0.019122 | -0.0047925 | 1.1878e-05 | 7.0978e-06 | 0.028586 | 0.028587 | 0.028587 | 0.99604 | -0.075806 | 0.99537 | -0.088836 | 7.8534
24 | 0.0081692 | 0.0020475 | -0.0081684 | -0.0020472 | 8.2438e-07 | 3.4499e-07 | 0.01236 | 0.01236 | 0.01236 | 0.98353 | -0.31736 | 0.98343 | -0.31948 | 3.3955
25 | 0.013022 | 0.0032638 | -0.013021 | -0.0032634 | 8.4579e-07 | 4.6751e-07 | 0.019698 | 0.019698 | 0.019698 | 0.98371 | -0.31382 | 0.98364 | -0.31518 | 5.4115
26 | -0.013022 | -0.0032638 | 0.013027 | 0.0032669 | 5.577e-06 | 3.0824e-06 | 0.019698 | 0.019698 | 0.019698 | 0.98371 | -0.31382 | 0.98417 | -0.30483 | 5.4115
27 | -0.023975 | -0.0060109 | 0.023992 | 0.0060214 | 1.7071e-05 | 1.0485e-05 | 0.03625 | 0.03625 | 0.03625 | 0.98417 | -0.30483 | 0.98494 | -0.2899 | 9.9588
28 | 0.010948 | 0.002744 | -0.010947 | -0.0027435 | 9.1013e-07 | 4.6993e-07 | 0.016552 | 0.016552 | 0.016552 | 0.98417 | -0.30483 | 0.98408 | -0.30658 | 4.5474
29 | 0.0053666 | 0.001345 | -0.0053666 | -0.001345 | 8.2186e-08 | 1.0083e-08 | 0.0081037 | 0.0081037 | 0.0081037 | 0.98543 | -0.2802 | 0.98542 | -0.28052 | 2.2263
30 | -0.0053666 | -0.001345 | 0.0053674 | 0.0013451 | 7.2741e-07 | 8.9169e-08 | 0.0081037 | 0.0081036 | 0.0081037 | 0.98543 | -0.2802 | 0.98558 | -0.27735 | 2.2263
31 | -0.013442 | -0.0033689 | 0.013443 | 0.0033693 | 8.0396e-07 | 4.482e-07 | 0.020295 | 0.020295 | 0.020295 | 0.98558 | -0.27735 | 0.98564 | -0.2761 | 5.5756
32 | 0.011371 | 0.0028506 | -0.011368 | -0.0028491 | 2.9107e-06 | 1.5082e-06 | 0.016931 | 0.016931 | 0.016931 | 0.99938 | -0.012002 | 0.9991 | -0.017375 | 4.6514
33 | 0.010943 | 0.0027431 | -0.010942 | -0.0027422 | 1.7393e-06 | 8.9724e-07 | 0.016533 | 0.016533 | 0.016533 | 0.98494 | -0.2899 | 0.98477 | -0.29324 | 4.5421
34 | -0.034936 | -0.0087645 | 0.034959 | 0.008779 | 2.3007e-05 | 1.4444e-05 | 0.052783 | 0.052783 | 0.052783 | 0.98494 | -0.2899 | 0.98564 | -0.2761 | 14.5008
35 | 0.0073747 | 0.0018483 | -0.0073724 | -0.0018475 | 2.2352e-06 | 7.989e-07 | 0.011049 | 0.011049 | 0.011049 | 0.99318 | -0.13111 | 0.99285 | -0.13748 | 3.0355
36 | 0.013238 | 0.0033193 | -0.013233 | -0.0033165 | 5.0434e-06 | 2.7866e-06 | 0.019847 | 0.019847 | 0.019847 | 0.99255 | -0.14339 | 0.99213 | -0.15139 | 5.4524
37 | 0.087764 | 0.022122 | -0.087615 | -0.022027 | 0.00014946 | 9.5362e-05 | 0.13205 | 0.13205 | 0.13205 | 0.98935 | -0.20416 | 0.98751 | -0.23982 | 36.2762
38 | -0.087764 | -0.022122 | 0.087887 | 0.0222 | 0.00012244 | 7.812e-05 | 0.13205 | 0.13205 | 0.13205 | 0.98935 | -0.20416 | 0.99086 | -0.17505 | 36.2762
39 | 0.080973 | 0.020362 | -0.080945 | -0.020345 | 2.7486e-05 | 1.7528e-05 | 0.12204 | 0.12204 | 0.12204 | 0.98751 | -0.23982 | 0.98714 | -0.24693 | 33.5268
40 | -0.099982 | -0.025232 | 0.10025 | 0.025405 | 0.00027233 | 0.00017388 | 0.15021 | 0.15021 | 0.15021 | 0.99086 | -0.17505 | 0.9938 | -0.11835 | 41.2664
41 | 0.12157 | 0.030881 | -0.12123 | -0.030661 | 0.00034387 | 0.00021972 | 0.18161 | 0.18161 | 0.18161 | 0.99688 | -0.059402 | 0.9938 | -0.11835 | 49.8929
42 | -0.048402 | -0.012148 | 0.048437 | 0.01217 | 3.5008e-05 | 2.2182e-05 | 0.073078 | 0.073078 | 0.073078 | 0.98564 | -0.2761 | 0.98642 | -0.26094 | 20.0764
43 | -0.013515 | -0.0033872 | 0.013519 | 0.0033891 | 3.3755e-06 | 1.8848e-06 | 0.020407 | 0.020407 | 0.020407 | 0.9855 | -0.27887 | 0.98577 | -0.27363 | 5.6062
44 | -0.027032 | -0.0067758 | 0.027048 | 0.0067859 | 1.6345e-05 | 1.0127e-05 | 0.040804 | 0.040804 | 0.040804 | 0.98577 | -0.27363 | 0.98642 | -0.26094 | 11.21
45 | 0.005367 | 0.0013449 | -0.0053668 | -0.0013449 | 1.7684e-07 | 1.8922e-08 | 0.0080436 | 0.0080437 | 0.0080437 | 0.99285 | -0.13748 | 0.99282 | -0.13817 | 2.2098
46 | 0.0083276 | 0.0020871 | -0.0083259 | -0.0020864 | 1.7713e-06 | 7.4271e-07 | 0.01249 | 0.01249 | 0.01249 | 0.99213 | -0.15139 | 0.9919 | -0.15585 | 3.4313
47 | 0.075535 | 0.018989 | -0.075485 | -0.018956 | 5.0502e-05 | 3.2189e-05 | 0.11388 | 0.11388 | 0.11388 | 0.98714 | -0.24693 | 0.98642 | -0.26094 | 31.2863
48 | -0.0015722 | -0.00039402 | 0.0015722 | 0.00039377 | 4.4823e-08 | -2.4866e-07 | 0.0023586 | 0.0023585 | 0.0023586 | 0.99187 | -0.15645 | 0.9919 | -0.15585 | 0.64796
49 | -0.00338 | -0.00084711 | 0.0033802 | 0.00084695 | 2.1624e-07 | -1.5212e-07 | 0.0050662 | 0.0050661 | 0.0050662 | 0.99275 | -0.13951 | 0.99282 | -0.13817 | 1.3918

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.51313 | 0.12962

## res_load
| p_mw | q_mvar
0 | 0.037572 | 0.0094163
1 | 0.079537 | 0.019934
2 | 0.046341 | 0.011614
3 | 0.078663 | 0.019715
4 | 0.027897 | 0.0069915
5 | 0.042893 | 0.01075
6 | 0.019122 | 0.0047925
7 | 0.011074 | 0.0027754
8 | 0.013021 | 0.0032634
9 | 0.0053666 | 0.001345
10 | 0.0080751 | 0.0020238
11 | 0.011368 | 0.0028491
12 | 0.0081684 | 0.0020472
13 | 0.010947 | 0.0027435
14 | 0.0040173 | 0.0010068
15 | 0.0066417 | 0.0016646
16 | 0.012096 | 0.0030315
17 | 0.020971 | 0.0052559
18 | 0.013515 | 0.0033872
19 | 0.013513 | 0.0033867
20 | 0.010942 | 0.0027422
21 | 0.0020054 | 0.0005026
22 | 0.0049052 | 0.0012293
23 | 0.0054102 | 0.0013559
24 | 0.0015722 | 0.00039402
25 | 0.0067537 | 0.0016926
26 | 0.00338 | 0.00084711
27 | 0.0019866 | 0.0004979

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1