## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1040-17_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1040-17_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1040-17_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1040-17_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1040-17_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1040-17_0_4_node_39 | 0.4 | n |  | TRUE
6 | bus_LV_1040-17_0_4_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1040-17_0_4_node_53 | 0.4 | n |  | TRUE
8 | bus_LV_1040-17_0_4_node_42 | 0.4 | n |  | TRUE
9 | bus_LV_1040-17_0_4_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_1040-17_0_4_node_11 | 0.4 | n |  | TRUE
11 | bus_LV_1040-17_0_4_node_52 | 0.4 | n |  | TRUE
12 | bus_LV_1040-17_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_1040-17_0_4_node_40 | 0.4 | n |  | TRUE
14 | bus_LV_1040-17_0_4_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_1040-17_0_4_node_78 | 0.4 | n |  | TRUE
16 | bus_LV_1040-17_0_4_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_1040-17_0_4_node_77 | 0.4 | n |  | TRUE
18 | bus_LV_1040-17_0_4_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_1040-17_0_4_node_38 | 0.4 | n |  | TRUE
20 | bus_LV_1040-17_0_4_node_51 | 0.4 | n |  | TRUE
21 | bus_LV_1040-17_0_4_node_41 | 0.4 | n |  | TRUE
22 | bus_LV_1040-17_0_4_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_1040-17_0_4_node_46 | 0.4 | n |  | TRUE
24 | bus_LV_1040-17_0_4_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_1040-17_0_4_node_14 | 0.4 | n |  | TRUE
26 | bus_LV_1040-17_0_4_node_45 | 0.4 | n |  | TRUE
27 | bus_LV_1040-17_0_4_node_99 | 0.4 | n |  | TRUE
28 | bus_LV_1040-17_0_4_node_122 | 0.4 | n |  | TRUE
29 | bus_LV_1040-17_0_4_node_15 | 0.4 | n |  | TRUE
30 | bus_LV_1040-17_0_4_node_128 | 0.4 | n |  | TRUE
31 | bus_LV_1040-17_0_4_node_131 | 0.4 | n |  | TRUE
32 | bus_LV_1040-17_0_4_node_129 | 0.4 | n |  | TRUE
33 | bus_LV_1040-17_0_4_node_18 | 0.4 | n |  | TRUE
34 | bus_LV_1040-17_0_4_node_20 | 0.4 | n |  | TRUE
35 | bus_LV_1040-17_0_4_node_101 | 0.4 | n |  | TRUE
36 | bus_LV_1040-17_0_4_node_139 | 0.4 | n |  | TRUE
37 | bus_LV_1040-17_0_4_node_21 | 0.4 | n |  | TRUE
38 | bus_LV_1040-17_0_4_node_135 | 0.4 | n |  | TRUE
39 | bus_LV_1040-17_0_4_node_133 | 0.4 | n |  | TRUE
40 | bus_LV_1040-17_0_4_node_23 | 0.4 | n |  | TRUE
41 | bus_LV_1040-17_0_4_node_100 | 0.4 | n |  | TRUE
42 | bus_LV_1040-17_0_4_node_98 | 0.4 | n |  | TRUE
43 | bus_LV_1040-17_0_4_node_27 | 0.4 | n |  | TRUE
44 | bus_LV_1040-17_0_4_node_44 | 0.4 | n |  | TRUE
45 | bus_LV_1040-17_0_4_node_130 | 0.4 | n |  | TRUE
46 | bus_LV_1040-17_0_4_node_28 | 0.4 | n |  | TRUE
47 | bus_LV_1040-17_0_4_node_37 | 0.4 | n |  | TRUE
48 | bus_LV_1040-17_0_4_node_118 | 0.4 | n |  | TRUE
49 | bus_LV_1040-17_0_4_node_30 | 0.4 | n |  | TRUE
50 | bus_LV_1040-17_0_4_node_36 | 0.4 | n |  | TRUE
51 | bus_LV_1040-17_0_4_node_87 | 0.4 | n |  | TRUE
52 | bus_LV_1040-17_0_4_node_31 | 0.4 | n |  | TRUE
53 | bus_LV_1040-17_0_4_node_136 | 0.4 | n |  | TRUE
54 | bus_LV_1040-17_0_4_node_134 | 0.4 | n |  | TRUE
55 | bus_LV_1040-17_0_4_node_33 | 0.4 | n |  | TRUE
56 | bus_LV_1040-17_0_4_node_35 | 0.4 | n |  | TRUE
57 | bus_LV_1040-17_0_4_node_145 | 0.4 | n |  | TRUE
58 | bus_LV_1040-17_0_4_node_34 | 0.4 | n |  | TRUE
59 | bus_LV_1040-17_0_4_node_81 | 0.4 | n |  | TRUE
60 | bus_LV_1040-17_0_4_node_63 | 0.4 | n |  | TRUE
61 | bus_LV_1040-17_0_4_node_80 | 0.4 | n |  | TRUE
62 | bus_LV_1040-17_0_4_node_66 | 0.4 | n |  | TRUE
63 | bus_LV_1040-17_0_4_node_65 | 0.4 | n |  | TRUE
64 | bus_LV_1040-17_0_4_node_70 | 0.4 | n |  | TRUE
65 | bus_LV_1040-17_0_4_node_67 | 0.4 | n |  | TRUE
66 | bus_LV_1040-17_0_4_node_144 | 0.4 | n |  | TRUE
67 | bus_LV_1040-17_0_4_node_43 | 0.4 | n |  | TRUE
68 | bus_LV_1040-17_0_4_node_75 | 0.4 | n |  | TRUE
69 | bus_LV_1040-17_0_4_node_47 | 0.4 | n |  | TRUE
70 | bus_LV_1040-17_0_4_node_109 | 0.4 | n |  | TRUE
71 | bus_LV_1040-17_0_4_node_121 | 0.4 | n |  | TRUE
72 | bus_LV_1040-17_0_4_node_127 | 0.4 | n |  | TRUE
73 | bus_LV_1040-17_0_4_node_92 | 0.4 | n |  | TRUE
74 | bus_LV_1040-17_0_4_node_114 | 0.4 | n |  | TRUE
75 | bus_LV_1040-17_0_4_node_112 | 0.4 | n |  | TRUE
76 | bus_LV_1040-17_0_4_node_97 | 0.4 | n |  | TRUE
77 | bus_LV_1040-17_0_4_node_91 | 0.4 | n |  | TRUE
78 | bus_LV_1040-17_0_4_node_96 | 0.4 | n |  | TRUE
79 | bus_LV_1040-17_0_4_node_138 | 0.4 | n |  | TRUE
80 | bus_LV_1040-17_0_4_node_132 | 0.4 | n |  | TRUE
81 | bus_LV_1040-17_0_4_node_50 | 0.4 | n |  | TRUE
82 | bus_LV_1040-17_0_4_node_49 | 0.4 | n |  | TRUE
83 | bus_LV_1040-17_0_4_node_85 | 0.4 | n |  | TRUE
84 | bus_LV_1040-17_0_4_node_137 | 0.4 | n |  | TRUE
85 | bus_LV_1040-17_0_4_node_64 | 0.4 | n |  | TRUE
86 | bus_LV_1040-17_0_4_node_73 | 0.4 | n |  | TRUE
87 | bus_LV_1040-17_0_4_node_68 | 0.4 | n |  | TRUE
88 | bus_LV_1040-17_0_4_node_48 | 0.4 | n |  | TRUE
89 | bus_LV_1040-17_0_4_node_54 | 0.4 | n |  | TRUE
90 | bus_LV_1040-17_0_4_node_55 | 0.4 | n |  | TRUE
91 | bus_LV_1040-17_0_4_node_56 | 0.4 | n |  | TRUE
92 | bus_LV_1040-17_0_4_node_57 | 0.4 | n |  | TRUE
93 | bus_LV_1040-17_0_4_node_76 | 0.4 | n |  | TRUE
94 | bus_LV_1040-17_0_4_node_79 | 0.4 | n |  | TRUE
95 | bus_LV_1040-17_0_4_node_104 | 0.4 | n |  | TRUE
96 | bus_LV_1040-17_0_4_node_58 | 0.4 | n |  | TRUE
97 | bus_LV_1040-17_0_4_node_59 | 0.4 | n |  | TRUE
98 | bus_LV_1040-17_0_4_node_60 | 0.4 | n |  | TRUE
99 | bus_LV_1040-17_0_4_node_61 | 0.4 | n |  | TRUE
100 | bus_LV_1040-17_0_4_node_62 | 0.4 | n |  | TRUE
101 | bus_LV_1040-17_0_4_node_84 | 0.4 | n |  | TRUE
102 | bus_LV_1040-17_0_4_node_94 | 0.4 | n |  | TRUE
103 | bus_LV_1040-17_0_4_node_82 | 0.4 | n |  | TRUE
104 | bus_LV_1040-17_0_4_node_146 | 0.4 | n |  | TRUE
105 | bus_LV_1040-17_0_4_node_83 | 0.4 | n |  | TRUE
106 | bus_LV_1040-17_0_4_node_93 | 0.4 | n |  | TRUE
107 | bus_LV_1040-17_0_4_node_86 | 0.4 | n |  | TRUE
108 | bus_LV_1040-17_0_4_node_72 | 0.4 | n |  | TRUE
109 | bus_LV_1040-17_0_4_node_74 | 0.4 | n |  | TRUE
110 | bus_LV_1040-17_0_4_node_69 | 0.4 | n |  | TRUE
111 | bus_LV_1040-17_0_4_node_71 | 0.4 | n |  | TRUE
112 | bus_LV_1040-17_0_4_node_90 | 0.4 | n |  | TRUE
113 | bus_LV_1040-17_0_4_node_143 | 0.4 | n |  | TRUE
114 | bus_LV_1040-17_0_4_node_88 | 0.4 | n |  | TRUE
115 | bus_LV_1040-17_0_4_node_141 | 0.4 | n |  | TRUE
116 | bus_LV_1040-17_0_4_node_115 | 0.4 | n |  | TRUE
117 | bus_LV_1040-17_0_4_node_106 | 0.4 | n |  | TRUE
118 | bus_LV_1040-17_0_4_node_102 | 0.4 | n |  | TRUE
119 | bus_LV_1040-17_0_4_node_142 | 0.4 | n |  | TRUE
120 | bus_LV_1040-17_0_4_node_95 | 0.4 | n |  | TRUE
121 | bus_LV_1040-17_0_4_node_116 | 0.4 | n |  | TRUE
122 | bus_LV_1040-17_0_4_node_113 | 0.4 | n |  | TRUE
123 | bus_LV_1040-17_0_4_node_103 | 0.4 | n |  | TRUE
124 | bus_LV_1040-17_0_4_node_105 | 0.4 | n |  | TRUE
125 | bus_LV_1040-17_0_4_node_119 | 0.4 | n |  | TRUE
126 | bus_LV_1040-17_0_4_node_110 | 0.4 | n |  | TRUE
127 | bus_LV_1040-17_0_4_node_120 | 0.4 | n |  | TRUE
128 | bus_LV_1040-17_0_4_node_111 | 0.4 | n |  | TRUE
129 | bus_LV_1040-17_0_4_node_108 | 0.4 | n |  | TRUE
130 | bus_LV_1040-17_0_4_node_107 | 0.4 | n |  | TRUE
131 | bus_LV_1040-17_0_4_node_125 | 0.4 | n |  | TRUE
132 | bus_LV_1040-17_0_4_node_126 | 0.4 | n |  | TRUE
133 | bus_LV_1040-17_0_4_node_117 | 0.4 | n |  | TRUE
134 | bus_LV_1040-17_0_4_node_123 | 0.4 | n |  | TRUE
135 | bus_LV_1040-17_0_4_node_124 | 0.4 | n |  | TRUE
136 | bus_LV_1040-17_0_4_node_140 | 0.4 | n |  | TRUE
137 | bus_MV_214_1_node_66 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1040-17_0_4_load_0 | 0 | 0.01468 | 0.0036791 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1040-17_0_4_load_3 | 3 | 0.0030187 | 0.00075656 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1040-17_0_4_load_39 | 5 | 0.0052867 | 0.001325 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1040-17_0_4_load_53 | 7 | 0.0033574 | 0.00084144 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1040-17_0_4_load_42 | 8 | 0.0022323 | 0.00055946 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1040-17_0_4_load_52 | 11 | 0.0063992 | 0.0016038 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1040-17_0_4_load_40 | 13 | 0.0026453 | 0.00066297 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1040-17_0_4_load_78 | 15 | 0.0026395 | 0.00066152 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1040-17_0_4_load_77 | 17 | 0.011175 | 0.0028007 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1040-17_0_4_load_51 | 20 | 0.010048 | 0.0025182 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1040-17_0_4_load_41 | 21 | 0.0035263 | 0.00088377 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1040-17_0_4_load_46 | 23 | 0.0039551 | 0.00099123 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1040-17_0_4_load_45 | 26 | 0.0073601 | 0.0018446 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1040-17_0_4_load_122 | 28 | 0.0025066 | 0.00062821 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1040-17_0_4_load_131 | 31 | 0.0024401 | 0.00061155 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1040-17_0_4_load_129 | 32 | 0.0036051 | 0.00090351 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1040-17_0_4_load_101 | 35 | 0.012794 | 0.0032064 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1040-17_0_4_load_139 | 36 | 0.001081 | 0.00027091 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1040-17_0_4_load_133 | 39 | 0.00088666 | 0.00022222 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1040-17_0_4_load_98 | 42 | 0.012868 | 0.0032249 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1040-17_0_4_load_130 | 45 | 0.0057455 | 0.0014399 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1040-17_0_4_load_118 | 48 | 0.00084713 | 0.00021231 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1040-17_0_4_load_87 | 51 | 0.010575 | 0.0026504 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1040-17_0_4_load_136 | 53 | 0.00088202 | 0.00022106 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1040-17_0_4_load_134 | 54 | 0.0010504 | 0.00026326 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1040-17_0_4_load_145 | 57 | 0.0013777 | 0.00034528 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1040-17_0_4_load_81 | 59 | 0.00054955 | 0.00013773 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1040-17_0_4_load_80 | 61 | 0.0024289 | 0.00060874 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1040-17_0_4_load_66 | 62 | 0.00068189 | 0.0001709 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1040-17_0_4_load_65 | 63 | 0.0006983 | 0.00017501 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1040-17_0_4_load_70 | 64 | 0.0066361 | 0.0016632 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1040-17_0_4_load_67 | 65 | 0.002381 | 0.00059672 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1040-17_0_4_load_144 | 66 | 0.012916 | 0.003237 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1040-17_0_4_load_43 | 67 | 0.0010482 | 0.0002627 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1040-17_0_4_load_47 | 69 | 0.0073991 | 0.0018544 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1040-17_0_4_load_109 | 70 | 0.0083366 | 0.0020894 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1040-17_0_4_load_121 | 71 | 0.0021377 | 0.00053577 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1040-17_0_4_load_127 | 72 | 0.0051574 | 0.0012926 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1040-17_0_4_load_112 | 75 | 0.0030251 | 0.00075816 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1040-17_0_4_load_96 | 78 | 0.0065382 | 0.0016386 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1040-17_0_4_load_132 | 80 | 0.001117 | 0.00027994 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1040-17_0_4_load_50 | 81 | 0.0081857 | 0.0020515 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1040-17_0_4_load_49 | 82 | 0.0018496 | 0.00046355 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1040-17_0_4_load_85 | 83 | 0.00074459 | 0.00018661 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1040-17_0_4_load_73 | 86 | 0.0017396 | 0.000436 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1040-17_0_4_load_68 | 87 | 0.0089368 | 0.0022398 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1040-17_0_4_load_48 | 88 | 0.0017279 | 0.00043306 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1040-17_0_4_load_54 | 89 | 0.0026152 | 0.00065544 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1040-17_0_4_load_55 | 90 | 0.0023507 | 0.00058915 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1040-17_0_4_load_56 | 91 | 0.0024759 | 0.00062052 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1040-17_0_4_load_76 | 93 | 0.0021443 | 0.0005374 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1040-17_0_4_load_79 | 94 | 0.0029392 | 0.00073664 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1040-17_0_4_load_58 | 96 | 0.0030393 | 0.00076173 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1040-17_0_4_load_59 | 97 | 0.004308 | 0.0010797 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1040-17_0_4_load_61 | 99 | 0.0032645 | 0.00081817 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1040-17_0_4_load_94 | 102 | 0.0013892 | 0.00034816 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1040-17_0_4_load_82 | 103 | 0.0031419 | 0.00078744 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1040-17_0_4_load_146 | 104 | 0.001142 | 0.00028621 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1040-17_0_4_load_86 | 107 | 0.00092674 | 0.00023226 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1040-17_0_4_load_72 | 108 | 0.0028705 | 0.00071943 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1040-17_0_4_load_69 | 110 | 0.0032695 | 0.00081941 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1040-17_0_4_load_71 | 111 | 0.0011761 | 0.00029477 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1040-17_0_4_load_143 | 113 | 0.0049679 | 0.0012451 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1040-17_0_4_load_88 | 114 | 0.0010243 | 0.00025673 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1040-17_0_4_load_115 | 116 | 0.0034689 | 0.00086938 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1040-17_0_4_load_106 | 117 | 0.0021247 | 0.0005325 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1040-17_0_4_load_102 | 118 | 0.0023384 | 0.00058605 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1040-17_0_4_load_142 | 119 | 0.0065075 | 0.0016309 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1040-17_0_4_load_95 | 120 | 0.0022935 | 0.00057482 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1040-17_0_4_load_116 | 121 | 0.0028529 | 0.00071501 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1040-17_0_4_load_113 | 122 | 0.0030608 | 0.00076712 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1040-17_0_4_load_103 | 123 | 0.0020913 | 0.00052412 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1040-17_0_4_load_105 | 124 | 0.001944 | 0.00048721 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1040-17_0_4_load_119 | 125 | 0.0023156 | 0.00058035 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1040-17_0_4_load_120 | 127 | 0.0021492 | 0.00053863 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1040-17_0_4_load_111 | 128 | 0.0022467 | 0.00056308 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1040-17_0_4_load_108 | 129 | 0.00082252 | 0.00020614 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1040-17_0_4_load_107 | 130 | 0.0079837 | 0.0020009 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1040-17_0_4_load_125 | 131 | 0.0017151 | 0.00042984 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1040-17_0_4_load_126 | 132 | 0.0023606 | 0.00059161 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1040-17_0_4_load_117 | 133 | 0.0025913 | 0.00064945 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1040-17_0_4_load_123 | 134 | 0.0021573 | 0.00054066 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1040-17_0_4_load_124 | 135 | 0.0020426 | 0.00051193 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1040-17_0_4_load_140 | 136 | 0.000833 | 0.00020877 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 118 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1040-17_0_4_line_0 |  | 0 | 1 | 0.045983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1040-17_0_4_line_1 |  | 0 | 2 | 0.029197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1040-17_0_4_line_2 |  | 1 | 3 | 0.011747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1040-17_0_4_line_3 |  | 1 | 4 | 0.011935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1040-17_0_4_line_4 |  | 2 | 5 | 0.024011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1040-17_0_4_line_5 |  | 2 | 6 | 0.027439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1040-17_0_4_line_6 |  | 4 | 7 | 0.0099196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1040-17_0_4_line_7 |  | 5 | 67 | 0.017614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1040-17_0_4_line_8 |  | 6 | 8 | 0.010364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1040-17_0_4_line_9 |  | 8 | 12 | 0.038353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1040-17_0_4_line_10 |  | 9 | 10 | 0.013825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1040-17_0_4_line_11 |  | 9 | 11 | 0.02351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1040-17_0_4_line_12 |  | 10 | 21 | 0.034867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1040-17_0_4_line_13 |  | 10 | 13 | 0.017515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1040-17_0_4_line_14 |  | 11 | 16 | 0.072224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1040-17_0_4_line_15 |  | 12 | 13 | 0.003684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1040-17_0_4_line_16 |  | 14 | 15 | 0.022154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_1040-17_0_4_line_17 |  | 14 | 16 | 0.012532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1040-17_0_4_line_18 |  | 14 | 17 | 0.019171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_1040-17_0_4_line_19 |  | 15 | 68 | 0.0098241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
20 | LV_1040-17_0_4_line_20 |  | 16 | 20 | 0.01916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1040-17_0_4_line_21 |  | 17 | 64 | 0.038456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_1040-17_0_4_line_22 |  | 18 | 19 | 0.035727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1040-17_0_4_line_23 |  | 18 | 20 | 0.016974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1040-17_0_4_line_24 |  | 19 | 66 | 0.071134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1040-17_0_4_line_25 |  | 22 | 23 | 0.02906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1040-17_0_4_line_26 |  | 22 | 24 | 0.016607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1040-17_0_4_line_27 |  | 22 | 25 | 0.036813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1040-17_0_4_line_28 |  | 22 | 26 | 0.024609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1040-17_0_4_line_29 |  | 23 | 69 | 0.015404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1040-17_0_4_line_30 |  | 24 | 30 | 0.044199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1040-17_0_4_line_31 |  | 24 | 32 | 0.018448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1040-17_0_4_line_32 |  | 25 | 27 | 0.023841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1040-17_0_4_line_33 |  | 25 | 28 | 0.012902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1040-17_0_4_line_34 |  | 27 | 70 | 0.018572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1040-17_0_4_line_35 |  | 28 | 71 | 0.0098637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1040-17_0_4_line_36 |  | 29 | 30 | 0.037189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1040-17_0_4_line_37 |  | 29 | 31 | 0.0098856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1040-17_0_4_line_38 |  | 30 | 72 | 0.013146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1040-17_0_4_line_39 |  | 33 | 34 | 0.014627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1040-17_0_4_line_40 |  | 33 | 35 | 0.010308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1040-17_0_4_line_41 |  | 34 | 36 | 0.026551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1040-17_0_4_line_42 |  | 35 | 41 | 0.019991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1040-17_0_4_line_43 |  | 36 | 38 | 0.028732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1040-17_0_4_line_44 |  | 37 | 38 | 0.025778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1040-17_0_4_line_45 |  | 37 | 39 | 0.017371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1040-17_0_4_line_46 |  | 38 | 79 | 0.038387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1040-17_0_4_line_47 |  | 39 | 80 | 0.018295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1040-17_0_4_line_48 |  | 40 | 41 | 0.009135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1040-17_0_4_line_49 |  | 40 | 42 | 0.040036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1040-17_0_4_line_50 |  | 43 | 44 | 0.025265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1040-17_0_4_line_51 |  | 43 | 45 | 0.014288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1040-17_0_4_line_52 |  | 44 | 82 | 0.03444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1040-17_0_4_line_53 |  | 44 | 67 | 0.030735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1040-17_0_4_line_54 |  | 46 | 47 | 0.048404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1040-17_0_4_line_55 |  | 46 | 48 | 0.017604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1040-17_0_4_line_56 |  | 47 | 51 | 0.01642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1040-17_0_4_line_57 |  | 49 | 50 | 0.042284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1040-17_0_4_line_58 |  | 49 | 51 | 0.021874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1040-17_0_4_line_59 |  | 50 | 64 | 0.032578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1040-17_0_4_line_60 |  | 50 | 65 | 0.01526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1040-17_0_4_line_61 |  | 52 | 53 | 0.024341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1040-17_0_4_line_62 |  | 52 | 54 | 0.020952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1040-17_0_4_line_63 |  | 53 | 84 | 0.0021048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1040-17_0_4_line_64 |  | 55 | 56 | 0.04215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1040-17_0_4_line_65 |  | 55 | 57 | 0.027026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1040-17_0_4_line_66 |  | 56 | 62 | 0.03666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1040-17_0_4_line_67 |  | 56 | 63 | 0.014816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1040-17_0_4_line_68 |  | 58 | 59 | 0.0052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1040-17_0_4_line_69 |  | 58 | 60 | 0.011118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1040-17_0_4_line_70 |  | 58 | 61 | 0.018225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1040-17_0_4_line_71 |  | 60 | 83 | 0.020376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1040-17_0_4_line_72 |  | 61 | 85 | 0.024079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1040-17_0_4_line_73 |  | 62 | 86 | 0.023338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1040-17_0_4_line_74 |  | 65 | 87 | 0.0025583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1040-17_0_4_line_75 |  | 68 | 94 | 0.0052076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1040-17_0_4_line_76 |  | 68 | 92 | 0.002043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
77 | LV_1040-17_0_4_line_77 |  | 69 | 88 | 0.0067748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1040-17_0_4_line_78 |  | 71 | 134 | 0.0093816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1040-17_0_4_line_79 |  | 73 | 74 | 0.024858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1040-17_0_4_line_80 |  | 73 | 75 | 0.012923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1040-17_0_4_line_81 |  | 74 | 121 | 0.023233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1040-17_0_4_line_82 |  | 74 | 116 | 0.010612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1040-17_0_4_line_83 |  | 75 | 122 | 0.020761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1040-17_0_4_line_84 |  | 76 | 77 | 0.013942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1040-17_0_4_line_85 |  | 76 | 78 | 0.035755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1040-17_0_4_line_86 |  | 77 | 119 | 0.022268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1040-17_0_4_line_87 |  | 79 | 136 | 0.0061018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1040-17_0_4_line_88 |  | 79 | 84 | 0.024614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1040-17_0_4_line_89 |  | 81 | 82 | 0.017269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1040-17_0_4_line_90 |  | 83 | 107 | 0.019706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1040-17_0_4_line_91 |  | 85 | 103 | 0.006102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1040-17_0_4_line_92 |  | 85 | 98 | 0.01267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1040-17_0_4_line_93 |  | 86 | 109 | 0.017465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1040-17_0_4_line_94 |  | 87 | 110 | 0.014744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1040-17_0_4_line_95 |  | 89 | 90 | 0.011933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1040-17_0_4_line_96 |  | 89 | 91 | 0.012476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1040-17_0_4_line_97 |  | 90 | 92 | 0.019751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1040-17_0_4_line_98 |  | 92 | 93 | 0.015729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
99 | LV_1040-17_0_4_line_99 |  | 93 | 95 | 0.010877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
100 | LV_1040-17_0_4_line_100 |  | 94 | 116 | 0.025563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1040-17_0_4_line_101 |  | 95 | 117 | 0.016884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1040-17_0_4_line_102 |  | 95 | 118 | 0.017122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
103 | LV_1040-17_0_4_line_103 |  | 96 | 97 | 0.011591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1040-17_0_4_line_104 |  | 96 | 98 | 0.023005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1040-17_0_4_line_105 |  | 97 | 99 | 0.0041002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1040-17_0_4_line_106 |  | 98 | 100 | 0.022442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1040-17_0_4_line_107 |  | 100 | 101 | 0.003753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1040-17_0_4_line_108 |  | 100 | 102 | 0.0082097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1040-17_0_4_line_109 |  | 101 | 104 | 0.008238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1040-17_0_4_line_110 |  | 101 | 105 | 0.006459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1040-17_0_4_line_111 |  | 102 | 106 | 0.020847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1040-17_0_4_line_112 |  | 105 | 108 | 0.012677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1040-17_0_4_line_113 |  | 106 | 120 | 0.007941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1040-17_0_4_line_114 |  | 106 | 112 | 0.029485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1040-17_0_4_line_115 |  | 108 | 111 | 0.0091822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1040-17_0_4_line_116 |  | 109 | 112 | 0.026537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1040-17_0_4_line_117 |  | 109 | 113 | 0.020615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1040-17_0_4_line_118 |  | 110 | 111 | 0.019283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1040-17_0_4_line_119 |  | 112 | 114 | 0.012774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1040-17_0_4_line_120 |  | 113 | 115 | 0.034761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_1040-17_0_4_line_121 |  | 115 | 119 | 0.033785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_1040-17_0_4_line_122 |  | 115 | 136 | 0.016138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_1040-17_0_4_line_123 |  | 117 | 126 | 0.010341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_1040-17_0_4_line_124 |  | 118 | 123 | 0.010042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_1040-17_0_4_line_125 |  | 121 | 133 | 0.014492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_1040-17_0_4_line_126 |  | 123 | 124 | 0.0097287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_1040-17_0_4_line_127 |  | 124 | 125 | 0.010197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_1040-17_0_4_line_128 |  | 125 | 127 | 0.0095777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_1040-17_0_4_line_129 |  | 126 | 128 | 0.01688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_1040-17_0_4_line_130 |  | 126 | 129 | 0.016994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_1040-17_0_4_line_131 |  | 128 | 131 | 0.0099352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_1040-17_0_4_line_132 |  | 129 | 130 | 0.022394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_1040-17_0_4_line_133 |  | 131 | 132 | 0.010126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_1040-17_0_4_line_134 |  | 132 | 135 | 0.010117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_1040-17_0_4_line_135 |  | 134 | 135 | 0.0091196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1040-17_0_4_trafo_102 | 0.63 MVA 20/0.4 kV | 137 | 118 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13
0 | 2663320.7806 | 1216441.4455 | 2663318.4455 | 1216454.6956 | 2663315.7217 | 1216468.8088 | 2663314.5986 | 1216470.1866 | 2663312.2611 | 1216470.8066 | 2663298.4542 | 1216468.7481
1 | 2663278.9191 | 1216481.8707 | 2663282.3238 | 1216470.8333 | 2663284.5082 | 1216468.1882 | 2663287.8521 | 1216467.1675 | 2663298.4542 | 1216468.7481
2 | 2663320.7806 | 1216441.4455 | 2663332.3354 | 1216443.5618
3 | 2663317.8139 | 1216433.3979 | 2663316.993 | 1216437.0581 | 2663321.4191 | 1216437.8056 | 2663320.7806 | 1216441.4455
4 | 2663278.9191 | 1216481.8707 | 2663301.8865 | 1216488.872
5 | 2663267.9297 | 1216502.9005 | 2663269.1257 | 1216498.9552 | 2663274.9762 | 1216480.6725 | 2663278.9191 | 1216481.8707
6 | 2663317.8139 | 1216433.3979 | 2663322.0395 | 1216434.4323 | 2663327.5359 | 1216435.3295
7 | 2663304.168 | 1216502.218 | 2663307.1475 | 1216490.4757 | 2663301.8865 | 1216488.872
8 | 2663267.9297 | 1216502.9005 | 2663264.9337 | 1216512.8217
9 | 2663253.4357 | 1216549.4089 | 2663260.1787 | 1216528.5675 | 2663264.9337 | 1216512.8217
10 | 2663238.8658 | 1216563.0184 | 2663242.4577 | 1216564.3796 | 2663247.4084 | 1216565.7663 | 2663252.0714 | 1216567.0721
11 | 2663238.8658 | 1216563.0184 | 2663233.4079 | 1216574.3676 | 2663227.9097 | 1216583.7991
12 | 2663252.0714 | 1216567.0721 | 2663268.7025 | 1216571.707 | 2663268.9164 | 1216575.1558 | 2663269.9835 | 1216575.4785 | 2663269.1333 | 1216588.4825
13 | 2663252.0714 | 1216567.0721 | 2663257.0177 | 1216550.2697
14 | 2663182.1556 | 1216639.209 | 2663191.1602 | 1216631.3106 | 2663201.265 | 1216620.6222 | 2663210.4606 | 1216609.7574 | 2663220.2145 | 1216596.3636 | 2663226.9663 | 1216585.4172 | 2663227.9097 | 1216583.7991
15 | 2663253.4357 | 1216549.4089 | 2663257.0177 | 1216550.2697
16 | 2663190.2078 | 1216648.8114 | 2663191.1516 | 1216650.0222 | 2663194.3805 | 1216653.3918 | 2663204.2563 | 1216661.4237 | 2663206.7153 | 1216663.5068
17 | 2663182.1556 | 1216639.209 | 2663182.8378 | 1216640.0279 | 2663185.3345 | 1216643.0006 | 2663185.7918 | 1216643.5502 | 2663186.5715 | 1216644.4813 | 2663189.1957 | 1216647.5999 | 2663190.2078 | 1216648.8114
18 | 2663190.2078 | 1216648.8114 | 2663174.943 | 1216658.5446 | 2663174.0504 | 1216659.1293
19 | 2663214.2113 | 1216669.8567 | 2663206.7153 | 1216663.5068
20 | 2663182.1556 | 1216639.209 | 2663171.7118 | 1216647.5146 | 2663166.9887 | 1216650.9092
21 | 2663174.0504 | 1216659.1293 | 2663158.5744 | 1216669.2667 | 2663148.8606 | 1216676.0347 | 2663142.6242 | 1216681.2284
22 | 2663124.6689 | 1216639.7671 | 2663142.7775 | 1216650.4099 | 2663152.5571 | 1216659.6415 | 2663153.2052 | 1216660.8157
23 | 2663153.2052 | 1216660.8157 | 2663166.9887 | 1216650.9092
24 | 2663173.3805 | 1216616.8688 | 2663156.2885 | 1216604.858 | 2663150.285 | 1216603.9606 | 2663147.417 | 1216605.9314 | 2663139.0828 | 1216619.3404 | 2663124.6689 | 1216639.7671
25 | 2663320.4295 | 1216609.524 | 2663322.9349 | 1216590.2387 | 2663313.9933 | 1216586.71
26 | 2663328.6027 | 1216616.2928 | 2663320.0867 | 1216617.492 | 2663319.9006 | 1216613.5654 | 2663320.4295 | 1216609.524
27 | 2663317.5255 | 1216636.3099 | 2663316.8527 | 1216624.6066 | 2663315.2345 | 1216621.1317 | 2663311.8575 | 1216617.4157 | 2663320.0867 | 1216617.492 | 2663319.9006 | 1216613.5654 | 2663320.4295 | 1216609.524
28 | 2663320.4295 | 1216609.524 | 2663324.8063 | 1216609.1814 | 2663332.8085 | 1216607.7544 | 2663344.5679 | 1216604.9472
29 | 2663313.9933 | 1216586.71 | 2663304.608 | 1216583.0062 | 2663299.4485 | 1216581.7345
30 | 2663329.304 | 1216658.8934 | 2663327.7713 | 1216653.0958 | 2663325.4216 | 1216637.0053 | 2663324.5425 | 1216626.1447 | 2663324.6752 | 1216622.9442 | 2663325.7022 | 1216619.8976 | 2663328.6027 | 1216616.2928
31 | 2663328.6027 | 1216616.2928 | 2663335.2941 | 1216615.3411 | 2663345.1272 | 1216613.0886 | 2663346.6552 | 1216612.6102
32 | 2663317.5255 | 1216636.3099 | 2663317.871 | 1216642.384 | 2663318.8086 | 1216648.4533 | 2663320.9628 | 1216658.6491 | 2663321.2846 | 1216659.7977
33 | 2663317.5255 | 1216636.3099 | 2663305.932 | 1216637.0428 | 2663305.1334 | 1216638.0504
34 | 2663321.2846 | 1216659.7977 | 2663312.9994 | 1216670.005 | 2663309.6477 | 1216674.2712
35 | 2663299.0069 | 1216645.7808 | 2663305.1334 | 1216638.0504
36 | 2663343.2425 | 1216693.2518 | 2663336.9209 | 1216680.8547 | 2663331.5744 | 1216667.434 | 2663329.304 | 1216658.8934
37 | 2663343.2425 | 1216693.2518 | 2663353.1224 | 1216693.5876
38 | 2663329.304 | 1216658.8934 | 2663342.4393 | 1216659.4288
39 | 2663351.8737 | 1216781.1871 | 2663347.9431 | 1216795.2763
40 | 2663351.8737 | 1216781.1871 | 2663354.6396 | 1216771.2574
41 | 2663347.9431 | 1216795.2763 | 2663343.4038 | 1216795.9174 | 2663337.3906 | 1216806.6602 | 2663333.0234 | 1216815.2718
42 | 2663360.0039 | 1216751.9997 | 2663354.6396 | 1216771.2574
43 | 2663320.0282 | 1216840.897 | 2663333.0234 | 1216815.2718
44 | 2663343.1291 | 1216852.4718 | 2663320.0282 | 1216840.897
45 | 2663343.1291 | 1216852.4718 | 2663336.6818 | 1216865.4892 | 2663335.3621 | 1216868.0094
46 | 2663289.6266 | 1216834.7816 | 2663316.182 | 1216848.4831 | 2663320.0282 | 1216840.897
47 | 2663326.8754 | 1216884.2163 | 2663335.3621 | 1216868.0094
48 | 2663360.0039 | 1216751.9997 | 2663360.581 | 1216749.849 | 2663360.5544 | 1216747.3471 | 2663359.6513 | 1216743.0349
49 | 2663359.6513 | 1216743.0349 | 2663352.9152 | 1216728.9323 | 2663341.5583 | 1216707.3282
50 | 2663328.4994 | 1216512.4272 | 2663353.552 | 1216516.2179
51 | 2663353.552 | 1216516.2179 | 2663355.8572 | 1216502.1172
52 | 2663328.4994 | 1216512.4272 | 2663324.1273 | 1216540.1869 | 2663328.7659 | 1216544.5055
53 | 2663328.4994 | 1216512.4272 | 2663328.96 | 1216506.9509 | 2663304.168 | 1216502.218 | 2663304.168 | 1216502.218
54 | 2663065.4364 | 1216791.657 | 2663066.0538 | 1216790.7073 | 2663067.7051 | 1216788.1899 | 2663069.1257 | 1216785.9591 | 2663070.191 | 1216784.2916 | 2663071.488 | 1216782.2596 | 2663073.3178 | 1216779.3771 | 2663073.9354 | 1216778.4164 | 2663072.4418 | 1216776.0658 | 2663071.7383 | 1216772.9564 | 2663071.9737 | 1216768.6451 | 2663075.2185 | 1216762.6313 | 2663076.3492 | 1216760.5308 | 2663087.473 | 1216767.564
55 | 2663065.4364 | 1216791.657 | 2663063.3294 | 1216791.3122 | 2663060.6626 | 1216791.5064 | 2663058.8148 | 1216792.4986 | 2663052.8039 | 1216801.3475
56 | 2663087.473 | 1216767.564 | 2663096.2464 | 1216753.6847
57 | 2663091.7953 | 1216735.79 | 2663097.1078 | 1216728.0859 | 2663111.4903 | 1216709.8823 | 2663118.3964 | 1216702.9733
58 | 2663091.7953 | 1216735.79 | 2663096.6544 | 1216740.0774 | 2663099.0136 | 1216743.1265 | 2663099.6747 | 1216745.9352 | 2663099.2713 | 1216748.8995 | 2663096.2464 | 1216753.6847
59 | 2663118.3964 | 1216702.9733 | 2663129.8644 | 1216691.8545 | 2663142.6242 | 1216681.2284
60 | 2663118.3964 | 1216702.9733 | 2663129.8966 | 1216713.0036
61 | 2663265.5928 | 1216877.453 | 2663276.6266 | 1216855.7566
62 | 2663265.5928 | 1216877.453 | 2663284.2064 | 1216887.0728
63 | 2663278.4914 | 1216856.7326 | 2663276.6266 | 1216855.7566
64 | 2663198.7838 | 1216861.0009 | 2663196.5366 | 1216865.2909 | 2663190.3995 | 1216877.0109 | 2663181.9506 | 1216871.1955 | 2663174.4645 | 1216865.5127 | 2663171.0013 | 1216862.7632
65 | 2663223.1963 | 1216872.7448 | 2663198.7838 | 1216861.0009
66 | 2663171.0013 | 1216862.7632 | 2663193.116 | 1216833.5246
67 | 2663171.0013 | 1216862.7632 | 2663159.409 | 1216853.5366
68 | 2663130.1399 | 1216808.4521 | 2663125.8514 | 1216805.4938
69 | 2663130.1399 | 1216808.4521 | 2663132.6196 | 1216810.1572 | 2663137.5016 | 1216803.6827
70 | 2663130.1399 | 1216808.4521 | 2663131.593 | 1216806.7331 | 2663141.2955 | 1216794.0436
71 | 2663137.5016 | 1216803.6827 | 2663154.1865 | 1216815.378
72 | 2663155.921 | 1216774.9154 | 2663141.2955 | 1216794.0436
73 | 2663193.116 | 1216833.5246 | 2663207.1943 | 1216814.9111
74 | 2663129.8966 | 1216713.0036 | 2663130.1392 | 1216713.2151 | 2663131.8249 | 1216714.6848
75 | 2663214.2113 | 1216669.8567 | 2663218.1864 | 1216673.221
76 | 2663214.2113 | 1216669.8567 | 2663215.4434 | 1216668.2243
77 | 2663292.8706 | 1216580.1132 | 2663292.8706 | 1216580.1132 | 2663299.4485 | 1216581.7345
78 | 2663299.0069 | 1216645.7808 | 2663293.1798 | 1216653.1333
79 | 2663265.0296 | 1216712.4111 | 2663245.9149 | 1216696.4539
80 | 2663265.0296 | 1216712.4111 | 2663257.2305 | 1216722.7154
81 | 2663245.9149 | 1216696.4539 | 2663231.5363 | 1216714.7026
82 | 2663245.9149 | 1216696.4539 | 2663237.7665 | 1216689.6557
83 | 2663257.2305 | 1216722.7154 | 2663244.7014 | 1216739.2692
84 | 2663295.9102 | 1216774.9888 | 2663308.6882 | 1216780.6502
85 | 2663308.6882 | 1216780.6502 | 2663312.2985 | 1216771.6941 | 2663310.7021 | 1216769.0311 | 2663304.4142 | 1216766.3293 | 2663303.0335 | 1216762.6568 | 2663306.0088 | 1216750.7976
86 | 2663295.9102 | 1216774.9888 | 2663288.3256 | 1216790.7292 | 2663285.7692 | 1216794.787
87 | 2663289.6266 | 1216834.7816 | 2663284.2051 | 1216831.9816
88 | 2663278.4914 | 1216856.7326 | 2663284.2761 | 1216845.3313 | 2663289.6266 | 1216834.7816
89 | 2663345.847 | 1216547.0453 | 2663328.7659 | 1216544.5055
90 | 2663154.6995 | 1216829.2807 | 2663161.2401 | 1216820.3222 | 2663154.1865 | 1216815.378
91 | 2663155.921 | 1216774.9154 | 2663150.732 | 1216771.6807
92 | 2663155.921 | 1216774.9154 | 2663158.1611 | 1216776.3067 | 2663164.2058 | 1216768.2991
93 | 2663219.201 | 1216802.8034 | 2663214.8063 | 1216804.847 | 2663207.1943 | 1216814.9111
94 | 2663142.9378 | 1216724.3743 | 2663141.0094 | 1216722.6917 | 2663131.8249 | 1216714.6848
95 | 2663234.5824 | 1216642.9738 | 2663227.3742 | 1216652.4837
96 | 2663234.5824 | 1216642.9738 | 2663242.1186 | 1216633.0311
97 | 2663215.4434 | 1216668.2243 | 2663227.3742 | 1216652.4837
98 | 2663215.4434 | 1216668.2243 | 2663228.1147 | 1216677.5425
99 | 2663237.7615 | 1216681.3803 | 2663233.2072 | 1216681.2875 | 2663228.1147 | 1216677.5425
100 | 2663237.7665 | 1216689.6557 | 2663226.4238 | 1216680.1926 | 2663218.1864 | 1216673.221
101 | 2663237.7615 | 1216681.3803 | 2663251.1464 | 1216691.6717
102 | 2663237.7615 | 1216681.3803 | 2663248.1474 | 1216667.7681
103 | 2663183.3849 | 1216781.0033 | 2663188.7003 | 1216784.5243 | 2663185.583 | 1216788.7051
104 | 2663164.2058 | 1216768.2991 | 2663183.3849 | 1216781.0033
105 | 2663183.1321 | 1216791.9921 | 2663185.583 | 1216788.7051
106 | 2663180.0378 | 1216753.024 | 2663178.1336 | 1216753.6042 | 2663175.8726 | 1216754.9032 | 2663171.9137 | 1216758.0855 | 2663164.2058 | 1216768.2991
107 | 2663180.0378 | 1216753.024 | 2663179.3404 | 1216749.3365
108 | 2663180.0378 | 1216753.024 | 2663182.7262 | 1216752.9413 | 2663187.7051 | 1216753.8057 | 2663188.1095 | 1216754.0385
109 | 2663179.3404 | 1216749.3365 | 2663178.9309 | 1216747.1419 | 2663173.6703 | 1216744.2177
110 | 2663173.5052 | 1216751.9096 | 2663175.9983 | 1216750.2017 | 2663179.3404 | 1216749.3365
111 | 2663205.9922 | 1216764.7508 | 2663194.1796 | 1216757.5322 | 2663188.1095 | 1216754.0385
112 | 2663173.5052 | 1216751.9096 | 2663164.1209 | 1216743.386
113 | 2663210.2768 | 1216758.0587 | 2663205.9922 | 1216764.7508
114 | 2663205.9922 | 1216764.7508 | 2663231.2091 | 1216780.15
115 | 2663164.1209 | 1216743.386 | 2663157.324 | 1216737.2124
116 | 2663219.201 | 1216802.8034 | 2663218.693 | 1216798.4509 | 2663231.2091 | 1216780.15
117 | 2663219.201 | 1216802.8034 | 2663224.707 | 1216804.7852 | 2663237.9636 | 1216811.2826
118 | 2663142.9378 | 1216724.3743 | 2663149.3294 | 1216729.951 | 2663157.324 | 1216737.2124
119 | 2663231.2091 | 1216780.15 | 2663239.992 | 1216770.8739
120 | 2663269.8667 | 1216824.5766 | 2663261.5038 | 1216822.8201 | 2663237.9636 | 1216811.2826
121 | 2663269.8667 | 1216824.5766 | 2663282.8428 | 1216799.432 | 2663285.7692 | 1216794.787
122 | 2663269.8667 | 1216824.5766 | 2663284.2051 | 1216831.9816
123 | 2663259.3445 | 1216697.9751 | 2663251.1464 | 1216691.6717
124 | 2663248.1474 | 1216667.7681 | 2663254.2386 | 1216659.7846
125 | 2663231.5363 | 1216714.7026 | 2663222.567 | 1216726.0861
126 | 2663254.2386 | 1216659.7846 | 2663260.1399 | 1216652.0501
127 | 2663266.3252 | 1216643.9434 | 2663260.1399 | 1216652.0501
128 | 2663266.3252 | 1216643.9434 | 2663272.1349 | 1216636.3289
129 | 2663259.3445 | 1216697.9751 | 2663269.589 | 1216684.5592
130 | 2663259.3445 | 1216697.9751 | 2663260.9635 | 1216699.2264 | 2663273.0512 | 1216708.0195
131 | 2663275.6097 | 1216676.6562 | 2663275.1433 | 1216677.2854 | 2663269.589 | 1216684.5592
132 | 2663288.4005 | 1216701.3156 | 2663279.4669 | 1216712.6867 | 2663273.0512 | 1216708.0195
133 | 2663275.6097 | 1216676.6562 | 2663281.6392 | 1216668.5214
134 | 2663287.6633 | 1216660.3939 | 2663281.6392 | 1216668.5214
135 | 2663287.6633 | 1216660.3939 | 2663291.0953 | 1216655.7636 | 2663293.1798 | 1216653.1333

## bus_geodata
| x | y | coords
0 | 2663298.4542 | 1216468.7481
1 | 2663320.7806 | 1216441.4455
2 | 2663278.9191 | 1216481.8707
3 | 2663332.3354 | 1216443.5618
4 | 2663317.8139 | 1216433.3979
5 | 2663301.8865 | 1216488.872
6 | 2663267.9297 | 1216502.9005
7 | 2663327.5359 | 1216435.3295
8 | 2663264.9337 | 1216512.8217
9 | 2663238.8658 | 1216563.0184
10 | 2663252.0714 | 1216567.0721
11 | 2663227.9097 | 1216583.799
12 | 2663253.4357 | 1216549.4089
13 | 2663257.0177 | 1216550.2697
14 | 2663190.2078 | 1216648.8114
15 | 2663206.7153 | 1216663.5068
16 | 2663182.1556 | 1216639.209
17 | 2663174.0504 | 1216659.1293
18 | 2663153.2052 | 1216660.8157
19 | 2663124.6689 | 1216639.7671
20 | 2663166.9887 | 1216650.9092
21 | 2663269.1333 | 1216588.4825
22 | 2663320.4295 | 1216609.524
23 | 2663313.9933 | 1216586.71
24 | 2663328.6027 | 1216616.2928
25 | 2663317.5255 | 1216636.3099
26 | 2663344.5679 | 1216604.9472
27 | 2663321.2846 | 1216659.7977
28 | 2663305.1334 | 1216638.0504
29 | 2663343.2425 | 1216693.2518
30 | 2663329.304 | 1216658.8934
31 | 2663353.1224 | 1216693.5876
32 | 2663346.6552 | 1216612.6102
33 | 2663351.8737 | 1216781.1871
34 | 2663347.9431 | 1216795.2763
35 | 2663354.6396 | 1216771.2574
36 | 2663333.0234 | 1216815.2718
37 | 2663343.1291 | 1216852.4718
38 | 2663320.0282 | 1216840.897
39 | 2663335.3621 | 1216868.0094
40 | 2663359.6513 | 1216743.0349
41 | 2663360.0039 | 1216751.9997
42 | 2663341.5583 | 1216707.3282
43 | 2663353.552 | 1216516.2179
44 | 2663328.4994 | 1216512.4272
45 | 2663355.8572 | 1216502.1172
46 | 2663065.4364 | 1216791.657
47 | 2663087.473 | 1216767.564
48 | 2663052.8039 | 1216801.3475
49 | 2663091.7953 | 1216735.79
50 | 2663118.3964 | 1216702.9733
51 | 2663096.2464 | 1216753.6847
52 | 2663265.5928 | 1216877.453
53 | 2663276.6266 | 1216855.7566
54 | 2663284.2064 | 1216887.0728
55 | 2663198.7838 | 1216861.0009
56 | 2663171.0013 | 1216862.7632
57 | 2663223.1963 | 1216872.7448
58 | 2663130.1399 | 1216808.4521
59 | 2663125.8514 | 1216805.4938
60 | 2663137.5016 | 1216803.6827
61 | 2663141.2955 | 1216794.0436
62 | 2663193.116 | 1216833.5246
63 | 2663159.409 | 1216853.5366
64 | 2663142.6242 | 1216681.2284
65 | 2663129.8966 | 1216713.0036
66 | 2663173.3805 | 1216616.8688
67 | 2663304.168 | 1216502.218
68 | 2663214.2113 | 1216669.8567
69 | 2663299.4485 | 1216581.7345
70 | 2663309.6477 | 1216674.2712
71 | 2663299.0069 | 1216645.7808
72 | 2663342.4393 | 1216659.4288
73 | 2663265.0296 | 1216712.4111
74 | 2663245.9149 | 1216696.4539
75 | 2663257.2305 | 1216722.7154
76 | 2663308.6882 | 1216780.6502
77 | 2663295.9102 | 1216774.9888
78 | 2663306.0088 | 1216750.7976
79 | 2663289.6266 | 1216834.7816
80 | 2663326.8754 | 1216884.2163
81 | 2663345.847 | 1216547.0453
82 | 2663328.7659 | 1216544.5055
83 | 2663154.1865 | 1216815.378
84 | 2663278.4914 | 1216856.7326
85 | 2663155.921 | 1216774.9154
86 | 2663207.1943 | 1216814.9111
87 | 2663131.8249 | 1216714.6848
88 | 2663292.8706 | 1216580.1132
89 | 2663234.5824 | 1216642.9738
90 | 2663227.3742 | 1216652.4837
91 | 2663242.1186 | 1216633.0311
92 | 2663215.4434 | 1216668.2243
93 | 2663228.1147 | 1216677.5425
94 | 2663218.1864 | 1216673.221
95 | 2663237.7615 | 1216681.3803
96 | 2663183.3849 | 1216781.0033
97 | 2663185.583 | 1216788.7051
98 | 2663164.2058 | 1216768.2991
99 | 2663183.1321 | 1216791.9921
100 | 2663180.0378 | 1216753.024
101 | 2663179.3404 | 1216749.3365
102 | 2663188.1095 | 1216754.0385
103 | 2663150.732 | 1216771.6807
104 | 2663173.6703 | 1216744.2177
105 | 2663173.5052 | 1216751.9096
106 | 2663205.9922 | 1216764.7508
107 | 2663154.6995 | 1216829.2807
108 | 2663164.1209 | 1216743.386
109 | 2663219.201 | 1216802.8034
110 | 2663142.9378 | 1216724.3743
111 | 2663157.324 | 1216737.2124
112 | 2663231.2091 | 1216780.15
113 | 2663237.9636 | 1216811.2826
114 | 2663239.992 | 1216770.8739
115 | 2663269.8667 | 1216824.5766
116 | 2663237.7665 | 1216689.6557
117 | 2663251.1464 | 1216691.6717
118 | 2663248.1474 | 1216667.7681
119 | 2663285.7692 | 1216794.787
120 | 2663210.2768 | 1216758.0587
121 | 2663231.5363 | 1216714.7026
122 | 2663244.7014 | 1216739.2692
123 | 2663254.2386 | 1216659.7846
124 | 2663260.1399 | 1216652.0501
125 | 2663266.3252 | 1216643.9434
126 | 2663259.3445 | 1216697.9751
127 | 2663272.1349 | 1216636.3289
128 | 2663269.589 | 1216684.5592
129 | 2663273.0512 | 1216708.0195
130 | 2663288.4005 | 1216701.3156
131 | 2663275.6097 | 1216676.6562
132 | 2663281.6392 | 1216668.5214
133 | 2663222.567 | 1216726.0861
134 | 2663293.1798 | 1216653.1333
135 | 2663287.6633 | 1216660.3939
136 | 2663284.2051 | 1216831.9816
137 | 2663237.7615 | 1216681.3803

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98311 | -0.32486 | 0.01468 | 0.0036791
1 | 0.98284 | -0.33015 | 0 | 0
2 | 0.98368 | -0.31378 | 0 | 0
3 | 0.98281 | -0.33079 | 0.0030187 | 0.00075656
4 | 0.9828 | -0.33088 | 0 | 0
5 | 0.98319 | -0.32335 | 0.0052867 | 0.001325
6 | 0.98477 | -0.29246 | 0 | 0
7 | 0.98277 | -0.33148 | 0.0033574 | 0.00084144
8 | 0.98518 | -0.28442 | 0.0022323 | 0.00055946
9 | 0.98838 | -0.22242 | 0 | 0
10 | 0.98772 | -0.23515 | 0 | 0
11 | 0.9895 | -0.2008 | 0.0063992 | 0.0016038
12 | 0.98679 | -0.25319 | 0 | 0
13 | 0.98694 | -0.2502 | 0.0026453 | 0.00066297
14 | 0.99429 | -0.10863 | 0 | 0
15 | 0.9957 | -0.081698 | 0.0026395 | 0.00066152
16 | 0.99336 | -0.12653 | 0 | 0
17 | 0.99354 | -0.12286 | 0.011175 | 0.0028007
18 | 0.99275 | -0.13819 | 0 | 0
19 | 0.99233 | -0.14635 | 0 | 0
20 | 0.99295 | -0.13431 | 0.010048 | 0.0025182
21 | 0.98761 | -0.23735 | 0.0035263 | 0.00088377
22 | 0.99184 | -0.15683 | 0 | 0
23 | 0.99149 | -0.16357 | 0.0039551 | 0.00099123
24 | 0.99167 | -0.16013 | 0 | 0
25 | 0.9929 | -0.1362 | 0 | 0
26 | 0.99167 | -0.16004 | 0.0073601 | 0.0018446
27 | 0.99272 | -0.13972 | 0 | 0
28 | 0.99337 | -0.12709 | 0.0025066 | 0.00062821
29 | 0.99128 | -0.16769 | 0 | 0
30 | 0.99136 | -0.16608 | 0 | 0
31 | 0.99125 | -0.16812 | 0.0024401 | 0.00061155
32 | 0.9916 | -0.1613 | 0.0036051 | 0.00090351
33 | 0.97212 | -0.53865 | 0 | 0
34 | 0.97247 | -0.53173 | 0 | 0
35 | 0.97187 | -0.54353 | 0.012794 | 0.0032064
36 | 0.97311 | -0.51918 | 0.001081 | 0.00027091
37 | 0.97378 | -0.50599 | 0 | 0
38 | 0.97382 | -0.50504 | 0 | 0
39 | 0.97374 | -0.50663 | 0.00088666 | 0.00022222
40 | 0.97152 | -0.55045 | 0 | 0
41 | 0.97163 | -0.54828 | 0 | 0
42 | 0.97104 | -0.55997 | 0.012868 | 0.0032249
43 | 0.98233 | -0.34008 | 0 | 0
44 | 0.98246 | -0.33746 | 0 | 0
45 | 0.98225 | -0.34156 | 0.0057455 | 0.0014399
46 | 0.98818 | -0.22569 | 0 | 0
47 | 0.98822 | -0.22496 | 0 | 0
48 | 0.98817 | -0.22596 | 0.00084713 | 0.00021231
49 | 0.98846 | -0.22025 | 0 | 0
50 | 0.98891 | -0.21164 | 0 | 0
51 | 0.98823 | -0.22471 | 0.010575 | 0.0026504
52 | 0.97478 | -0.4862 | 0 | 0
53 | 0.9748 | -0.48573 | 0.00088202 | 0.00022106
54 | 0.97476 | -0.4866 | 0.0010504 | 0.00026326
55 | 0.97764 | -0.43011 | 0 | 0
56 | 0.97769 | -0.42905 | 0 | 0
57 | 0.97761 | -0.43079 | 0.0013777 | 0.00034528
58 | 0.98169 | -0.35113 | 0 | 0
59 | 0.98169 | -0.35118 | 0.00054955 | 0.00013773
60 | 0.98168 | -0.35147 | 0 | 0
61 | 0.98173 | -0.3504 | 0.0024289 | 0.00060874
62 | 0.97776 | -0.42766 | 0.00068189 | 0.0001709
63 | 0.97768 | -0.42924 | 0.0006983 | 0.00017501
64 | 0.99218 | -0.14892 | 0.0066361 | 0.0016632
65 | 0.98753 | -0.23804 | 0.002381 | 0.00059672
66 | 0.99149 | -0.16263 | 0.012916 | 0.003237
67 | 0.98291 | -0.3287 | 0.0010482 | 0.0002627
68 | 0.99633 | -0.069628 | 0 | 0
69 | 0.99136 | -0.16606 | 0.0073991 | 0.0018544
70 | 0.99258 | -0.14246 | 0.0083366 | 0.0020894
71 | 0.99376 | -0.11969 | 0.0021377 | 0.00053577
72 | 0.9913 | -0.16728 | 0.0051574 | 0.0012926
73 | 0.99565 | -0.082817 | 0 | 0
74 | 0.99579 | -0.080157 | 0 | 0
75 | 0.99558 | -0.0842 | 0.0030251 | 0.00075816
76 | 0.97487 | -0.48444 | 0 | 0
77 | 0.97496 | -0.48277 | 0 | 0
78 | 0.97465 | -0.48873 | 0.0065382 | 0.0016386
79 | 0.97485 | -0.48478 | 0 | 0
80 | 0.97372 | -0.50701 | 0.001117 | 0.00027994
81 | 0.98201 | -0.34625 | 0.0081857 | 0.0020515
82 | 0.98215 | -0.3437 | 0.0018496 | 0.00046355
83 | 0.98165 | -0.35208 | 0.00074459 | 0.00018661
84 | 0.97481 | -0.48565 | 0 | 0
85 | 0.98183 | -0.34837 | 0 | 0
86 | 0.97782 | -0.42649 | 0.0017396 | 0.000436
87 | 0.98731 | -0.24236 | 0.0089368 | 0.0022398
88 | 0.99135 | -0.16627 | 0.0017279 | 0.00043306
89 | 0.99629 | -0.070553 | 0.0026152 | 0.00065544
90 | 0.99634 | -0.069486 | 0.0023507 | 0.00058915
91 | 0.99626 | -0.071095 | 0.0024759 | 0.00062052
92 | 0.99648 | -0.066905 | 0 | 0
93 | 0.99761 | -0.045287 | 0.0021443 | 0.0005374
94 | 0.99625 | -0.071268 | 0.0029392 | 0.00073664
95 | 0.99841 | -0.030231 | 0 | 0
96 | 0.9817 | -0.351 | 0.0030393 | 0.00076173
97 | 0.98162 | -0.35259 | 0.004308 | 0.0010797
98 | 0.98193 | -0.34659 | 0 | 0
99 | 0.98161 | -0.35283 | 0.0032645 | 0.00081817
100 | 0.98231 | -0.33912 | 0 | 0
101 | 0.98258 | -0.33389 | 0 | 0
102 | 0.98186 | -0.34784 | 0.0013892 | 0.00034816
103 | 0.98182 | -0.34872 | 0.0031419 | 0.00078744
104 | 0.98257 | -0.33406 | 0.001142 | 0.00028621
105 | 0.98305 | -0.32477 | 0 | 0
106 | 0.98074 | -0.36948 | 0 | 0
107 | 0.98163 | -0.35241 | 0.00092674 | 0.00023226
108 | 0.98397 | -0.30688 | 0.0028705 | 0.00071943
109 | 0.9779 | -0.42506 | 0 | 0
110 | 0.98614 | -0.26496 | 0.0032695 | 0.00081941
111 | 0.98466 | -0.29347 | 0.0011761 | 0.00029477
112 | 0.97923 | -0.39895 | 0 | 0
113 | 0.97695 | -0.44369 | 0.0049679 | 0.0012451
114 | 0.97922 | -0.39919 | 0.0010243 | 0.00025673
115 | 0.9755 | -0.47202 | 0 | 0
116 | 0.9959 | -0.078006 | 0.0034689 | 0.00086938
117 | 0.99739 | -0.049762 | 0.0021247 | 0.0005325
118 | 1 | 0 | -0.31726 | -0.080535
119 | 0.97509 | -0.4801 | 0.0065075 | 0.0016309
120 | 0.98073 | -0.36981 | 0.0022935 | 0.00057482
121 | 0.99567 | -0.082381 | 0.0028529 | 0.00071501
122 | 0.99552 | -0.085318 | 0.0030608 | 0.00076712
123 | 0.99992 | -0.001488 | 0.0020913 | 0.00052412
124 | 0.99987 | -0.0025751 | 0.001944 | 0.00048721
125 | 0.99982 | -0.0033689 | 0.0023156 | 0.00058035
126 | 0.99678 | -0.06136 | 0 | 0
127 | 0.99981 | -0.0037279 | 0.0021492 | 0.00053863
128 | 0.99593 | -0.077707 | 0.0022467 | 0.00056308
129 | 0.99665 | -0.063986 | 0.00082252 | 0.00020614
130 | 0.99649 | -0.067123 | 0.0079837 | 0.0020009
131 | 0.99545 | -0.086949 | 0.0017151 | 0.00042984
132 | 0.99498 | -0.096072 | 0.0023606 | 0.00059161
133 | 0.99564 | -0.083041 | 0.0025913 | 0.00064945
134 | 0.99414 | -0.1123 | 0.0021573 | 0.00054066
135 | 0.99453 | -0.10477 | 0.0020426 | 0.00051193
136 | 0.97503 | -0.48135 | 0.000833 | 0.00020877
137 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.006378 | 0.0015982 | -0.0063764 | -0.0015978 | 1.607e-06 | 4.4558e-07 | 0.0096536 | 0.0096538 | 0.0096538 | 0.98311 | -0.32486 | 0.98284 | -0.33015 | 2.6521
1 | -0.021058 | -0.0052773 | 0.021069 | 0.005284 | 1.1122e-05 | 6.7478e-06 | 0.031872 | 0.031872 | 0.031872 | 0.98311 | -0.32486 | 0.98368 | -0.31378 | 8.7562
2 | 0.0030188 | 0.00075647 | -0.0030187 | -0.00075656 | 9.202e-08 | -8.9971e-08 | 0.0045704 | 0.0045705 | 0.0045705 | 0.98284 | -0.33015 | 0.98281 | -0.33079 | 1.2556
3 | 0.0033576 | 0.0008413 | -0.0033575 | -0.00084138 | 1.1566e-07 | -7.7229e-08 | 0.0050834 | 0.0050834 | 0.0050834 | 0.98284 | -0.33015 | 0.9828 | -0.33088 | 1.3965
4 | 0.022142 | 0.0055573 | -0.022132 | -0.0055512 | 1.0103e-05 | 6.1613e-06 | 0.033497 | 0.033497 | 0.033497 | 0.98368 | -0.31378 | 0.98319 | -0.32335 | 9.2025
5 | -0.043211 | -0.010841 | 0.043255 | 0.010869 | 4.397e-05 | 2.7792e-05 | 0.065369 | 0.065369 | 0.065369 | 0.98368 | -0.31378 | 0.98477 | -0.29246 | 17.9586
6 | 0.0033575 | 0.00084138 | -0.0033574 | -0.00084144 | 9.6125e-08 | -6.4176e-08 | 0.0050834 | 0.0050835 | 0.0050835 | 0.9828 | -0.33088 | 0.98277 | -0.33148 | 1.3966
7 | 0.016845 | 0.0042262 | -0.016841 | -0.0042237 | 4.2937e-06 | 2.5247e-06 | 0.025496 | 0.025496 | 0.025496 | 0.98319 | -0.32335 | 0.98291 | -0.3287 | 7.0044
8 | -0.043255 | -0.010869 | 0.043271 | 0.01088 | 1.6607e-05 | 1.0497e-05 | 0.065369 | 0.065369 | 0.065369 | 0.98477 | -0.29246 | 0.98518 | -0.28442 | 17.9585
9 | -0.045503 | -0.011439 | 0.045571 | 0.011482 | 6.7961e-05 | 4.3006e-05 | 0.068741 | 0.06874 | 0.068741 | 0.98518 | -0.28442 | 0.98679 | -0.25319 | 18.8848
10 | 0.051816 | 0.013075 | -0.051785 | -0.013055 | 3.1575e-05 | 2.0031e-05 | 0.078041 | 0.078042 | 0.078042 | 0.98838 | -0.22242 | 0.98772 | -0.23515 | 21.44
11 | -0.051816 | -0.013075 | 0.05187 | 0.013109 | 5.3696e-05 | 3.4064e-05 | 0.078041 | 0.078041 | 0.078041 | 0.98838 | -0.22242 | 0.9895 | -0.2008 | 21.44
12 | 0.0035267 | 0.00088356 | -0.0035263 | -0.00088377 | 3.6908e-07 | -2.1e-07 | 0.0053129 | 0.005313 | 0.005313 | 0.98772 | -0.23515 | 0.98761 | -0.23735 | 1.4596
13 | 0.048258 | 0.012171 | -0.048223 | -0.012149 | 3.4743e-05 | 2.2011e-05 | 0.072729 | 0.072729 | 0.072729 | 0.98772 | -0.23515 | 0.98694 | -0.2502 | 19.9804
14 | -0.058269 | -0.014713 | 0.058477 | 0.014845 | 0.00020814 | 0.00013228 | 0.087665 | 0.087664 | 0.087665 | 0.9895 | -0.2008 | 0.99336 | -0.12653 | 24.0837
15 | -0.045571 | -0.011482 | 0.045578 | 0.011486 | 6.528e-06 | 4.1308e-06 | 0.06874 | 0.06874 | 0.06874 | 0.98679 | -0.25319 | 0.98694 | -0.2502 | 18.8848
16 | -0.20924 | -0.053254 | 0.20951 | 0.053427 | 0.00027205 | 0.00017325 | 0.31343 | 0.31343 | 0.31343 | 0.99429 | -0.10863 | 0.9957 | -0.081698 | 28.7022
17 | 0.081537 | 0.02066 | -0.081467 | -0.020615 | 7.0066e-05 | 4.468e-05 | 0.1221 | 0.1221 | 0.1221 | 0.99429 | -0.10863 | 0.99336 | -0.12653 | 33.5452
18 | 0.1277 | 0.032594 | -0.12761 | -0.032539 | 8.7718e-05 | 5.5394e-05 | 0.19132 | 0.19132 | 0.19132 | 0.99429 | -0.10863 | 0.99354 | -0.12286 | 17.5205
19 | -0.21215 | -0.054089 | 0.21227 | 0.054168 | 0.00012369 | 7.8779e-05 | 0.31737 | 0.31737 | 0.31737 | 0.9957 | -0.081698 | 0.99633 | -0.069628 | 29.0634
20 | 0.02299 | 0.00577 | -0.022981 | -0.0057648 | 8.5226e-06 | 5.2065e-06 | 0.034441 | 0.034441 | 0.034441 | 0.99336 | -0.12653 | 0.99295 | -0.13431 | 9.4617
21 | 0.11644 | 0.029738 | -0.11629 | -0.029646 | 0.00014652 | 9.2281e-05 | 0.17459 | 0.17459 | 0.17459 | 0.99354 | -0.12286 | 0.99218 | -0.14892 | 15.9879
22 | 0.012931 | 0.0032453 | -0.012926 | -0.0032425 | 5.0338e-06 | 2.7599e-06 | 0.019383 | 0.019384 | 0.019384 | 0.99275 | -0.13819 | 0.99233 | -0.14635 | 5.3252
23 | -0.012931 | -0.0032453 | 0.012933 | 0.0032466 | 2.3916e-06 | 1.3111e-06 | 0.019383 | 0.019383 | 0.019383 | 0.99275 | -0.13819 | 0.99295 | -0.13431 | 5.3251
24 | 0.012926 | 0.0032425 | -0.012916 | -0.003237 | 1.0023e-05 | 5.4964e-06 | 0.019384 | 0.019384 | 0.019384 | 0.99233 | -0.14635 | 0.99149 | -0.16263 | 5.3253
25 | 0.013087 | 0.0032814 | -0.013083 | -0.0032791 | 4.2014e-06 | 2.314e-06 | 0.019635 | 0.019635 | 0.019635 | 0.99184 | -0.15683 | 0.99149 | -0.16357 | 5.3943
26 | 0.011207 | 0.0028088 | -0.011205 | -0.0028079 | 1.7606e-06 | 9.1248e-07 | 0.016814 | 0.016814 | 0.016814 | 0.99184 | -0.15683 | 0.99167 | -0.16013 | 4.6192
27 | -0.031656 | -0.0079352 | 0.031687 | 0.0079547 | 3.1138e-05 | 1.9453e-05 | 0.047493 | 0.047493 | 0.047493 | 0.99184 | -0.15683 | 0.9929 | -0.1362 | 13.0474
28 | 0.0073612 | 0.001845 | -0.0073601 | -0.0018446 | 1.1255e-06 | 4.0279e-07 | 0.011044 | 0.011044 | 0.011044 | 0.99184 | -0.15683 | 0.99167 | -0.16004 | 3.034
29 | 0.0091282 | 0.0022879 | -0.0091271 | -0.0022874 | 1.0841e-06 | 4.9519e-07 | 0.0137 | 0.0137 | 0.0137 | 0.99149 | -0.16357 | 0.99136 | -0.16606 | 3.7636
30 | 0.0076002 | 0.0019045 | -0.007598 | -0.0019037 | 2.1557e-06 | 8.0956e-07 | 0.011404 | 0.011404 | 0.011404 | 0.99167 | -0.16013 | 0.99136 | -0.16608 | 3.1331
31 | 0.0036053 | 0.00090341 | -0.0036051 | -0.00090351 | 2.0246e-07 | -1.0842e-07 | 0.0054097 | 0.0054098 | 0.0054098 | 0.99167 | -0.16013 | 0.9916 | -0.1613 | 1.4862
32 | 0.0083391 | 0.0020904 | -0.0083377 | -0.0020898 | 1.3964e-06 | 5.854e-07 | 0.012498 | 0.012498 | 0.012498 | 0.9929 | -0.1362 | 0.99272 | -0.13972 | 3.4334
33 | -0.040026 | -0.010045 | 0.040043 | 0.010056 | 1.7412e-05 | 1.0977e-05 | 0.05999 | 0.05999 | 0.05999 | 0.9929 | -0.1362 | 0.99337 | -0.12709 | 16.4808
34 | 0.0083377 | 0.0020898 | -0.0083366 | -0.0020894 | 1.0878e-06 | 4.5611e-07 | 0.012498 | 0.012498 | 0.012498 | 0.99272 | -0.13972 | 0.99258 | -0.14246 | 3.4335
35 | -0.04255 | -0.010684 | 0.042565 | 0.010694 | 1.503e-05 | 9.4915e-06 | 0.063745 | 0.063745 | 0.063745 | 0.99337 | -0.12709 | 0.99376 | -0.11969 | 17.5123
36 | -0.0024402 | -0.00061145 | 0.0024403 | 0.00061109 | 1.871e-07 | -3.5971e-07 | 0.0036629 | 0.0036627 | 0.0036629 | 0.99128 | -0.16769 | 0.99136 | -0.16608 | 1.0063
37 | 0.0024402 | 0.00061145 | -0.0024401 | -0.00061155 | 4.9739e-08 | -9.5603e-08 | 0.0036629 | 0.003663 | 0.003663 | 0.99128 | -0.16769 | 0.99125 | -0.16812 | 1.0063
38 | 0.0051577 | 0.0012926 | -0.0051574 | -0.0012926 | 2.9546e-07 | 1.9604e-08 | 0.0077416 | 0.0077417 | 0.0077417 | 0.99136 | -0.16608 | 0.9913 | -0.16728 | 2.1268
39 | -0.025678 | -0.0064407 | 0.025686 | 0.0064459 | 8.4744e-06 | 5.2422e-06 | 0.039306 | 0.039306 | 0.039306 | 0.97212 | -0.53865 | 0.97247 | -0.53173 | 10.7984
40 | 0.025678 | 0.0064407 | -0.025672 | -0.006437 | 5.972e-06 | 3.6943e-06 | 0.039306 | 0.039306 | 0.039306 | 0.97212 | -0.53865 | 0.97187 | -0.54353 | 10.7985
41 | -0.025686 | -0.0064459 | 0.025701 | 0.0064554 | 1.5383e-05 | 9.5154e-06 | 0.039306 | 0.039306 | 0.039306 | 0.97247 | -0.53173 | 0.97311 | -0.51918 | 10.7984
42 | 0.012878 | 0.0032305 | -0.012875 | -0.0032289 | 2.9147e-06 | 1.6177e-06 | 0.019718 | 0.019718 | 0.019718 | 0.97187 | -0.54353 | 0.97163 | -0.54828 | 5.417
43 | -0.026782 | -0.0067263 | 0.0268 | 0.0067376 | 1.8076e-05 | 1.1211e-05 | 0.040959 | 0.040959 | 0.040959 | 0.97311 | -0.51918 | 0.97382 | -0.50504 | 11.2525
44 | -0.0020037 | -0.00050177 | 0.0020038 | 0.00050151 | 9.0614e-08 | -2.6271e-07 | 0.0030617 | 0.0030616 | 0.0030617 | 0.97378 | -0.50599 | 0.97382 | -0.50504 | 0.84113
45 | 0.0020037 | 0.00050177 | -0.0020037 | -0.00050195 | 6.1067e-08 | -1.7701e-07 | 0.0030617 | 0.0030618 | 0.0030618 | 0.97378 | -0.50599 | 0.97374 | -0.50663 | 0.84115
46 | -0.028804 | -0.0072391 | 0.028832 | 0.0072564 | 2.7895e-05 | 1.7375e-05 | 0.044021 | 0.04402 | 0.044021 | 0.97382 | -0.50504 | 0.97485 | -0.48478 | 12.0936
47 | 0.001117 | 0.00027973 | -0.001117 | -0.00027994 | 1.9988e-08 | -2.1478e-07 | 0.0017069 | 0.0017069 | 0.0017069 | 0.97374 | -0.50663 | 0.97372 | -0.50701 | 0.46894
48 | -0.012873 | -0.0032282 | 0.012875 | 0.0032289 | 1.3319e-06 | 7.3928e-07 | 0.019718 | 0.019718 | 0.019718 | 0.97152 | -0.55045 | 0.97163 | -0.54828 | 5.417
49 | 0.012873 | 0.0032282 | -0.012868 | -0.0032249 | 5.8373e-06 | 3.2404e-06 | 0.019718 | 0.019718 | 0.019718 | 0.97152 | -0.55045 | 0.97104 | -0.55997 | 5.4171
50 | -0.0057459 | -0.00144 | 0.0057466 | 0.0014402 | 7.1772e-07 | 1.3945e-07 | 0.0087037 | 0.0087036 | 0.0087037 | 0.98233 | -0.34008 | 0.98246 | -0.33746 | 2.3911
51 | 0.0057459 | 0.00144 | -0.0057455 | -0.0014399 | 4.0589e-07 | 7.8905e-08 | 0.0087037 | 0.0087038 | 0.0087038 | 0.98233 | -0.34008 | 0.98225 | -0.34156 | 2.3911
52 | 0.010039 | 0.002517 | -0.010036 | -0.0025155 | 2.9861e-06 | 1.4751e-06 | 0.015206 | 0.015206 | 0.015206 | 0.98246 | -0.33746 | 0.98215 | -0.3437 | 4.1774
53 | -0.015786 | -0.0039571 | 0.015792 | 0.003961 | 6.5886e-06 | 3.8273e-06 | 0.023909 | 0.023909 | 0.023909 | 0.98246 | -0.33746 | 0.98291 | -0.3287 | 6.5684
54 | -0.00084714 | -0.00021209 | 0.00084717 | 0.00021149 | 2.9528e-08 | -6.0123e-07 | 0.0012756 | 0.0012753 | 0.0012756 | 0.98818 | -0.22569 | 0.98822 | -0.22496 | 0.35043
55 | 0.00084714 | 0.00021209 | -0.00084713 | -0.00021231 | 1.0741e-08 | -2.1864e-07 | 0.0012756 | 0.0012756 | 0.0012756 | 0.98818 | -0.22569 | 0.98817 | -0.22596 | 0.35045
56 | -0.00084717 | -0.00021149 | 0.00084718 | 0.00021129 | 1.0014e-08 | -2.0396e-07 | 0.0012753 | 0.0012753 | 0.0012753 | 0.98822 | -0.22496 | 0.98823 | -0.22471 | 0.35037
57 | -0.011425 | -0.0028629 | 0.011429 | 0.0028654 | 4.6901e-06 | 2.4594e-06 | 0.017198 | 0.017198 | 0.017198 | 0.98846 | -0.22025 | 0.98891 | -0.21164 | 4.7248
58 | 0.011425 | 0.0028629 | -0.011422 | -0.0028616 | 2.4262e-06 | 1.2725e-06 | 0.017198 | 0.017198 | 0.017198 | 0.98846 | -0.22025 | 0.98823 | -0.22471 | 4.7249
59 | -0.10933 | -0.027771 | 0.10966 | 0.027983 | 0.00033114 | 0.00021151 | 0.16464 | 0.16464 | 0.16464 | 0.98891 | -0.21164 | 0.99218 | -0.14892 | 45.2295
60 | 0.097896 | 0.024906 | -0.097771 | -0.024827 | 0.00012439 | 7.9416e-05 | 0.14744 | 0.14744 | 0.14744 | 0.98891 | -0.21164 | 0.98753 | -0.23804 | 40.5048
61 | -0.0010504 | -0.00026301 | 0.0010504 | 0.00026272 | 2.3465e-08 | -2.8842e-07 | 0.0016034 | 0.0016033 | 0.0016034 | 0.97478 | -0.4862 | 0.9748 | -0.48573 | 0.44049
62 | 0.0010504 | 0.00026301 | -0.0010504 | -0.00026326 | 2.0201e-08 | -2.4826e-07 | 0.0016034 | 0.0016035 | 0.0016035 | 0.97478 | -0.4862 | 0.97476 | -0.4866 | 0.44052
63 | -0.0019325 | -0.00048377 | 0.0019325 | 0.00048375 | 6.8673e-09 | -2.1844e-08 | 0.0029497 | 0.0029497 | 0.0029497 | 0.9748 | -0.48573 | 0.97481 | -0.48565 | 0.81035
64 | -0.0013777 | -0.00034497 | 0.0013778 | 0.00034449 | 6.9492e-08 | -4.8408e-07 | 0.0020969 | 0.0020967 | 0.0020969 | 0.97764 | -0.43011 | 0.97769 | -0.42905 | 0.57606
65 | 0.0013777 | 0.00034497 | -0.0013777 | -0.00034528 | 4.4564e-08 | -3.1035e-07 | 0.0020969 | 0.002097 | 0.002097 | 0.97764 | -0.43011 | 0.97761 | -0.43079 | 0.5761
66 | -0.0020761 | -0.00051932 | 0.0020762 | 0.00051894 | 1.3722e-07 | -3.7195e-07 | 0.0031594 | 0.0031592 | 0.0031594 | 0.97769 | -0.42905 | 0.97776 | -0.42766 | 0.86797
67 | 0.0006983 | 0.00017483 | -0.0006983 | -0.00017501 | 6.2752e-09 | -1.8178e-07 | 0.0010627 | 0.0010628 | 0.0010628 | 0.97769 | -0.42905 | 0.97768 | -0.42924 | 0.29198
68 | 0.00054955 | 0.00013766 | -0.00054955 | -0.00013773 | 1.353e-09 | -6.4879e-08 | 0.00083296 | 0.00083299 | 0.00083299 | 0.98169 | -0.35113 | 0.98169 | -0.35118 | 0.22884
69 | 0.0016714 | 0.00041828 | -0.0016714 | -0.00041841 | 2.6757e-08 | -1.2344e-07 | 0.0025333 | 0.0025333 | 0.0025333 | 0.98169 | -0.35113 | 0.98168 | -0.35147 | 0.69596
70 | -0.002221 | -0.00055595 | 0.002221 | 0.00055577 | 7.744e-08 | -1.8087e-07 | 0.0033662 | 0.0033661 | 0.0033662 | 0.98169 | -0.35113 | 0.98173 | -0.3504 | 0.92479
71 | 0.0016714 | 0.00041841 | -0.0016713 | -0.00041863 | 4.9038e-08 | -2.2622e-07 | 0.0025333 | 0.0025334 | 0.0025334 | 0.98168 | -0.35147 | 0.98165 | -0.35208 | 0.69599
72 | -0.00465 | -0.0011645 | 0.0046504 | 0.0011645 | 4.4849e-07 | -1.7462e-08 | 0.0070477 | 0.0070475 | 0.0070477 | 0.98173 | -0.3504 | 0.98183 | -0.34837 | 1.9362
73 | -0.0027581 | -0.00068984 | 0.0027583 | 0.00068965 | 1.5416e-07 | -1.9407e-07 | 0.004197 | 0.0041969 | 0.004197 | 0.97776 | -0.42766 | 0.97782 | -0.42649 | 1.153
74 | 0.09539 | 0.02423 | -0.095371 | -0.024217 | 1.9852e-05 | 1.2672e-05 | 0.14385 | 0.14385 | 0.14385 | 0.98753 | -0.23804 | 0.98731 | -0.24236 | 39.5192
75 | 0.017948 | 0.0045 | -0.017946 | -0.0044992 | 1.4032e-06 | 8.3022e-07 | 0.026805 | 0.026805 | 0.026805 | 0.99633 | -0.069628 | 0.99625 | -0.071268 | 7.3641
76 | -0.23022 | -0.058668 | 0.23025 | 0.058687 | 3.0251e-05 | 1.9281e-05 | 0.34418 | 0.34418 | 0.34418 | 0.99633 | -0.069628 | 0.99648 | -0.066905 | 31.518
77 | 0.0017279 | 0.00043298 | -0.0017279 | -0.00043306 | 1.7089e-08 | -7.6413e-08 | 0.0025936 | 0.0025936 | 0.0025936 | 0.99136 | -0.16606 | 0.99135 | -0.16627 | 0.71253
78 | -0.044703 | -0.01123 | 0.044719 | 0.011239 | 1.5767e-05 | 9.9694e-06 | 0.066946 | 0.066946 | 0.066946 | 0.99376 | -0.11969 | 0.99414 | -0.1123 | 18.3917
79 | -0.0060865 | -0.0015252 | 0.0060873 | 0.0015254 | 7.713e-07 | 1.703e-07 | 0.0090963 | 0.0090962 | 0.0090963 | 0.99565 | -0.082817 | 0.99579 | -0.080157 | 2.499
80 | 0.0060865 | 0.0015252 | -0.0060861 | -0.0015251 | 4.0099e-07 | 8.8574e-08 | 0.0090963 | 0.0090964 | 0.0090964 | 0.99565 | -0.082817 | 0.99558 | -0.0842 | 2.499
81 | 0.0054449 | 0.0013644 | -0.0054444 | -0.0013643 | 5.7676e-07 | 6.6924e-08 | 0.0081363 | 0.0081364 | 0.0081364 | 0.99579 | -0.080157 | 0.99567 | -0.082381 | 2.2353
82 | -0.011532 | -0.0028898 | 0.011533 | 0.0028904 | 1.1817e-06 | 6.1824e-07 | 0.017233 | 0.017232 | 0.017233 | 0.99579 | -0.080157 | 0.9959 | -0.078006 | 4.7342
83 | 0.003061 | 0.00076695 | -0.0030608 | -0.00076712 | 1.6295e-07 | -1.6566e-07 | 0.004575 | 0.0045751 | 0.0045751 | 0.99558 | -0.0842 | 0.99552 | -0.085318 | 1.2569
84 | -0.0065396 | -0.001639 | 0.0065401 | 0.0016392 | 5.2092e-07 | 1.5954e-07 | 0.0099818 | 0.0099818 | 0.0099818 | 0.97487 | -0.48444 | 0.97496 | -0.48277 | 2.7423
85 | 0.0065396 | 0.001639 | -0.0065382 | -0.0016386 | 1.336e-06 | 4.0932e-07 | 0.0099818 | 0.009982 | 0.009982 | 0.97487 | -0.48444 | 0.97465 | -0.48873 | 2.7423
86 | -0.0065401 | -0.0016392 | 0.0065409 | 0.0016395 | 8.3201e-07 | 2.5475e-07 | 0.0099818 | 0.0099817 | 0.0099818 | 0.97496 | -0.48277 | 0.97509 | -0.4801 | 2.7422
87 | -0.030765 | -0.0077399 | 0.03077 | 0.0077431 | 5.0481e-06 | 3.1547e-06 | 0.04697 | 0.04697 | 0.04697 | 0.97485 | -0.48478 | 0.97503 | -0.48135 | 12.9038
88 | 0.0019326 | 0.0004835 | -0.0019325 | -0.00048375 | 8.0304e-08 | -2.5547e-07 | 0.0029496 | 0.0029497 | 0.0029497 | 0.97485 | -0.48478 | 0.97481 | -0.48565 | 0.81035
89 | -0.0081857 | -0.0020515 | 0.0081867 | 0.002052 | 9.9629e-07 | 4.1911e-07 | 0.012404 | 0.012403 | 0.012404 | 0.98201 | -0.34625 | 0.98215 | -0.3437 | 3.4076
90 | 0.00092676 | 0.00023202 | -0.00092674 | -0.00023226 | 1.4583e-08 | -2.3979e-07 | 0.0014047 | 0.0014048 | 0.0014048 | 0.98165 | -0.35208 | 0.98163 | -0.35241 | 0.38594
91 | 0.003142 | 0.0007874 | -0.0031419 | -0.00078744 | 5.1886e-08 | -4.3964e-08 | 0.0047618 | 0.0047618 | 0.0047618 | 0.98183 | -0.34837 | 0.98182 | -0.34872 | 1.3082
92 | -0.0077924 | -0.0019519 | 0.007793 | 0.0019522 | 6.626e-07 | 2.6381e-07 | 0.011809 | 0.011809 | 0.011809 | 0.98183 | -0.34837 | 0.98193 | -0.34659 | 3.2443
93 | -0.0044979 | -0.0011256 | 0.0044982 | 0.0011256 | 3.0679e-07 | -2.275e-08 | 0.0068442 | 0.0068441 | 0.0068442 | 0.97782 | -0.42649 | 0.9779 | -0.42506 | 1.8803
94 | 0.086434 | 0.021977 | -0.08634 | -0.021918 | 9.3988e-05 | 5.9964e-05 | 0.13038 | 0.13038 | 0.13038 | 0.98731 | -0.24236 | 0.98614 | -0.26496 | 35.8189
95 | -0.0050912 | -0.0012758 | 0.0050915 | 0.0012759 | 2.5874e-07 | 1.0191e-08 | 0.007604 | 0.0076039 | 0.007604 | 0.99629 | -0.070553 | 0.99634 | -0.069486 | 2.089
96 | 0.002476 | 0.0006204 | -0.0024759 | -0.00062052 | 6.3979e-08 | -1.2151e-07 | 0.003698 | 0.003698 | 0.003698 | 0.99629 | -0.070553 | 0.99626 | -0.071095 | 1.0159
97 | -0.0074422 | -0.001865 | 0.0074431 | 0.0018653 | 9.1499e-07 | 3.2833e-07 | 0.011115 | 0.011115 | 0.011115 | 0.99634 | -0.069486 | 0.99648 | -0.066905 | 3.0535
98 | -0.23769 | -0.060552 | 0.23794 | 0.06071 | 0.00024818 | 0.00015822 | 0.35529 | 0.35529 | 0.35529 | 0.99648 | -0.066905 | 0.99761 | -0.045287 | 32.5358
99 | -0.24009 | -0.061248 | 0.24026 | 0.061359 | 0.00017472 | 0.0001114 | 0.35849 | 0.35849 | 0.35849 | 0.99761 | -0.045287 | 0.99841 | -0.030231 | 32.8287
100 | 0.015007 | 0.0037625 | -0.015002 | -0.0037598 | 4.8166e-06 | 2.7499e-06 | 0.022415 | 0.022415 | 0.022415 | 0.99625 | -0.071268 | 0.9959 | -0.078006 | 6.1581
101 | 0.066398 | 0.016759 | -0.066336 | -0.01672 | 6.2056e-05 | 3.9495e-05 | 0.099001 | 0.099001 | 0.099001 | 0.99841 | -0.030231 | 0.99739 | -0.049762 | 27.198
102 | -0.30666 | -0.078119 | 0.30711 | 0.078405 | 0.00044794 | 0.00028601 | 0.45749 | 0.45749 | 0.45749 | 0.99841 | -0.030231 | 1 | 0 | 41.8947
103 | 0.0075731 | 0.001898 | -0.0075726 | -0.0018978 | 5.7274e-07 | 2.2002e-07 | 0.011479 | 0.011479 | 0.011479 | 0.9817 | -0.351 | 0.98162 | -0.35259 | 3.1536
104 | -0.010612 | -0.0026598 | 0.010615 | 0.0026609 | 2.2323e-06 | 1.1377e-06 | 0.016086 | 0.016086 | 0.016086 | 0.9817 | -0.351 | 0.98193 | -0.34659 | 4.4192
105 | 0.0032646 | 0.00081814 | -0.0032645 | -0.00081817 | 3.7654e-08 | -2.7733e-08 | 0.0049487 | 0.0049487 | 0.0049487 | 0.98162 | -0.35259 | 0.98161 | -0.35283 | 1.3595
106 | -0.018408 | -0.0046131 | 0.018414 | 0.004617 | 6.5486e-06 | 3.9071e-06 | 0.027895 | 0.027895 | 0.027895 | 0.98193 | -0.34659 | 0.98231 | -0.33912 | 7.6635
107 | -0.077593 | -0.019614 | 0.077613 | 0.019626 | 1.9464e-05 | 1.2409e-05 | 0.1176 | 0.1176 | 0.1176 | 0.98231 | -0.33912 | 0.98258 | -0.33389 | 32.3077
108 | 0.059179 | 0.014997 | -0.059154 | -0.014981 | 2.4774e-05 | 1.5751e-05 | 0.089705 | 0.089705 | 0.089705 | 0.98231 | -0.33912 | 0.98186 | -0.34784 | 24.6443
109 | 0.001142 | 0.00028612 | -0.001142 | -0.00028621 | 9.24e-09 | -9.8429e-08 | 0.0017294 | 0.0017295 | 0.0017295 | 0.98258 | -0.33389 | 0.98257 | -0.33406 | 0.47513
110 | -0.078755 | -0.019913 | 0.078789 | 0.019935 | 3.449e-05 | 2.1992e-05 | 0.11933 | 0.11933 | 0.11933 | 0.98258 | -0.33389 | 0.98305 | -0.32477 | 32.7828
111 | 0.057765 | 0.014633 | -0.057705 | -0.014595 | 5.9991e-05 | 3.8131e-05 | 0.0876 | 0.0876 | 0.0876 | 0.98186 | -0.34784 | 0.98074 | -0.36948 | 24.0659
112 | -0.078789 | -0.019935 | 0.078857 | 0.019978 | 6.7695e-05 | 4.3164e-05 | 0.11933 | 0.11933 | 0.11933 | 0.98305 | -0.32477 | 0.98397 | -0.30688 | 32.7828
113 | 0.0022936 | 0.00057474 | -0.0022935 | -0.00057482 | 3.6061e-08 | -7.7126e-08 | 0.0034799 | 0.0034799 | 0.0034799 | 0.98074 | -0.36948 | 0.98073 | -0.36981 | 0.95602
114 | 0.055412 | 0.01402 | -0.055333 | -0.013971 | 7.8241e-05 | 4.9702e-05 | 0.08412 | 0.08412 | 0.08412 | 0.98074 | -0.36948 | 0.97923 | -0.39895 | 23.1099
115 | -0.081728 | -0.020697 | 0.08178 | 0.020731 | 5.2663e-05 | 3.3588e-05 | 0.12367 | 0.12367 | 0.12367 | 0.98397 | -0.30688 | 0.98466 | -0.29347 | 33.9754
116 | -0.054241 | -0.013671 | 0.054309 | 0.013714 | 6.7836e-05 | 4.3082e-05 | 0.082564 | 0.082564 | 0.082564 | 0.9779 | -0.42506 | 0.97923 | -0.39895 | 22.6824
117 | 0.049743 | 0.012545 | -0.049699 | -0.012517 | 4.4323e-05 | 2.8109e-05 | 0.07572 | 0.07572 | 0.07572 | 0.9779 | -0.42506 | 0.97695 | -0.44369 | 20.8021
118 | 0.08307 | 0.021098 | -0.082957 | -0.021026 | 0.00011379 | 7.2582e-05 | 0.12545 | 0.12545 | 0.12545 | 0.98614 | -0.26496 | 0.98466 | -0.29347 | 34.4636
119 | 0.0010244 | 0.00025657 | -0.0010243 | -0.00025673 | 1.1607e-08 | -1.5327e-07 | 0.0015565 | 0.0015566 | 0.0015566 | 0.97923 | -0.39895 | 0.97922 | -0.39919 | 0.42763
120 | 0.044731 | 0.011272 | -0.04467 | -0.011234 | 6.0547e-05 | 3.8316e-05 | 0.068153 | 0.068153 | 0.068153 | 0.97695 | -0.44369 | 0.9755 | -0.47202 | 18.7234
121 | 0.013053 | 0.0032732 | -0.013048 | -0.0032704 | 5.0234e-06 | 2.7934e-06 | 0.019912 | 0.019912 | 0.019912 | 0.9755 | -0.47202 | 0.97509 | -0.4801 | 5.4704
122 | 0.031617 | 0.0079607 | -0.031603 | -0.0079519 | 1.4083e-05 | 8.812e-06 | 0.048241 | 0.048241 | 0.048241 | 0.9755 | -0.47202 | 0.97503 | -0.48135 | 13.2531
123 | 0.064211 | 0.016187 | -0.064176 | -0.016165 | 3.5614e-05 | 2.2658e-05 | 0.095831 | 0.095831 | 0.095831 | 0.99739 | -0.049762 | 0.99678 | -0.06136 | 26.3272
124 | 0.0085012 | 0.0021305 | -0.0085006 | -0.0021303 | 6.0258e-07 | 2.5392e-07 | 0.01265 | 0.01265 | 0.01265 | 1 | 0 | 0.99992 | -0.001488 | 3.4752
125 | 0.0025914 | 0.00064932 | -0.0025913 | -0.00064945 | 8.1513e-08 | -1.3631e-07 | 0.0038728 | 0.0038728 | 0.0038728 | 0.99567 | -0.082381 | 0.99564 | -0.083041 | 1.064
126 | 0.0064093 | 0.0016061 | -0.006409 | -0.0016061 | 3.3188e-07 | 8.4798e-08 | 0.0095378 | 0.0095378 | 0.0095378 | 0.99992 | -0.001488 | 0.99987 | -0.0025751 | 2.6203
127 | 0.004465 | 0.0011188 | -0.0044648 | -0.0011189 | 1.6884e-07 | -2.568e-08 | 0.0066448 | 0.0066448 | 0.0066448 | 0.99987 | -0.0025751 | 0.99982 | -0.0033689 | 1.8255
128 | 0.0021492 | 0.00053853 | -0.0021492 | -0.00053863 | 3.6746e-08 | -1.0209e-07 | 0.0031986 | 0.0031986 | 0.0031986 | 0.99982 | -0.0033689 | 0.99981 | -0.0037279 | 0.87874
129 | 0.055367 | 0.013957 | -0.055324 | -0.013929 | 4.3273e-05 | 2.7475e-05 | 0.082681 | 0.082681 | 0.082681 | 0.99678 | -0.06136 | 0.99593 | -0.077707 | 22.7147
130 | 0.0088086 | 0.002208 | -0.0088074 | -0.0022075 | 1.1019e-06 | 4.8375e-07 | 0.01315 | 0.01315 | 0.01315 | 0.99678 | -0.06136 | 0.99665 | -0.063986 | 3.6126
131 | 0.053077 | 0.013366 | -0.053054 | -0.013351 | 2.3443e-05 | 1.4875e-05 | 0.079325 | 0.079325 | 0.079325 | 0.99593 | -0.077707 | 0.99545 | -0.086949 | 21.7925
132 | 0.0079849 | 0.0020014 | -0.0079837 | -0.0020009 | 1.1936e-06 | 4.7211e-07 | 0.011922 | 0.011922 | 0.011922 | 0.99665 | -0.063986 | 0.99649 | -0.067123 | 3.2752
133 | 0.051339 | 0.012921 | -0.051316 | -0.012907 | 2.2374e-05 | 1.4188e-05 | 0.076761 | 0.076761 | 0.076761 | 0.99545 | -0.086949 | 0.99498 | -0.096072 | 21.0882
134 | 0.048956 | 0.012316 | -0.048935 | -0.012303 | 2.0345e-05 | 1.2889e-05 | 0.073231 | 0.073231 | 0.073231 | 0.99498 | -0.096072 | 0.99453 | -0.10477 | 20.1184
135 | -0.046876 | -0.01178 | 0.046893 | 0.011791 | 1.6841e-05 | 1.066e-05 | 0.070175 | 0.070175 | 0.070175 | 0.99414 | -0.1123 | 0.99453 | -0.10477 | 19.2787

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.3196 | 0.081121

## res_load
| p_mw | q_mvar
0 | 0.01468 | 0.0036791
1 | 0.0030187 | 0.00075656
2 | 0.0052867 | 0.001325
3 | 0.0033574 | 0.00084144
4 | 0.0022323 | 0.00055946
5 | 0.0063992 | 0.0016038
6 | 0.0026453 | 0.00066297
7 | 0.0026395 | 0.00066152
8 | 0.011175 | 0.0028007
9 | 0.010048 | 0.0025182
10 | 0.0035263 | 0.00088377
11 | 0.0039551 | 0.00099123
12 | 0.0073601 | 0.0018446
13 | 0.0025066 | 0.00062821
14 | 0.0024401 | 0.00061155
15 | 0.0036051 | 0.00090351
16 | 0.012794 | 0.0032064
17 | 0.001081 | 0.00027091
18 | 0.00088666 | 0.00022222
19 | 0.012868 | 0.0032249
20 | 0.0057455 | 0.0014399
21 | 0.00084713 | 0.00021231
22 | 0.010575 | 0.0026504
23 | 0.00088202 | 0.00022106
24 | 0.0010504 | 0.00026326
25 | 0.0013777 | 0.00034528
26 | 0.00054955 | 0.00013773
27 | 0.0024289 | 0.00060874
28 | 0.00068189 | 0.0001709
29 | 0.0006983 | 0.00017501
30 | 0.0066361 | 0.0016632
31 | 0.002381 | 0.00059672
32 | 0.012916 | 0.003237
33 | 0.0010482 | 0.0002627
34 | 0.0073991 | 0.0018544
35 | 0.0083366 | 0.0020894
36 | 0.0021377 | 0.00053577
37 | 0.0051574 | 0.0012926
38 | 0.0030251 | 0.00075816
39 | 0.0065382 | 0.0016386
40 | 0.001117 | 0.00027994
41 | 0.0081857 | 0.0020515
42 | 0.0018496 | 0.00046355
43 | 0.00074459 | 0.00018661
44 | 0.0017396 | 0.000436
45 | 0.0089368 | 0.0022398
46 | 0.0017279 | 0.00043306
47 | 0.0026152 | 0.00065544
48 | 0.0023507 | 0.00058915
49 | 0.0024759 | 0.00062052
50 | 0.0021443 | 0.0005374
51 | 0.0029392 | 0.00073664
52 | 0.0030393 | 0.00076173
53 | 0.004308 | 0.0010797
54 | 0.0032645 | 0.00081817
55 | 0.0013892 | 0.00034816
56 | 0.0031419 | 0.00078744
57 | 0.001142 | 0.00028621
58 | 0.00092674 | 0.00023226
59 | 0.0028705 | 0.00071943
60 | 0.0032695 | 0.00081941
61 | 0.0011761 | 0.00029477
62 | 0.0049679 | 0.0012451
63 | 0.0010243 | 0.00025673
64 | 0.0034689 | 0.00086938
65 | 0.0021247 | 0.0005325
66 | 0.0023384 | 0.00058605
67 | 0.0065075 | 0.0016309
68 | 0.0022935 | 0.00057482
69 | 0.0028529 | 0.00071501
70 | 0.0030608 | 0.00076712
71 | 0.0020913 | 0.00052412
72 | 0.001944 | 0.00048721
73 | 0.0023156 | 0.00058035
74 | 0.0021492 | 0.00053863
75 | 0.0022467 | 0.00056308
76 | 0.00082252 | 0.00020614
77 | 0.0079837 | 0.0020009
78 | 0.0017151 | 0.00042984
79 | 0.0023606 | 0.00059161
80 | 0.0025913 | 0.00064945
81 | 0.0021573 | 0.00054066
82 | 0.0020426 | 0.00051193
83 | 0.000833 | 0.00020877

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1