## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1040-18_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1040-18_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1040-18_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1040-18_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1040-18_0_6_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_1040-18_0_6_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_1040-18_0_6_node_161 | 0.4 | n |  | TRUE
7 | bus_LV_1040-18_0_6_node_162 | 0.4 | n |  | TRUE
8 | bus_LV_1040-18_0_6_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_1040-18_0_6_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_1040-18_0_6_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_1040-18_0_6_node_253 | 0.4 | n |  | TRUE
12 | bus_LV_1040-18_0_6_node_252 | 0.4 | n |  | TRUE
13 | bus_LV_1040-18_0_6_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_1040-18_0_6_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_1040-18_0_6_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_1040-18_0_6_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_1040-18_0_6_node_251 | 0.4 | n |  | TRUE
18 | bus_LV_1040-18_0_6_node_189 | 0.4 | n |  | TRUE
19 | bus_LV_1040-18_0_6_node_147 | 0.4 | n |  | TRUE
20 | bus_LV_1040-18_0_6_node_187 | 0.4 | n |  | TRUE
21 | bus_LV_1040-18_0_6_node_145 | 0.4 | n |  | TRUE
22 | bus_LV_1040-18_0_6_node_149 | 0.4 | n |  | TRUE
23 | bus_LV_1040-18_0_6_node_212 | 0.4 | n |  | TRUE
24 | bus_LV_1040-18_0_6_node_48 | 0.4 | n |  | TRUE
25 | bus_LV_1040-18_0_6_node_275 | 0.4 | n |  | TRUE
26 | bus_LV_1040-18_0_6_node_47 | 0.4 | n |  | TRUE
27 | bus_LV_1040-18_0_6_node_148 | 0.4 | n |  | TRUE
28 | bus_LV_1040-18_0_6_node_143 | 0.4 | n |  | TRUE
29 | bus_LV_1040-18_0_6_node_150 | 0.4 | n |  | TRUE
30 | bus_LV_1040-18_0_6_node_182 | 0.4 | n |  | TRUE
31 | bus_LV_1040-18_0_6_node_179 | 0.4 | n |  | TRUE
32 | bus_LV_1040-18_0_6_node_146 | 0.4 | n |  | TRUE
33 | bus_LV_1040-18_0_6_node_173 | 0.4 | n |  | TRUE
34 | bus_LV_1040-18_0_6_node_171 | 0.4 | n |  | TRUE
35 | bus_LV_1040-18_0_6_node_15 | 0.4 | n |  | TRUE
36 | bus_LV_1040-18_0_6_node_16 | 0.4 | n |  | TRUE
37 | bus_LV_1040-18_0_6_node_17 | 0.4 | n |  | TRUE
38 | bus_LV_1040-18_0_6_node_273 | 0.4 | n |  | TRUE
39 | bus_LV_1040-18_0_6_node_18 | 0.4 | n |  | TRUE
40 | bus_LV_1040-18_0_6_node_20 | 0.4 | n |  | TRUE
41 | bus_LV_1040-18_0_6_node_166 | 0.4 | n |  | TRUE
42 | bus_LV_1040-18_0_6_node_21 | 0.4 | n |  | TRUE
43 | bus_LV_1040-18_0_6_node_19 | 0.4 | n |  | TRUE
44 | bus_LV_1040-18_0_6_node_22 | 0.4 | n |  | TRUE
45 | bus_LV_1040-18_0_6_node_129 | 0.4 | n |  | TRUE
46 | bus_LV_1040-18_0_6_node_23 | 0.4 | n |  | TRUE
47 | bus_LV_1040-18_0_6_node_33 | 0.4 | n |  | TRUE
48 | bus_LV_1040-18_0_6_node_127 | 0.4 | n |  | TRUE
49 | bus_LV_1040-18_0_6_node_24 | 0.4 | n |  | TRUE
50 | bus_LV_1040-18_0_6_node_131 | 0.4 | n |  | TRUE
51 | bus_LV_1040-18_0_6_node_25 | 0.4 | n |  | TRUE
52 | bus_LV_1040-18_0_6_node_130 | 0.4 | n |  | TRUE
53 | bus_LV_1040-18_0_6_node_132 | 0.4 | n |  | TRUE
54 | bus_LV_1040-18_0_6_node_109 | 0.4 | n |  | TRUE
55 | bus_LV_1040-18_0_6_node_26 | 0.4 | n |  | TRUE
56 | bus_LV_1040-18_0_6_node_134 | 0.4 | n |  | TRUE
57 | bus_LV_1040-18_0_6_node_133 | 0.4 | n |  | TRUE
58 | bus_LV_1040-18_0_6_node_27 | 0.4 | n |  | TRUE
59 | bus_LV_1040-18_0_6_node_108 | 0.4 | n |  | TRUE
60 | bus_LV_1040-18_0_6_node_105 | 0.4 | n |  | TRUE
61 | bus_LV_1040-18_0_6_node_28 | 0.4 | n |  | TRUE
62 | bus_LV_1040-18_0_6_node_106 | 0.4 | n |  | TRUE
63 | bus_LV_1040-18_0_6_node_107 | 0.4 | n |  | TRUE
64 | bus_LV_1040-18_0_6_node_29 | 0.4 | n |  | TRUE
65 | bus_LV_1040-18_0_6_node_30 | 0.4 | n |  | TRUE
66 | bus_LV_1040-18_0_6_node_100 | 0.4 | n |  | TRUE
67 | bus_LV_1040-18_0_6_node_90 | 0.4 | n |  | TRUE
68 | bus_LV_1040-18_0_6_node_114 | 0.4 | n |  | TRUE
69 | bus_LV_1040-18_0_6_node_128 | 0.4 | n |  | TRUE
70 | bus_LV_1040-18_0_6_node_34 | 0.4 | n |  | TRUE
71 | bus_LV_1040-18_0_6_node_32 | 0.4 | n |  | TRUE
72 | bus_LV_1040-18_0_6_node_260 | 0.4 | n |  | TRUE
73 | bus_LV_1040-18_0_6_node_87 | 0.4 | n |  | TRUE
74 | bus_LV_1040-18_0_6_node_89 | 0.4 | n |  | TRUE
75 | bus_LV_1040-18_0_6_node_85 | 0.4 | n |  | TRUE
76 | bus_LV_1040-18_0_6_node_99 | 0.4 | n |  | TRUE
77 | bus_LV_1040-18_0_6_node_97 | 0.4 | n |  | TRUE
78 | bus_LV_1040-18_0_6_node_258 | 0.4 | n |  | TRUE
79 | bus_LV_1040-18_0_6_node_112 | 0.4 | n |  | TRUE
80 | bus_LV_1040-18_0_6_node_110 | 0.4 | n |  | TRUE
81 | bus_LV_1040-18_0_6_node_113 | 0.4 | n |  | TRUE
82 | bus_LV_1040-18_0_6_node_115 | 0.4 | n |  | TRUE
83 | bus_LV_1040-18_0_6_node_101 | 0.4 | n |  | TRUE
84 | bus_LV_1040-18_0_6_node_35 | 0.4 | n |  | TRUE
85 | bus_LV_1040-18_0_6_node_36 | 0.4 | n |  | TRUE
86 | bus_LV_1040-18_0_6_node_37 | 0.4 | n |  | TRUE
87 | bus_LV_1040-18_0_6_node_302 | 0.4 | n |  | TRUE
88 | bus_LV_1040-18_0_6_node_262 | 0.4 | n |  | TRUE
89 | bus_LV_1040-18_0_6_node_268 | 0.4 | n |  | TRUE
90 | bus_LV_1040-18_0_6_node_267 | 0.4 | n |  | TRUE
91 | bus_LV_1040-18_0_6_node_261 | 0.4 | n |  | TRUE
92 | bus_LV_1040-18_0_6_node_299 | 0.4 | n |  | TRUE
93 | bus_LV_1040-18_0_6_node_265 | 0.4 | n |  | TRUE
94 | bus_LV_1040-18_0_6_node_38 | 0.4 | n |  | TRUE
95 | bus_LV_1040-18_0_6_node_39 | 0.4 | n |  | TRUE
96 | bus_LV_1040-18_0_6_node_40 | 0.4 | n |  | TRUE
97 | bus_LV_1040-18_0_6_node_41 | 0.4 | n |  | TRUE
98 | bus_LV_1040-18_0_6_node_44 | 0.4 | n |  | TRUE
99 | bus_LV_1040-18_0_6_node_43 | 0.4 | n |  | TRUE
100 | bus_LV_1040-18_0_6_node_42 | 0.4 | n |  | TRUE
101 | bus_LV_1040-18_0_6_node_72 | 0.4 | n |  | TRUE
102 | bus_LV_1040-18_0_6_node_304 | 0.4 | n |  | TRUE
103 | bus_LV_1040-18_0_6_node_305 | 0.4 | n |  | TRUE
104 | bus_LV_1040-18_0_6_node_289 | 0.4 | n |  | TRUE
105 | bus_LV_1040-18_0_6_node_303 | 0.4 | n |  | TRUE
106 | bus_LV_1040-18_0_6_node_68 | 0.4 | n |  | TRUE
107 | bus_LV_1040-18_0_6_node_45 | 0.4 | n |  | TRUE
108 | bus_LV_1040-18_0_6_node_67 | 0.4 | n |  | TRUE
109 | bus_LV_1040-18_0_6_node_84 | 0.4 | n |  | TRUE
110 | bus_LV_1040-18_0_6_node_256 | 0.4 | n |  | TRUE
111 | bus_LV_1040-18_0_6_node_49 | 0.4 | n |  | TRUE
112 | bus_LV_1040-18_0_6_node_290 | 0.4 | n |  | TRUE
113 | bus_LV_1040-18_0_6_node_292 | 0.4 | n |  | TRUE
114 | bus_LV_1040-18_0_6_node_50 | 0.4 | n |  | TRUE
115 | bus_LV_1040-18_0_6_node_282 | 0.4 | n |  | TRUE
116 | bus_LV_1040-18_0_6_node_294 | 0.4 | n |  | TRUE
117 | bus_LV_1040-18_0_6_node_54 | 0.4 | n |  | TRUE
118 | bus_LV_1040-18_0_6_node_286 | 0.4 | n |  | TRUE
119 | bus_LV_1040-18_0_6_node_74 | 0.4 | n |  | TRUE
120 | bus_LV_1040-18_0_6_node_71 | 0.4 | n |  | TRUE
121 | bus_LV_1040-18_0_6_node_70 | 0.4 | n |  | TRUE
122 | bus_LV_1040-18_0_6_node_63 | 0.4 | n |  | TRUE
123 | bus_LV_1040-18_0_6_node_64 | 0.4 | n |  | TRUE
124 | bus_LV_1040-18_0_6_node_82 | 0.4 | n |  | TRUE
125 | bus_LV_1040-18_0_6_node_255 | 0.4 | n |  | TRUE
126 | bus_LV_1040-18_0_6_node_276 | 0.4 | n |  | TRUE
127 | bus_LV_1040-18_0_6_node_83 | 0.4 | n |  | TRUE
128 | bus_LV_1040-18_0_6_node_291 | 0.4 | n |  | TRUE
129 | bus_LV_1040-18_0_6_node_284 | 0.4 | n |  | TRUE
130 | bus_LV_1040-18_0_6_node_280 | 0.4 | n |  | TRUE
131 | bus_LV_1040-18_0_6_node_51 | 0.4 | n |  | TRUE
132 | bus_LV_1040-18_0_6_node_52 | 0.4 | n |  | TRUE
133 | bus_LV_1040-18_0_6_node_53 | 0.4 | n |  | TRUE
134 | bus_LV_1040-18_0_6_node_55 | 0.4 | n |  | TRUE
135 | bus_LV_1040-18_0_6_node_56 | 0.4 | n |  | TRUE
136 | bus_LV_1040-18_0_6_node_73 | 0.4 | n |  | TRUE
137 | bus_LV_1040-18_0_6_node_75 | 0.4 | n |  | TRUE
138 | bus_LV_1040-18_0_6_node_76 | 0.4 | n |  | TRUE
139 | bus_LV_1040-18_0_6_node_57 | 0.4 | n |  | TRUE
140 | bus_LV_1040-18_0_6_node_58 | 0.4 | n |  | TRUE
141 | bus_LV_1040-18_0_6_node_59 | 0.4 | n |  | TRUE
142 | bus_LV_1040-18_0_6_node_60 | 0.4 | n |  | TRUE
143 | bus_LV_1040-18_0_6_node_61 | 0.4 | n |  | TRUE
144 | bus_LV_1040-18_0_6_node_62 | 0.4 | n |  | TRUE
145 | bus_LV_1040-18_0_6_node_65 | 0.4 | n |  | TRUE
146 | bus_LV_1040-18_0_6_node_66 | 0.4 | n |  | TRUE
147 | bus_LV_1040-18_0_6_node_94 | 0.4 | n |  | TRUE
148 | bus_LV_1040-18_0_6_node_246 | 0.4 | n |  | TRUE
149 | bus_LV_1040-18_0_6_node_257 | 0.4 | n |  | TRUE
150 | bus_LV_1040-18_0_6_node_77 | 0.4 | n |  | TRUE
151 | bus_LV_1040-18_0_6_node_78 | 0.4 | n |  | TRUE
152 | bus_LV_1040-18_0_6_node_79 | 0.4 | n |  | TRUE
153 | bus_LV_1040-18_0_6_node_80 | 0.4 | n |  | TRUE
154 | bus_LV_1040-18_0_6_node_81 | 0.4 | n |  | TRUE
155 | bus_LV_1040-18_0_6_node_86 | 0.4 | n |  | TRUE
156 | bus_LV_1040-18_0_6_node_88 | 0.4 | n |  | TRUE
157 | bus_LV_1040-18_0_6_node_95 | 0.4 | n |  | TRUE
158 | bus_LV_1040-18_0_6_node_96 | 0.4 | n |  | TRUE
159 | bus_LV_1040-18_0_6_node_98 | 0.4 | n |  | TRUE
160 | bus_LV_1040-18_0_6_node_102 | 0.4 | n |  | TRUE
161 | bus_LV_1040-18_0_6_node_103 | 0.4 | n |  | TRUE
162 | bus_LV_1040-18_0_6_node_104 | 0.4 | n |  | TRUE
163 | bus_LV_1040-18_0_6_node_279 | 0.4 | n |  | TRUE
164 | bus_LV_1040-18_0_6_node_116 | 0.4 | n |  | TRUE
165 | bus_LV_1040-18_0_6_node_135 | 0.4 | n |  | TRUE
166 | bus_LV_1040-18_0_6_node_111 | 0.4 | n |  | TRUE
167 | bus_LV_1040-18_0_6_node_136 | 0.4 | n |  | TRUE
168 | bus_LV_1040-18_0_6_node_117 | 0.4 | n |  | TRUE
169 | bus_LV_1040-18_0_6_node_123 | 0.4 | n |  | TRUE
170 | bus_LV_1040-18_0_6_node_121 | 0.4 | n |  | TRUE
171 | bus_LV_1040-18_0_6_node_118 | 0.4 | n |  | TRUE
172 | bus_LV_1040-18_0_6_node_119 | 0.4 | n |  | TRUE
173 | bus_LV_1040-18_0_6_node_120 | 0.4 | n |  | TRUE
174 | bus_LV_1040-18_0_6_node_125 | 0.4 | n |  | TRUE
175 | bus_LV_1040-18_0_6_node_126 | 0.4 | n |  | TRUE
176 | bus_LV_1040-18_0_6_node_122 | 0.4 | n |  | TRUE
177 | bus_LV_1040-18_0_6_node_124 | 0.4 | n |  | TRUE
178 | bus_LV_1040-18_0_6_node_232 | 0.4 | n |  | TRUE
179 | bus_LV_1040-18_0_6_node_231 | 0.4 | n |  | TRUE
180 | bus_LV_1040-18_0_6_node_160 | 0.4 | n |  | TRUE
181 | bus_LV_1040-18_0_6_node_184 | 0.4 | n |  | TRUE
182 | bus_LV_1040-18_0_6_node_259 | 0.4 | n |  | TRUE
183 | bus_LV_1040-18_0_6_node_235 | 0.4 | n |  | TRUE
184 | bus_LV_1040-18_0_6_node_137 | 0.4 | n |  | TRUE
185 | bus_LV_1040-18_0_6_node_138 | 0.4 | n |  | TRUE
186 | bus_LV_1040-18_0_6_node_140 | 0.4 | n |  | TRUE
187 | bus_LV_1040-18_0_6_node_274 | 0.4 | n |  | TRUE
188 | bus_LV_1040-18_0_6_node_263 | 0.4 | n |  | TRUE
189 | bus_LV_1040-18_0_6_node_141 | 0.4 | n |  | TRUE
190 | bus_LV_1040-18_0_6_node_142 | 0.4 | n |  | TRUE
191 | bus_LV_1040-18_0_6_node_266 | 0.4 | n |  | TRUE
192 | bus_LV_1040-18_0_6_node_264 | 0.4 | n |  | TRUE
193 | bus_LV_1040-18_0_6_node_144 | 0.4 | n |  | TRUE
194 | bus_LV_1040-18_0_6_node_151 | 0.4 | n |  | TRUE
195 | bus_LV_1040-18_0_6_node_152 | 0.4 | n |  | TRUE
196 | bus_LV_1040-18_0_6_node_213 | 0.4 | n |  | TRUE
197 | bus_LV_1040-18_0_6_node_180 | 0.4 | n |  | TRUE
198 | bus_LV_1040-18_0_6_node_153 | 0.4 | n |  | TRUE
199 | bus_LV_1040-18_0_6_node_238 | 0.4 | n |  | TRUE
200 | bus_LV_1040-18_0_6_node_154 | 0.4 | n |  | TRUE
201 | bus_LV_1040-18_0_6_node_155 | 0.4 | n |  | TRUE
202 | bus_LV_1040-18_0_6_node_156 | 0.4 | n |  | TRUE
203 | bus_LV_1040-18_0_6_node_157 | 0.4 | n |  | TRUE
204 | bus_LV_1040-18_0_6_node_158 | 0.4 | n |  | TRUE
205 | bus_LV_1040-18_0_6_node_159 | 0.4 | n |  | TRUE
206 | bus_LV_1040-18_0_6_node_219 | 0.4 | n |  | TRUE
207 | bus_LV_1040-18_0_6_node_236 | 0.4 | n |  | TRUE
208 | bus_LV_1040-18_0_6_node_278 | 0.4 | n |  | TRUE
209 | bus_LV_1040-18_0_6_node_217 | 0.4 | n |  | TRUE
210 | bus_LV_1040-18_0_6_node_203 | 0.4 | n |  | TRUE
211 | bus_LV_1040-18_0_6_node_183 | 0.4 | n |  | TRUE
212 | bus_LV_1040-18_0_6_node_168 | 0.4 | n |  | TRUE
213 | bus_LV_1040-18_0_6_node_220 | 0.4 | n |  | TRUE
214 | bus_LV_1040-18_0_6_node_163 | 0.4 | n |  | TRUE
215 | bus_LV_1040-18_0_6_node_164 | 0.4 | n |  | TRUE
216 | bus_LV_1040-18_0_6_node_165 | 0.4 | n |  | TRUE
217 | bus_LV_1040-18_0_6_node_167 | 0.4 | n |  | TRUE
218 | bus_LV_1040-18_0_6_node_248 | 0.4 | n |  | TRUE
219 | bus_LV_1040-18_0_6_node_247 | 0.4 | n |  | TRUE
220 | bus_LV_1040-18_0_6_node_221 | 0.4 | n |  | TRUE
221 | bus_LV_1040-18_0_6_node_169 | 0.4 | n |  | TRUE
222 | bus_LV_1040-18_0_6_node_170 | 0.4 | n |  | TRUE
223 | bus_LV_1040-18_0_6_node_172 | 0.4 | n |  | TRUE
224 | bus_LV_1040-18_0_6_node_277 | 0.4 | n |  | TRUE
225 | bus_LV_1040-18_0_6_node_174 | 0.4 | n |  | TRUE
226 | bus_LV_1040-18_0_6_node_175 | 0.4 | n |  | TRUE
227 | bus_LV_1040-18_0_6_node_176 | 0.4 | n |  | TRUE
228 | bus_LV_1040-18_0_6_node_177 | 0.4 | n |  | TRUE
229 | bus_LV_1040-18_0_6_node_178 | 0.4 | n |  | TRUE
230 | bus_LV_1040-18_0_6_node_243 | 0.4 | n |  | TRUE
231 | bus_LV_1040-18_0_6_node_270 | 0.4 | n |  | TRUE
232 | bus_LV_1040-18_0_6_node_244 | 0.4 | n |  | TRUE
233 | bus_LV_1040-18_0_6_node_269 | 0.4 | n |  | TRUE
234 | bus_LV_1040-18_0_6_node_181 | 0.4 | n |  | TRUE
235 | bus_LV_1040-18_0_6_node_245 | 0.4 | n |  | TRUE
236 | bus_LV_1040-18_0_6_node_254 | 0.4 | n |  | TRUE
237 | bus_LV_1040-18_0_6_node_185 | 0.4 | n |  | TRUE
238 | bus_LV_1040-18_0_6_node_186 | 0.4 | n |  | TRUE
239 | bus_LV_1040-18_0_6_node_188 | 0.4 | n |  | TRUE
240 | bus_LV_1040-18_0_6_node_222 | 0.4 | n |  | TRUE
241 | bus_LV_1040-18_0_6_node_226 | 0.4 | n |  | TRUE
242 | bus_LV_1040-18_0_6_node_190 | 0.4 | n |  | TRUE
243 | bus_LV_1040-18_0_6_node_191 | 0.4 | n |  | TRUE
244 | bus_LV_1040-18_0_6_node_192 | 0.4 | n |  | TRUE
245 | bus_LV_1040-18_0_6_node_193 | 0.4 | n |  | TRUE
246 | bus_LV_1040-18_0_6_node_194 | 0.4 | n |  | TRUE
247 | bus_LV_1040-18_0_6_node_225 | 0.4 | n |  | TRUE
248 | bus_LV_1040-18_0_6_node_271 | 0.4 | n |  | TRUE
249 | bus_LV_1040-18_0_6_node_272 | 0.4 | n |  | TRUE
250 | bus_LV_1040-18_0_6_node_241 | 0.4 | n |  | TRUE
251 | bus_LV_1040-18_0_6_node_210 | 0.4 | n |  | TRUE
252 | bus_LV_1040-18_0_6_node_195 | 0.4 | n |  | TRUE
253 | bus_LV_1040-18_0_6_node_196 | 0.4 | n |  | TRUE
254 | bus_LV_1040-18_0_6_node_197 | 0.4 | n |  | TRUE
255 | bus_LV_1040-18_0_6_node_198 | 0.4 | n |  | TRUE
256 | bus_LV_1040-18_0_6_node_199 | 0.4 | n |  | TRUE
257 | bus_LV_1040-18_0_6_node_229 | 0.4 | n |  | TRUE
258 | bus_LV_1040-18_0_6_node_242 | 0.4 | n |  | TRUE
259 | bus_LV_1040-18_0_6_node_228 | 0.4 | n |  | TRUE
260 | bus_LV_1040-18_0_6_node_209 | 0.4 | n |  | TRUE
261 | bus_LV_1040-18_0_6_node_200 | 0.4 | n |  | TRUE
262 | bus_LV_1040-18_0_6_node_201 | 0.4 | n |  | TRUE
263 | bus_LV_1040-18_0_6_node_202 | 0.4 | n |  | TRUE
264 | bus_LV_1040-18_0_6_node_204 | 0.4 | n |  | TRUE
265 | bus_LV_1040-18_0_6_node_239 | 0.4 | n |  | TRUE
266 | bus_LV_1040-18_0_6_node_240 | 0.4 | n |  | TRUE
267 | bus_LV_1040-18_0_6_node_205 | 0.4 | n |  | TRUE
268 | bus_LV_1040-18_0_6_node_206 | 0.4 | n |  | TRUE
269 | bus_LV_1040-18_0_6_node_207 | 0.4 | n |  | TRUE
270 | bus_LV_1040-18_0_6_node_208 | 0.4 | n |  | TRUE
271 | bus_LV_1040-18_0_6_node_211 | 0.4 | n |  | TRUE
272 | bus_LV_1040-18_0_6_node_223 | 0.4 | n |  | TRUE
273 | bus_LV_1040-18_0_6_node_296 | 0.4 | n |  | TRUE
274 | bus_LV_1040-18_0_6_node_224 | 0.4 | n |  | TRUE
275 | bus_LV_1040-18_0_6_node_295 | 0.4 | n |  | TRUE
276 | bus_LV_1040-18_0_6_node_214 | 0.4 | n |  | TRUE
277 | bus_LV_1040-18_0_6_node_237 | 0.4 | n |  | TRUE
278 | bus_LV_1040-18_0_6_node_215 | 0.4 | n |  | TRUE
279 | bus_LV_1040-18_0_6_node_216 | 0.4 | n |  | TRUE
280 | bus_LV_1040-18_0_6_node_218 | 0.4 | n |  | TRUE
281 | bus_LV_1040-18_0_6_node_227 | 0.4 | n |  | TRUE
282 | bus_LV_1040-18_0_6_node_230 | 0.4 | n |  | TRUE
283 | bus_LV_1040-18_0_6_node_233 | 0.4 | n |  | TRUE
284 | bus_LV_1040-18_0_6_node_234 | 0.4 | n |  | TRUE
285 | bus_LV_1040-18_0_6_node_301 | 0.4 | n |  | TRUE
286 | bus_LV_1040-18_0_6_node_297 | 0.4 | n |  | TRUE
287 | bus_LV_1040-18_0_6_node_300 | 0.4 | n |  | TRUE
288 | bus_LV_1040-18_0_6_node_250 | 0.4 | n |  | TRUE
289 | bus_LV_1040-18_0_6_node_249 | 0.4 | n |  | TRUE
290 | bus_LV_1040-18_0_6_node_298 | 0.4 | n |  | TRUE
291 | bus_LV_1040-18_0_6_node_281 | 0.4 | n |  | TRUE
292 | bus_LV_1040-18_0_6_node_283 | 0.4 | n |  | TRUE
293 | bus_LV_1040-18_0_6_node_293 | 0.4 | n |  | TRUE
294 | bus_LV_1040-18_0_6_node_288 | 0.4 | n |  | TRUE
295 | bus_LV_1040-18_0_6_node_285 | 0.4 | n |  | TRUE
296 | bus_LV_1040-18_0_6_node_287 | 0.4 | n |  | TRUE
297 | bus_MV_214_1_node_118 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1040-18_0_6_load_0 | 0 | 0.00032747 | 8.2071e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1040-18_0_6_load_2 | 2 | 0.00040583 | 0.00010171 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1040-18_0_6_load_5 | 4 | 0.0020068 | 0.00050294 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1040-18_0_6_load_4 | 5 | 0.0076284 | 0.0019119 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1040-18_0_6_load_161 | 6 | 0.0013574 | 0.00034021 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1040-18_0_6_load_162 | 7 | 0.0013596 | 0.00034075 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1040-18_0_6_load_6 | 8 | 0.0013813 | 0.0003462 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1040-18_0_6_load_8 | 10 | 0.0022081 | 0.0005534 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1040-18_0_6_load_253 | 11 | 0.0013899 | 0.00034835 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1040-18_0_6_load_252 | 12 | 0.0018718 | 0.00046911 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1040-18_0_6_load_9 | 13 | 0.0019651 | 0.00049249 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1040-18_0_6_load_11 | 15 | 0.0028063 | 0.00070333 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1040-18_0_6_load_251 | 17 | 0.0024335 | 0.0006099 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1040-18_0_6_load_189 | 18 | 0.0021994 | 0.00055122 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1040-18_0_6_load_187 | 20 | 0.0027224 | 0.00068231 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1040-18_0_6_load_212 | 23 | 0.0047742 | 0.0011965 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1040-18_0_6_load_275 | 25 | 0.0030164 | 0.00075597 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1040-18_0_6_load_148 | 27 | 0.004022 | 0.001008 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1040-18_0_6_load_143 | 28 | 0.0052596 | 0.0013182 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1040-18_0_6_load_182 | 30 | 0.00049156 | 0.0001232 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1040-18_0_6_load_179 | 31 | 0.0014057 | 0.0003523 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1040-18_0_6_load_146 | 32 | 0.0015576 | 0.00039036 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1040-18_0_6_load_173 | 33 | 0.0035121 | 0.00088023 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1040-18_0_6_load_15 | 35 | 0.0035716 | 0.00089514 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1040-18_0_6_load_17 | 37 | 0.0045744 | 0.0011464 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1040-18_0_6_load_273 | 38 | 0.0029379 | 0.00073631 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1040-18_0_6_load_18 | 39 | 0.0048376 | 0.0012124 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1040-18_0_6_load_166 | 41 | 0.0029348 | 0.00073552 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1040-18_0_6_load_19 | 43 | 0.003168 | 0.00079398 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1040-18_0_6_load_127 | 48 | 0.0020331 | 0.00050955 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1040-18_0_6_load_131 | 50 | 0.0016211 | 0.00040629 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1040-18_0_6_load_130 | 52 | 0.0084432 | 0.0021161 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1040-18_0_6_load_132 | 53 | 0.003962 | 0.00099297 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1040-18_0_6_load_109 | 54 | 0.0035839 | 0.00089821 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1040-18_0_6_load_134 | 56 | 0.003123 | 0.00078271 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1040-18_0_6_load_133 | 57 | 0.0048974 | 0.0012274 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1040-18_0_6_load_105 | 60 | 0.0020773 | 0.00052063 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1040-18_0_6_load_106 | 62 | 0.0026593 | 0.00066649 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1040-18_0_6_load_107 | 63 | 0.001645 | 0.00041228 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1040-18_0_6_load_100 | 66 | 0.0042078 | 0.0010546 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1040-18_0_6_load_114 | 68 | 0.0049567 | 0.0012423 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1040-18_0_6_load_128 | 69 | 0.0014696 | 0.00036832 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1040-18_0_6_load_34 | 70 | 0.0020276 | 0.00050815 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1040-18_0_6_load_32 | 71 | 0.0021114 | 0.00052917 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1040-18_0_6_load_89 | 74 | 0.01135 | 0.0028446 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1040-18_0_6_load_85 | 75 | 0.0084216 | 0.0021106 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1040-18_0_6_load_99 | 76 | 0.0036865 | 0.00092393 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1040-18_0_6_load_97 | 77 | 0.0039174 | 0.00098178 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1040-18_0_6_load_112 | 79 | 0.0057226 | 0.0014342 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1040-18_0_6_load_110 | 80 | 0.0035624 | 0.00089282 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1040-18_0_6_load_113 | 81 | 0.001913 | 0.00047945 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1040-18_0_6_load_115 | 82 | 0.0014599 | 0.00036588 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1040-18_0_6_load_101 | 83 | 0.004047 | 0.0010143 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1040-18_0_6_load_37 | 86 | 0.0012268 | 0.00030747 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1040-18_0_6_load_302 | 87 | 0.0012839 | 0.00032178 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1040-18_0_6_load_267 | 90 | 0.0020216 | 0.00050665 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1040-18_0_6_load_261 | 91 | 0.0010341 | 0.00025918 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1040-18_0_6_load_299 | 92 | 0.0014888 | 0.00037312 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1040-18_0_6_load_38 | 94 | 0.0060267 | 0.0015104 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1040-18_0_6_load_72 | 101 | 0.0027315 | 0.00068459 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1040-18_0_6_load_304 | 102 | 0.0025843 | 0.00064768 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1040-18_0_6_load_305 | 103 | 0.0028265 | 0.00070838 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1040-18_0_6_load_289 | 104 | 0.00072843 | 0.00018256 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1040-18_0_6_load_303 | 105 | 0.0031358 | 0.0007859 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1040-18_0_6_load_68 | 106 | 0.0012256 | 0.00030717 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1040-18_0_6_load_84 | 109 | 0.00078499 | 0.00019674 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1040-18_0_6_load_256 | 110 | 0.00054393 | 0.00013632 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1040-18_0_6_load_290 | 112 | 0.00085951 | 0.00021541 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1040-18_0_6_load_292 | 113 | 0.00083464 | 0.00020918 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1040-18_0_6_load_294 | 116 | 0.00070785 | 0.0001774 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1040-18_0_6_load_74 | 119 | 0.00082583 | 0.00020697 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1040-18_0_6_load_71 | 120 | 0.013294 | 0.0033318 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1040-18_0_6_load_70 | 121 | 0.0027826 | 0.00069738 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1040-18_0_6_load_63 | 122 | 0.0010702 | 0.00026821 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1040-18_0_6_load_255 | 125 | 0.00052012 | 0.00013036 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1040-18_0_6_load_276 | 126 | 0.0028968 | 0.00072601 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1040-18_0_6_load_83 | 127 | 0.00086014 | 0.00021557 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1040-18_0_6_load_291 | 128 | 0.00083364 | 0.00020893 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1040-18_0_6_load_284 | 129 | 0.00070728 | 0.00017726 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1040-18_0_6_load_280 | 130 | 0.00070866 | 0.00017761 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1040-18_0_6_load_51 | 131 | 0.00054893 | 0.00013757 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1040-18_0_6_load_52 | 132 | 0.00083852 | 0.00021015 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1040-18_0_6_load_55 | 134 | 0.0070437 | 0.0017653 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1040-18_0_6_load_56 | 135 | 0.0017809 | 0.00044635 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1040-18_0_6_load_73 | 136 | 0.005352 | 0.0013413 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1040-18_0_6_load_75 | 137 | 0.0014641 | 0.00036693 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1040-18_0_6_load_76 | 138 | 0.0016117 | 0.00040392 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1040-18_0_6_load_57 | 139 | 0.0017709 | 0.00044383 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1040-18_0_6_load_58 | 140 | 0.0010429 | 0.00026137 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1040-18_0_6_load_60 | 142 | 0.0015608 | 0.00039118 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1040-18_0_6_load_61 | 143 | 0.0019913 | 0.00049906 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1040-18_0_6_load_65 | 145 | 0.0029897 | 0.0007493 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1040-18_0_6_load_66 | 146 | 0.0022832 | 0.00057222 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1040-18_0_6_load_94 | 147 | 0.00074344 | 0.00018632 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1040-18_0_6_load_246 | 148 | 0.0015437 | 0.00038688 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1040-18_0_6_load_257 | 149 | 0.0014594 | 0.00036575 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1040-18_0_6_load_77 | 150 | 0.00076059 | 0.00019062 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1040-18_0_6_load_78 | 151 | 0.00083297 | 0.00020876 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1040-18_0_6_load_79 | 152 | 0.00076067 | 0.00019064 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1040-18_0_6_load_80 | 153 | 0.0008317 | 0.00020844 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1040-18_0_6_load_81 | 154 | 0.00078433 | 0.00019657 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_1040-18_0_6_load_86 | 155 | 0.0090909 | 0.0022784 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_1040-18_0_6_load_88 | 156 | 0.0099186 | 0.0024858 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_1040-18_0_6_load_95 | 157 | 0.0025398 | 0.00063653 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_1040-18_0_6_load_98 | 159 | 0.0028139 | 0.00070523 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_1040-18_0_6_load_102 | 160 | 0.0053367 | 0.0013375 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_1040-18_0_6_load_103 | 161 | 0.0020324 | 0.00050936 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_1040-18_0_6_load_104 | 162 | 0.0018042 | 0.00045217 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_1040-18_0_6_load_279 | 163 | 0.0018084 | 0.00045323 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_1040-18_0_6_load_116 | 164 | 0.0031641 | 0.00079301 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_1040-18_0_6_load_135 | 165 | 0.0037599 | 0.00094232 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_1040-18_0_6_load_111 | 166 | 0.003941 | 0.0009877 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_1040-18_0_6_load_136 | 167 | 0.0068908 | 0.001727 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_1040-18_0_6_load_117 | 168 | 0.0038602 | 0.00096745 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_1040-18_0_6_load_123 | 169 | 0.00050819 | 0.00012736 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_1040-18_0_6_load_121 | 170 | 0.00047773 | 0.00011973 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_1040-18_0_6_load_118 | 171 | 0.0019371 | 0.00048549 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_1040-18_0_6_load_119 | 172 | 0.0060726 | 0.0015219 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_1040-18_0_6_load_120 | 173 | 0.0033766 | 0.00084627 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_1040-18_0_6_load_125 | 174 | 0.00077348 | 0.00019385 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_1040-18_0_6_load_126 | 175 | 0.0015403 | 0.00038603 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_1040-18_0_6_load_122 | 176 | 0.0071771 | 0.0017988 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_1040-18_0_6_load_124 | 177 | 0.00076104 | 0.00019073 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_1040-18_0_6_load_232 | 178 | 0.0026026 | 0.00065228 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_1040-18_0_6_load_160 | 180 | 0.0013737 | 0.00034428 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_1040-18_0_6_load_184 | 181 | 0.0015668 | 0.00039269 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_1040-18_0_6_load_137 | 184 | 0.0030051 | 0.00075315 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_1040-18_0_6_load_138 | 185 | 0.0025551 | 0.00064036 | 0 | 0 |  | 1 | TRUE | wye
128 | LV_1040-18_0_6_load_274 | 187 | 0.0087676 | 0.0021974 | 0 | 0 |  | 1 | TRUE | wye
129 | LV_1040-18_0_6_load_141 | 189 | 0.0010989 | 0.00027542 | 0 | 0 |  | 1 | TRUE | wye
130 | LV_1040-18_0_6_load_142 | 190 | 0.0021482 | 0.00053839 | 0 | 0 |  | 1 | TRUE | wye
131 | LV_1040-18_0_6_load_144 | 193 | 0.0014718 | 0.00036888 | 0 | 0 |  | 1 | TRUE | wye
132 | LV_1040-18_0_6_load_151 | 194 | 0.0041629 | 0.0010433 | 0 | 0 |  | 1 | TRUE | wye
133 | LV_1040-18_0_6_load_152 | 195 | 0.0028377 | 0.00071119 | 0 | 0 |  | 1 | TRUE | wye
134 | LV_1040-18_0_6_load_213 | 196 | 0.0072054 | 0.0018059 | 0 | 0 |  | 1 | TRUE | wye
135 | LV_1040-18_0_6_load_180 | 197 | 0.0016059 | 0.00040248 | 0 | 0 |  | 1 | TRUE | wye
136 | LV_1040-18_0_6_load_153 | 198 | 0.0024397 | 0.00061145 | 0 | 0 |  | 1 | TRUE | wye
137 | LV_1040-18_0_6_load_238 | 199 | 0.0021598 | 0.00054129 | 0 | 0 |  | 1 | TRUE | wye
138 | LV_1040-18_0_6_load_154 | 200 | 0.0014641 | 0.00036693 | 0 | 0 |  | 1 | TRUE | wye
139 | LV_1040-18_0_6_load_158 | 204 | 0.0028514 | 0.00071463 | 0 | 0 |  | 1 | TRUE | wye
140 | LV_1040-18_0_6_load_159 | 205 | 0.0014741 | 0.00036945 | 0 | 0 |  | 1 | TRUE | wye
141 | LV_1040-18_0_6_load_236 | 207 | 0.0014341 | 0.00035942 | 0 | 0 |  | 1 | TRUE | wye
142 | LV_1040-18_0_6_load_278 | 208 | 0.0014452 | 0.0003622 | 0 | 0 |  | 1 | TRUE | wye
143 | LV_1040-18_0_6_load_217 | 209 | 0.001609 | 0.00040326 | 0 | 0 |  | 1 | TRUE | wye
144 | LV_1040-18_0_6_load_203 | 210 | 0.0015436 | 0.00038687 | 0 | 0 |  | 1 | TRUE | wye
145 | LV_1040-18_0_6_load_183 | 211 | 0.0016804 | 0.00042116 | 0 | 0 |  | 1 | TRUE | wye
146 | LV_1040-18_0_6_load_168 | 212 | 0.00094344 | 0.00023645 | 0 | 0 |  | 1 | TRUE | wye
147 | LV_1040-18_0_6_load_220 | 213 | 0.0008876 | 0.00022245 | 0 | 0 |  | 1 | TRUE | wye
148 | LV_1040-18_0_6_load_163 | 214 | 0.0045208 | 0.001133 | 0 | 0 |  | 1 | TRUE | wye
149 | LV_1040-18_0_6_load_164 | 215 | 0.0022204 | 0.00055649 | 0 | 0 |  | 1 | TRUE | wye
150 | LV_1040-18_0_6_load_165 | 216 | 0.0022192 | 0.00055618 | 0 | 0 |  | 1 | TRUE | wye
151 | LV_1040-18_0_6_load_167 | 217 | 0.006707 | 0.0016809 | 0 | 0 |  | 1 | TRUE | wye
152 | LV_1040-18_0_6_load_248 | 218 | 0.0062427 | 0.0015646 | 0 | 0 |  | 1 | TRUE | wye
153 | LV_1040-18_0_6_load_247 | 219 | 0.0021538 | 0.00053978 | 0 | 0 |  | 1 | TRUE | wye
154 | LV_1040-18_0_6_load_221 | 220 | 0.00068973 | 0.00017286 | 0 | 0 |  | 1 | TRUE | wye
155 | LV_1040-18_0_6_load_169 | 221 | 0.0072086 | 0.0018067 | 0 | 0 |  | 1 | TRUE | wye
156 | LV_1040-18_0_6_load_170 | 222 | 0.0028507 | 0.00071446 | 0 | 0 |  | 1 | TRUE | wye
157 | LV_1040-18_0_6_load_172 | 223 | 0.0031518 | 0.00078992 | 0 | 0 |  | 1 | TRUE | wye
158 | LV_1040-18_0_6_load_277 | 224 | 0.0029574 | 0.00074118 | 0 | 0 |  | 1 | TRUE | wye
159 | LV_1040-18_0_6_load_174 | 225 | 0.0030617 | 0.00076734 | 0 | 0 |  | 1 | TRUE | wye
160 | LV_1040-18_0_6_load_176 | 227 | 0.0027556 | 0.00069062 | 0 | 0 |  | 1 | TRUE | wye
161 | LV_1040-18_0_6_load_177 | 228 | 0.0013279 | 0.00033279 | 0 | 0 |  | 1 | TRUE | wye
162 | LV_1040-18_0_6_load_178 | 229 | 0.0021227 | 0.00053199 | 0 | 0 |  | 1 | TRUE | wye
163 | LV_1040-18_0_6_load_243 | 230 | 0.0021558 | 0.0005403 | 0 | 0 |  | 1 | TRUE | wye
164 | LV_1040-18_0_6_load_270 | 231 | 0.0021238 | 0.00053228 | 0 | 0 |  | 1 | TRUE | wye
165 | LV_1040-18_0_6_load_244 | 232 | 0.0013263 | 0.00033241 | 0 | 0 |  | 1 | TRUE | wye
166 | LV_1040-18_0_6_load_269 | 233 | 0.0035783 | 0.0008968 | 0 | 0 |  | 1 | TRUE | wye
167 | LV_1040-18_0_6_load_181 | 234 | 0.0015202 | 0.00038101 | 0 | 0 |  | 1 | TRUE | wye
168 | LV_1040-18_0_6_load_245 | 235 | 0.0015445 | 0.00038708 | 0 | 0 |  | 1 | TRUE | wye
169 | LV_1040-18_0_6_load_254 | 236 | 0.0015437 | 0.00038688 | 0 | 0 |  | 1 | TRUE | wye
170 | LV_1040-18_0_6_load_185 | 237 | 0.0021271 | 0.00053311 | 0 | 0 |  | 1 | TRUE | wye
171 | LV_1040-18_0_6_load_186 | 238 | 0.00218 | 0.00054635 | 0 | 0 |  | 1 | TRUE | wye
172 | LV_1040-18_0_6_load_188 | 239 | 0.0025258 | 0.00063302 | 0 | 0 |  | 1 | TRUE | wye
173 | LV_1040-18_0_6_load_222 | 240 | 0.001312 | 0.00032882 | 0 | 0 |  | 1 | TRUE | wye
174 | LV_1040-18_0_6_load_226 | 241 | 0.0013439 | 0.00033682 | 0 | 0 |  | 1 | TRUE | wye
175 | LV_1040-18_0_6_load_190 | 242 | 0.0097445 | 0.0024422 | 0 | 0 |  | 1 | TRUE | wye
176 | LV_1040-18_0_6_load_191 | 243 | 0.00094697 | 0.00023733 | 0 | 0 |  | 1 | TRUE | wye
177 | LV_1040-18_0_6_load_192 | 244 | 0.0013722 | 0.00034391 | 0 | 0 |  | 1 | TRUE | wye
178 | LV_1040-18_0_6_load_193 | 245 | 0.0014981 | 0.00037547 | 0 | 0 |  | 1 | TRUE | wye
179 | LV_1040-18_0_6_load_225 | 247 | 0.0014334 | 0.00035925 | 0 | 0 |  | 1 | TRUE | wye
180 | LV_1040-18_0_6_load_271 | 248 | 0.0034198 | 0.00085709 | 0 | 0 |  | 1 | TRUE | wye
181 | LV_1040-18_0_6_load_272 | 249 | 0.0021673 | 0.00054319 | 0 | 0 |  | 1 | TRUE | wye
182 | LV_1040-18_0_6_load_241 | 250 | 0.00068973 | 0.00017286 | 0 | 0 |  | 1 | TRUE | wye
183 | LV_1040-18_0_6_load_210 | 251 | 0.0021673 | 0.00054319 | 0 | 0 |  | 1 | TRUE | wye
184 | LV_1040-18_0_6_load_195 | 252 | 0.0025582 | 0.00064114 | 0 | 0 |  | 1 | TRUE | wye
185 | LV_1040-18_0_6_load_196 | 253 | 0.0029072 | 0.00072862 | 0 | 0 |  | 1 | TRUE | wye
186 | LV_1040-18_0_6_load_197 | 254 | 0.0025593 | 0.00064142 | 0 | 0 |  | 1 | TRUE | wye
187 | LV_1040-18_0_6_load_198 | 255 | 0.0030605 | 0.00076703 | 0 | 0 |  | 1 | TRUE | wye
188 | LV_1040-18_0_6_load_199 | 256 | 0.0025582 | 0.00064114 | 0 | 0 |  | 1 | TRUE | wye
189 | LV_1040-18_0_6_load_229 | 257 | 0.0024475 | 0.00061339 | 0 | 0 |  | 1 | TRUE | wye
190 | LV_1040-18_0_6_load_242 | 258 | 0.0021655 | 0.00054272 | 0 | 0 |  | 1 | TRUE | wye
191 | LV_1040-18_0_6_load_228 | 259 | 0.0024455 | 0.0006129 | 0 | 0 |  | 1 | TRUE | wye
192 | LV_1040-18_0_6_load_200 | 261 | 0.0014092 | 0.00035318 | 0 | 0 |  | 1 | TRUE | wye
193 | LV_1040-18_0_6_load_201 | 262 | 0.0014599 | 0.00036589 | 0 | 0 |  | 1 | TRUE | wye
194 | LV_1040-18_0_6_load_202 | 263 | 0.0028773 | 0.00072113 | 0 | 0 |  | 1 | TRUE | wye
195 | LV_1040-18_0_6_load_204 | 264 | 0.0048971 | 0.0012273 | 0 | 0 |  | 1 | TRUE | wye
196 | LV_1040-18_0_6_load_240 | 266 | 0.0013456 | 0.00033724 | 0 | 0 |  | 1 | TRUE | wye
197 | LV_1040-18_0_6_load_205 | 267 | 0.0042456 | 0.001064 | 0 | 0 |  | 1 | TRUE | wye
198 | LV_1040-18_0_6_load_206 | 268 | 0.0036552 | 0.00091608 | 0 | 0 |  | 1 | TRUE | wye
199 | LV_1040-18_0_6_load_208 | 270 | 0.00090237 | 0.00022616 | 0 | 0 |  | 1 | TRUE | wye
200 | LV_1040-18_0_6_load_223 | 272 | 0.0053842 | 0.0013494 | 0 | 0 |  | 1 | TRUE | wye
201 | LV_1040-18_0_6_load_296 | 273 | 0.0033172 | 0.00083136 | 0 | 0 |  | 1 | TRUE | wye
202 | LV_1040-18_0_6_load_224 | 274 | 0.0016728 | 0.00041925 | 0 | 0 |  | 1 | TRUE | wye
203 | LV_1040-18_0_6_load_295 | 275 | 0.0058821 | 0.0014742 | 0 | 0 |  | 1 | TRUE | wye
204 | LV_1040-18_0_6_load_214 | 276 | 0.0077348 | 0.0019385 | 0 | 0 |  | 1 | TRUE | wye
205 | LV_1040-18_0_6_load_237 | 277 | 0.007574 | 0.0018982 | 0 | 0 |  | 1 | TRUE | wye
206 | LV_1040-18_0_6_load_215 | 278 | 0.0013932 | 0.00034918 | 0 | 0 |  | 1 | TRUE | wye
207 | LV_1040-18_0_6_load_216 | 279 | 0.0014594 | 0.00036576 | 0 | 0 |  | 1 | TRUE | wye
208 | LV_1040-18_0_6_load_218 | 280 | 0.0014599 | 0.0003659 | 0 | 0 |  | 1 | TRUE | wye
209 | LV_1040-18_0_6_load_227 | 281 | 0.002444 | 0.00061252 | 0 | 0 |  | 1 | TRUE | wye
210 | LV_1040-18_0_6_load_230 | 282 | 0.0015397 | 0.00038589 | 0 | 0 |  | 1 | TRUE | wye
211 | LV_1040-18_0_6_load_233 | 283 | 0.0014595 | 0.00036579 | 0 | 0 |  | 1 | TRUE | wye
212 | LV_1040-18_0_6_load_301 | 285 | 0.003121 | 0.00078219 | 0 | 0 |  | 1 | TRUE | wye
213 | LV_1040-18_0_6_load_297 | 286 | 0.0023216 | 0.00058185 | 0 | 0 |  | 1 | TRUE | wye
214 | LV_1040-18_0_6_load_300 | 287 | 0.0044788 | 0.0011225 | 0 | 0 |  | 1 | TRUE | wye
215 | LV_1040-18_0_6_load_250 | 288 | 0.0012987 | 0.00032549 | 0 | 0 |  | 1 | TRUE | wye
216 | LV_1040-18_0_6_load_249 | 289 | 0.0021513 | 0.00053916 | 0 | 0 |  | 1 | TRUE | wye
217 | LV_1040-18_0_6_load_298 | 290 | 0.0013997 | 0.00035081 | 0 | 0 |  | 1 | TRUE | wye
218 | LV_1040-18_0_6_load_281 | 291 | 0.00070866 | 0.00017761 | 0 | 0 |  | 1 | TRUE | wye
219 | LV_1040-18_0_6_load_283 | 292 | 0.00072211 | 0.00018098 | 0 | 0 |  | 1 | TRUE | wye
220 | LV_1040-18_0_6_load_293 | 293 | 0.00072133 | 0.00018078 | 0 | 0 |  | 1 | TRUE | wye
221 | LV_1040-18_0_6_load_288 | 294 | 0.0007285 | 0.00018258 | 0 | 0 |  | 1 | TRUE | wye
222 | LV_1040-18_0_6_load_285 | 295 | 0.0007061 | 0.00017696 | 0 | 0 |  | 1 | TRUE | wye
223 | LV_1040-18_0_6_load_287 | 296 | 0.00070567 | 0.00017686 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 58 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1040-18_0_6_line_0 |  | 0 | 1 | 0.19474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1040-18_0_6_line_1 |  | 0 | 2 | 0.0018283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1040-18_0_6_line_2 |  | 1 | 3 | 0.002161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1040-18_0_6_line_3 |  | 3 | 4 | 0.13899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1040-18_0_6_line_4 |  | 3 | 5 | 0.073426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1040-18_0_6_line_5 |  | 4 | 6 | 0.00016974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1040-18_0_6_line_6 |  | 6 | 7 | 5.7826e-07 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1040-18_0_6_line_7 |  | 7 | 212 | 0.013525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1040-18_0_6_line_8 |  | 8 | 9 | 0.067964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1040-18_0_6_line_9 |  | 9 | 10 | 0.06904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1040-18_0_6_line_10 |  | 10 | 11 | 0.0069605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1040-18_0_6_line_11 |  | 11 | 12 | 0.01472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1040-18_0_6_line_12 |  | 12 | 274 | 0.0091762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1040-18_0_6_line_13 |  | 13 | 14 | 0.10677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1040-18_0_6_line_14 |  | 13 | 15 | 0.018192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1040-18_0_6_line_15 |  | 14 | 16 | 0.22412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1040-18_0_6_line_16 |  | 16 | 17 | 0.021353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1040-18_0_6_line_17 |  | 16 | 18 | 0.016948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1040-18_0_6_line_18 |  | 17 | 19 | 0.018768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1040-18_0_6_line_19 |  | 18 | 20 | 0.014948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1040-18_0_6_line_20 |  | 19 | 21 | 0.028061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1040-18_0_6_line_21 |  | 20 | 237 | 0.0052998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1040-18_0_6_line_22 |  | 21 | 27 | 0.017667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1040-18_0_6_line_23 |  | 21 | 28 | 0.023031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1040-18_0_6_line_24 |  | 21 | 22 | 0.038421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1040-18_0_6_line_25 |  | 22 | 23 | 0.021081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1040-18_0_6_line_26 |  | 23 | 196 | 0.019353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1040-18_0_6_line_27 |  | 24 | 25 | 0.035378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1040-18_0_6_line_28 |  | 24 | 26 | 0.030503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1040-18_0_6_line_29 |  | 25 | 126 | 0.005823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1040-18_0_6_line_30 |  | 26 | 109 | 0.012185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1040-18_0_6_line_31 |  | 26 | 110 | 0.036663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1040-18_0_6_line_32 |  | 27 | 194 | 0.01723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1040-18_0_6_line_33 |  | 28 | 193 | 0.022834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1040-18_0_6_line_34 |  | 29 | 30 | 0.02074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1040-18_0_6_line_35 |  | 29 | 31 | 0.013825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1040-18_0_6_line_36 |  | 29 | 32 | 0.020445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1040-18_0_6_line_37 |  | 30 | 125 | 0.0026323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1040-18_0_6_line_38 |  | 31 | 197 | 0.011376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1040-18_0_6_line_39 |  | 32 | 193 | 0.002662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1040-18_0_6_line_40 |  | 33 | 34 | 0.088816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1040-18_0_6_line_41 |  | 34 | 221 | 0.032309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1040-18_0_6_line_42 |  | 35 | 36 | 0.040246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1040-18_0_6_line_43 |  | 36 | 37 | 0.0056119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1040-18_0_6_line_44 |  | 37 | 38 | 0.024374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1040-18_0_6_line_45 |  | 38 | 41 | 0.011577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1040-18_0_6_line_46 |  | 39 | 40 | 0.034852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1040-18_0_6_line_47 |  | 40 | 42 | 0.004442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1040-18_0_6_line_48 |  | 40 | 43 | 0.10131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1040-18_0_6_line_49 |  | 41 | 215 | 0.020089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1040-18_0_6_line_50 |  | 42 | 44 | 0.014417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1040-18_0_6_line_51 |  | 44 | 45 | 0.002837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1040-18_0_6_line_52 |  | 45 | 55 | 0.009362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1040-18_0_6_line_53 |  | 46 | 47 | 0.021601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1040-18_0_6_line_54 |  | 46 | 48 | 0.0088633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1040-18_0_6_line_55 |  | 47 | 70 | 0.020625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1040-18_0_6_line_56 |  | 47 | 71 | 0.044804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1040-18_0_6_line_57 |  | 48 | 69 | 0.0072467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1040-18_0_6_line_58 |  | 49 | 50 | 0.024911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
59 | LV_1040-18_0_6_line_59 |  | 49 | 51 | 0.0081703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
60 | LV_1040-18_0_6_line_60 |  | 49 | 52 | 0.013444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1040-18_0_6_line_61 |  | 50 | 72 | 0.0061372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
62 | LV_1040-18_0_6_line_62 |  | 51 | 53 | 0.015819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
63 | LV_1040-18_0_6_line_63 |  | 51 | 54 | 0.0019408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
64 | LV_1040-18_0_6_line_64 |  | 53 | 57 | 0.025998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
65 | LV_1040-18_0_6_line_65 |  | 54 | 58 | 0.013988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
66 | LV_1040-18_0_6_line_66 |  | 55 | 56 | 0.047104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
67 | LV_1040-18_0_6_line_67 |  | 55 | 57 | 0.017045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
68 | LV_1040-18_0_6_line_68 |  | 56 | 78 | 0.014368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
69 | LV_1040-18_0_6_line_69 |  | 58 | 59 | 0.017682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1040-18_0_6_line_70 |  | 58 | 60 | 0.038101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1040-18_0_6_line_71 |  | 59 | 79 | 0.015556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1040-18_0_6_line_72 |  | 59 | 80 | 0.013348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1040-18_0_6_line_73 |  | 60 | 61 | 0.01305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1040-18_0_6_line_74 |  | 61 | 62 | 0.018316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1040-18_0_6_line_75 |  | 61 | 63 | 0.031324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1040-18_0_6_line_76 |  | 62 | 81 | 0.037437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1040-18_0_6_line_77 |  | 63 | 82 | 0.0074413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1040-18_0_6_line_78 |  | 64 | 65 | 0.0082214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1040-18_0_6_line_79 |  | 64 | 66 | 0.082135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1040-18_0_6_line_80 |  | 65 | 67 | 0.025377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1040-18_0_6_line_81 |  | 65 | 68 | 0.017907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1040-18_0_6_line_82 |  | 66 | 83 | 0.02495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1040-18_0_6_line_83 |  | 67 | 76 | 0.02677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1040-18_0_6_line_84 |  | 67 | 77 | 0.049863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1040-18_0_6_line_85 |  | 67 | 73 | 0.031822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1040-18_0_6_line_86 |  | 68 | 81 | 0.017456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1040-18_0_6_line_87 |  | 70 | 84 | 0.019875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1040-18_0_6_line_88 |  | 72 | 180 | 0.0066174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
89 | LV_1040-18_0_6_line_89 |  | 72 | 181 | 0.011416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1040-18_0_6_line_90 |  | 73 | 74 | 0.022219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1040-18_0_6_line_91 |  | 73 | 75 | 0.023539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1040-18_0_6_line_92 |  | 74 | 157 | 0.017399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1040-18_0_6_line_93 |  | 75 | 155 | 0.034597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1040-18_0_6_line_94 |  | 77 | 159 | 0.013687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1040-18_0_6_line_95 |  | 78 | 182 | 0.021384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1040-18_0_6_line_96 |  | 78 | 183 | 0.02541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1040-18_0_6_line_97 |  | 79 | 165 | 0.030658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1040-18_0_6_line_98 |  | 80 | 166 | 0.013676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1040-18_0_6_line_99 |  | 82 | 164 | 0.0068486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1040-18_0_6_line_100 |  | 83 | 160 | 0.024017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1040-18_0_6_line_101 |  | 84 | 85 | 0.009308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1040-18_0_6_line_102 |  | 84 | 86 | 0.006314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1040-18_0_6_line_103 |  | 85 | 87 | 0.012582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1040-18_0_6_line_104 |  | 85 | 88 | 0.02496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1040-18_0_6_line_105 |  | 85 | 89 | 0.017384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1040-18_0_6_line_106 |  | 88 | 90 | 0.018969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1040-18_0_6_line_107 |  | 88 | 91 | 0.0093425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1040-18_0_6_line_108 |  | 89 | 92 | 0.007667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1040-18_0_6_line_109 |  | 89 | 93 | 0.004145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1040-18_0_6_line_110 |  | 90 | 191 | 0.010791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1040-18_0_6_line_111 |  | 91 | 189 | 0.0068699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1040-18_0_6_line_112 |  | 93 | 290 | 0.007118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1040-18_0_6_line_113 |  | 93 | 188 | 0.012873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1040-18_0_6_line_114 |  | 94 | 95 | 0.014944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1040-18_0_6_line_115 |  | 94 | 96 | 0.016643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1040-18_0_6_line_116 |  | 95 | 97 | 0.003091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1040-18_0_6_line_117 |  | 95 | 98 | 0.025291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1040-18_0_6_line_118 |  | 96 | 99 | 0.003291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1040-18_0_6_line_119 |  | 97 | 100 | 0.020904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1040-18_0_6_line_120 |  | 97 | 101 | 0.033094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_1040-18_0_6_line_121 |  | 98 | 105 | 0.006104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_1040-18_0_6_line_122 |  | 98 | 106 | 0.025025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_1040-18_0_6_line_123 |  | 99 | 104 | 0.015823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_1040-18_0_6_line_124 |  | 100 | 102 | 0.00695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_1040-18_0_6_line_125 |  | 100 | 103 | 0.004298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_1040-18_0_6_line_126 |  | 101 | 117 | 0.014777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_1040-18_0_6_line_127 |  | 104 | 118 | 0.011038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_1040-18_0_6_line_128 |  | 106 | 119 | 0.020548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_1040-18_0_6_line_129 |  | 106 | 107 | 0.002644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_1040-18_0_6_line_130 |  | 107 | 108 | 0.009416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_1040-18_0_6_line_131 |  | 108 | 120 | 0.013841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_1040-18_0_6_line_132 |  | 108 | 121 | 0.013605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_1040-18_0_6_line_133 |  | 109 | 124 | 0.016133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_1040-18_0_6_line_134 |  | 110 | 125 | 0.019022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_1040-18_0_6_line_135 |  | 111 | 112 | 0.015176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_1040-18_0_6_line_136 |  | 111 | 113 | 0.010629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_1040-18_0_6_line_137 |  | 112 | 127 | 0.008862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_1040-18_0_6_line_138 |  | 113 | 128 | 0.0088357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_1040-18_0_6_line_139 |  | 114 | 115 | 0.024243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_1040-18_0_6_line_140 |  | 114 | 116 | 0.0112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_1040-18_0_6_line_141 |  | 115 | 129 | 0.015684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_1040-18_0_6_line_142 |  | 115 | 130 | 0.027285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_1040-18_0_6_line_143 |  | 117 | 136 | 0.016189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_1040-18_0_6_line_144 |  | 117 | 132 | 0.0097871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_1040-18_0_6_line_145 |  | 118 | 294 | 0.017916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_1040-18_0_6_line_146 |  | 118 | 295 | 0.017795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_1040-18_0_6_line_147 |  | 119 | 144 | 0.025053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_1040-18_0_6_line_148 |  | 120 | 147 | 0.0023046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_1040-18_0_6_line_149 |  | 122 | 123 | 0.011997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_1040-18_0_6_line_150 |  | 123 | 145 | 0.04075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_1040-18_0_6_line_151 |  | 123 | 146 | 0.022592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_1040-18_0_6_line_152 |  | 123 | 144 | 0.002652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_1040-18_0_6_line_153 |  | 124 | 127 | 0.020324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_1040-18_0_6_line_154 |  | 124 | 154 | 0.015925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
155 | LV_1040-18_0_6_line_155 |  | 126 | 224 | 0.0057702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
156 | LV_1040-18_0_6_line_156 |  | 129 | 294 | 0.0091082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
157 | LV_1040-18_0_6_line_157 |  | 130 | 291 | 0.0088086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
158 | LV_1040-18_0_6_line_158 |  | 131 | 132 | 0.018371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
159 | LV_1040-18_0_6_line_159 |  | 131 | 133 | 0.017993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
160 | LV_1040-18_0_6_line_160 |  | 133 | 134 | 0.015343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
161 | LV_1040-18_0_6_line_161 |  | 133 | 135 | 0.0051656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
162 | LV_1040-18_0_6_line_162 |  | 135 | 137 | 0.015564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
163 | LV_1040-18_0_6_line_163 |  | 137 | 138 | 0.017658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
164 | LV_1040-18_0_6_line_164 |  | 138 | 148 | 0.0037993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
165 | LV_1040-18_0_6_line_165 |  | 139 | 140 | 0.022294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
166 | LV_1040-18_0_6_line_166 |  | 139 | 141 | 0.019803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
167 | LV_1040-18_0_6_line_167 |  | 140 | 142 | 0.0086364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
168 | LV_1040-18_0_6_line_168 |  | 141 | 143 | 0.008847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
169 | LV_1040-18_0_6_line_169 |  | 141 | 144 | 0.001925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
170 | LV_1040-18_0_6_line_170 |  | 148 | 149 | 0.0054104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
171 | LV_1040-18_0_6_line_171 |  | 149 | 206 | 0.018565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
172 | LV_1040-18_0_6_line_172 |  | 150 | 151 | 0.025912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
173 | LV_1040-18_0_6_line_173 |  | 150 | 152 | 0.0083097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
174 | LV_1040-18_0_6_line_174 |  | 151 | 153 | 0.0082624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
175 | LV_1040-18_0_6_line_175 |  | 152 | 154 | 0.0097978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
176 | LV_1040-18_0_6_line_176 |  | 155 | 156 | 0.03774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
177 | LV_1040-18_0_6_line_177 |  | 157 | 158 | 0.060399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
178 | LV_1040-18_0_6_line_178 |  | 158 | 161 | 0.020165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
179 | LV_1040-18_0_6_line_179 |  | 158 | 162 | 0.042668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
180 | LV_1040-18_0_6_line_180 |  | 162 | 163 | 0.027216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
181 | LV_1040-18_0_6_line_181 |  | 164 | 168 | 0.0046772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
182 | LV_1040-18_0_6_line_182 |  | 165 | 167 | 0.011785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
183 | LV_1040-18_0_6_line_183 |  | 168 | 169 | 0.014925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
184 | LV_1040-18_0_6_line_184 |  | 169 | 170 | 0.0013809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
185 | LV_1040-18_0_6_line_185 |  | 170 | 176 | 0.0059445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
186 | LV_1040-18_0_6_line_186 |  | 171 | 172 | 0.0050998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
187 | LV_1040-18_0_6_line_187 |  | 172 | 173 | 0.021012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
188 | LV_1040-18_0_6_line_188 |  | 173 | 174 | 0.0093472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
189 | LV_1040-18_0_6_line_189 |  | 174 | 175 | 0.0026176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
190 | LV_1040-18_0_6_line_190 |  | 175 | 177 | 0.0097142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
191 | LV_1040-18_0_6_line_191 |  | 176 | 177 | 0.012509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
192 | LV_1040-18_0_6_line_192 |  | 178 | 179 | 0.012893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
193 | LV_1040-18_0_6_line_193 |  | 179 | 283 | 0.016965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
194 | LV_1040-18_0_6_line_194 |  | 179 | 284 | 0.024658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
195 | LV_1040-18_0_6_line_195 |  | 179 | 183 | 0.0085745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
196 | LV_1040-18_0_6_line_196 |  | 179 | 282 | 0.030811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
197 | LV_1040-18_0_6_line_197 |  | 180 | 202 | 0.015946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
198 | LV_1040-18_0_6_line_198 |  | 181 | 211 | 0.00031102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
199 | LV_1040-18_0_6_line_199 |  | 182 | 275 | 0.012313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
200 | LV_1040-18_0_6_line_200 |  | 182 | 271 | 0.002575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
201 | LV_1040-18_0_6_line_201 |  | 183 | 286 | 0.013049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
202 | LV_1040-18_0_6_line_202 |  | 184 | 185 | 0.010126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
203 | LV_1040-18_0_6_line_203 |  | 185 | 186 | 0.013459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
204 | LV_1040-18_0_6_line_204 |  | 186 | 187 | 0.011884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
205 | LV_1040-18_0_6_line_205 |  | 186 | 188 | 0.0381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
206 | LV_1040-18_0_6_line_206 |  | 188 | 192 | 0.01236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
207 | LV_1040-18_0_6_line_207 |  | 190 | 191 | 0.018164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
208 | LV_1040-18_0_6_line_208 |  | 192 | 287 | 0.009577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
209 | LV_1040-18_0_6_line_209 |  | 192 | 284 | 0.027157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
210 | LV_1040-18_0_6_line_210 |  | 194 | 195 | 0.003459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
211 | LV_1040-18_0_6_line_211 |  | 195 | 198 | 0.016541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
212 | LV_1040-18_0_6_line_212 |  | 196 | 276 | 0.016054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
213 | LV_1040-18_0_6_line_213 |  | 197 | 234 | 0.018138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
214 | LV_1040-18_0_6_line_214 |  | 198 | 199 | 0.0040019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
215 | LV_1040-18_0_6_line_215 |  | 200 | 201 | 0.011107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
216 | LV_1040-18_0_6_line_216 |  | 200 | 202 | 0.02777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
217 | LV_1040-18_0_6_line_217 |  | 201 | 203 | 0.012576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
218 | LV_1040-18_0_6_line_218 |  | 201 | 204 | 0.0001095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
219 | LV_1040-18_0_6_line_219 |  | 202 | 205 | 0.0090398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
220 | LV_1040-18_0_6_line_220 |  | 203 | 206 | 0.003823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
221 | LV_1040-18_0_6_line_221 |  | 203 | 207 | 0.0064919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
222 | LV_1040-18_0_6_line_222 |  | 205 | 208 | 0.0072195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
223 | LV_1040-18_0_6_line_223 |  | 206 | 209 | 0.015994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
224 | LV_1040-18_0_6_line_224 |  | 207 | 210 | 0.012466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
225 | LV_1040-18_0_6_line_225 |  | 209 | 278 | 0.019744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
226 | LV_1040-18_0_6_line_226 |  | 210 | 262 | 0.0021474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
227 | LV_1040-18_0_6_line_227 |  | 212 | 213 | 0.012443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
228 | LV_1040-18_0_6_line_228 |  | 213 | 220 | 0.00025108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
229 | LV_1040-18_0_6_line_229 |  | 214 | 215 | 0.0065812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
230 | LV_1040-18_0_6_line_230 |  | 214 | 216 | 0.0041737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
231 | LV_1040-18_0_6_line_231 |  | 216 | 217 | 0.014311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
232 | LV_1040-18_0_6_line_232 |  | 217 | 218 | 0.010989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
233 | LV_1040-18_0_6_line_233 |  | 218 | 219 | 0.011057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
234 | LV_1040-18_0_6_line_234 |  | 219 | 289 | 0.00036309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
235 | LV_1040-18_0_6_line_235 |  | 220 | 250 | 6.1337e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
236 | LV_1040-18_0_6_line_236 |  | 221 | 222 | 0.016863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
237 | LV_1040-18_0_6_line_237 |  | 222 | 223 | 0.0059115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
238 | LV_1040-18_0_6_line_238 |  | 223 | 224 | 0.0060205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
239 | LV_1040-18_0_6_line_239 |  | 225 | 226 | 0.013419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
240 | LV_1040-18_0_6_line_240 |  | 225 | 227 | 0.018603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
241 | LV_1040-18_0_6_line_241 |  | 226 | 228 | 0.019499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
242 | LV_1040-18_0_6_line_242 |  | 226 | 229 | 0.0015233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
243 | LV_1040-18_0_6_line_243 |  | 228 | 230 | 0.00042928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
244 | LV_1040-18_0_6_line_244 |  | 229 | 231 | 0.010688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
245 | LV_1040-18_0_6_line_245 |  | 230 | 232 | 0.01035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
246 | LV_1040-18_0_6_line_246 |  | 231 | 233 | 0.028187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
247 | LV_1040-18_0_6_line_247 |  | 232 | 241 | 0.017596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
248 | LV_1040-18_0_6_line_248 |  | 234 | 235 | 0.0012104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
249 | LV_1040-18_0_6_line_249 |  | 235 | 236 | 0.00055033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
250 | LV_1040-18_0_6_line_250 |  | 236 | 280 | 0.0073883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
251 | LV_1040-18_0_6_line_251 |  | 237 | 238 | 0.014418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
252 | LV_1040-18_0_6_line_252 |  | 238 | 239 | 0.0047491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
253 | LV_1040-18_0_6_line_253 |  | 239 | 240 | 0.016793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
254 | LV_1040-18_0_6_line_254 |  | 240 | 241 | 0.0014514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
255 | LV_1040-18_0_6_line_255 |  | 242 | 243 | 0.023263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
256 | LV_1040-18_0_6_line_256 |  | 242 | 244 | 0.0038547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
257 | LV_1040-18_0_6_line_257 |  | 243 | 245 | 0.00045324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
258 | LV_1040-18_0_6_line_258 |  | 244 | 246 | 0.029429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
259 | LV_1040-18_0_6_line_259 |  | 245 | 247 | 0.012514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
260 | LV_1040-18_0_6_line_260 |  | 246 | 248 | 0.012971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
261 | LV_1040-18_0_6_line_261 |  | 246 | 249 | 0.0044214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
262 | LV_1040-18_0_6_line_262 |  | 247 | 250 | 0.012483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
263 | LV_1040-18_0_6_line_263 |  | 249 | 251 | 0.00089589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
264 | LV_1040-18_0_6_line_264 |  | 251 | 269 | 0.021683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
265 | LV_1040-18_0_6_line_265 |  | 252 | 253 | 0.0035413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
266 | LV_1040-18_0_6_line_266 |  | 252 | 254 | 0.0070627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
267 | LV_1040-18_0_6_line_267 |  | 253 | 255 | 0.010796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
268 | LV_1040-18_0_6_line_268 |  | 254 | 256 | 0.0070627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
269 | LV_1040-18_0_6_line_269 |  | 255 | 257 | 0.00094058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
270 | LV_1040-18_0_6_line_270 |  | 256 | 258 | 0.0020645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
271 | LV_1040-18_0_6_line_271 |  | 257 | 259 | 0.0070289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
272 | LV_1040-18_0_6_line_272 |  | 258 | 260 | 0.016887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
273 | LV_1040-18_0_6_line_273 |  | 259 | 281 | 0.0070273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
274 | LV_1040-18_0_6_line_274 |  | 260 | 269 | 0.009179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
275 | LV_1040-18_0_6_line_275 |  | 261 | 262 | 0.0042343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
276 | LV_1040-18_0_6_line_276 |  | 261 | 263 | 0.011735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
277 | LV_1040-18_0_6_line_277 |  | 263 | 264 | 0.0093665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
278 | LV_1040-18_0_6_line_278 |  | 264 | 265 | 0.021268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
279 | LV_1040-18_0_6_line_279 |  | 265 | 266 | 0.014701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
280 | LV_1040-18_0_6_line_280 |  | 266 | 288 | 0.0013627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
281 | LV_1040-18_0_6_line_281 |  | 267 | 268 | 0.032657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
282 | LV_1040-18_0_6_line_282 |  | 267 | 269 | 0.018199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
283 | LV_1040-18_0_6_line_283 |  | 268 | 270 | 0.0010517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
284 | LV_1040-18_0_6_line_284 |  | 269 | 271 | 0.030411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
285 | LV_1040-18_0_6_line_285 |  | 270 | 272 | 0.038072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
286 | LV_1040-18_0_6_line_286 |  | 271 | 273 | 0.007742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
287 | LV_1040-18_0_6_line_287 |  | 272 | 274 | 0.032459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
288 | LV_1040-18_0_6_line_288 |  | 276 | 277 | 0.024692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
289 | LV_1040-18_0_6_line_289 |  | 278 | 279 | 0.0018902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
290 | LV_1040-18_0_6_line_290 |  | 279 | 280 | 0.0005504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
291 | LV_1040-18_0_6_line_291 |  | 284 | 285 | 0.008978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
292 | LV_1040-18_0_6_line_292 |  | 288 | 289 | 0.011531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
293 | LV_1040-18_0_6_line_293 |  | 291 | 292 | 0.029234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
294 | LV_1040-18_0_6_line_294 |  | 292 | 293 | 0.0089619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
295 | LV_1040-18_0_6_line_295 |  | 295 | 296 | 0.0087708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1040-18_0_6_trafo_27 | 0.63 MVA 20/0.4 kV | 297 | 58 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11
0 | 2663617.8797 | 1217104.4208 | 2663612.4495 | 1217109.5994 | 2663601.367 | 1217122.9895 | 2663504.262 | 1217262.3532
1 | 2663503.2167 | 1217263.8533 | 2663504.262 | 1217262.3532
2 | 2663617.8797 | 1217104.4208 | 2663619.7121 | 1217105.5744
3 | 2663619.7121 | 1217105.5744 | 2663702.6255 | 1216994.0249
4 | 2663619.7121 | 1217105.5744 | 2663649.7246 | 1217128.7759 | 2663659.0776 | 1217135.869 | 2663678.3921 | 1217149.6935
5 | 2663702.7267 | 1216993.8887 | 2663702.6255 | 1216994.0249
6 | 2663702.7271 | 1216993.8882 | 2663702.7267 | 1216993.8887
7 | 2663710.7944 | 1216983.0321 | 2663708.7755 | 1216985.7507 | 2663702.7271 | 1216993.8882
8 | 2663841.289 | 1217071.6218 | 2663844.106 | 1217073.6977 | 2663853.1844 | 1217080.1989 | 2663867.6527 | 1217090.9495 | 2663872.1273 | 1217088.5404 | 2663878.0554 | 1217089.3377 | 2663885.6722 | 1217093.3663 | 2663889.3498 | 1217096.6077 | 2663896.6875 | 1217104.3836
9 | 2663841.289 | 1217071.6218 | 2663864.5201 | 1217040.4067 | 2663866.9598 | 1217036.6082 | 2663868.9417 | 1217030.9036 | 2663868.6776 | 1217025.7976 | 2663867.2224 | 1217022.7357 | 2663865.3958 | 1217018.9137 | 2663861.4836 | 1217013.3078
10 | 2663857.5002 | 1217007.5999 | 2663861.4836 | 1217013.3078
11 | 2663847.6926 | 1216996.6231 | 2663857.5002 | 1217007.5999 | 2663857.5002 | 1217007.5999
12 | 2663841.5787 | 1216989.7804 | 2663847.6926 | 1216996.6231
13 | 2663745.013 | 1216494.4877 | 2663850.297 | 1216512.2677
14 | 2663868.2353 | 1216515.297 | 2663850.297 | 1216512.2677
15 | 2663745.013 | 1216494.4877 | 2663731.3929 | 1216538.4361 | 2663729.0173 | 1216545.4595 | 2663728.0293 | 1216548.3841 | 2663805.4963 | 1216575.1292 | 2663862.6487 | 1216596.6323 | 2663881.4063 | 1216605.4053 | 2663879.4043 | 1216608.7304
16 | 2663879.4043 | 1216608.7304 | 2663889.2198 | 1216613.8054 | 2663898.1385 | 1216618.9646
17 | 2663879.4043 | 1216608.7304 | 2663878.9325 | 1216609.537 | 2663874.2138 | 1216616.9799 | 2663870.0672 | 1216622.8673
18 | 2663914.3839 | 1216628.3619 | 2663898.1385 | 1216618.9646
19 | 2663870.0672 | 1216622.8673 | 2663861.4595 | 1216635.0885
20 | 2663914.3839 | 1216628.3619 | 2663938.7332 | 1216642.4318
21 | 2663861.4595 | 1216635.0885 | 2663858.4077 | 1216639.4214
22 | 2663938.7332 | 1216642.4318 | 2663938.1396 | 1216643.2704 | 2663928.4318 | 1216656.7846
23 | 2663938.7332 | 1216642.4318 | 2663951.4508 | 1216650.1619 | 2663958.2423 | 1216654.6651
24 | 2663938.7332 | 1216642.4318 | 2663941.0322 | 1216639.0321 | 2663951.9104 | 1216646.2421 | 2663965.8417 | 1216655.4751 | 2663967.9501 | 1216651.4397
25 | 2663967.9501 | 1216651.4397 | 2663976.5523 | 1216657.0799 | 2663985.8559 | 1216662.554
26 | 2663985.8559 | 1216662.554 | 2664002.5358 | 1216672.3683
27 | 2664047.5962 | 1216709.7421 | 2664061.6354 | 1216681.3753 | 2664063.7157 | 1216678.2825
28 | 2664047.5962 | 1216709.7421 | 2664061.7438 | 1216719.3112 | 2664065.6859 | 1216721.9663 | 2664063.6455 | 1216725.3243 | 2664059.6954 | 1216722.7024
29 | 2664063.7157 | 1216678.2825 | 2664066.9657 | 1216673.4508
30 | 2664059.6954 | 1216722.7024 | 2664053.4087 | 1216733.1409
31 | 2664059.6954 | 1216722.7024 | 2664038.945 | 1216708.6708 | 2664037.7442 | 1216710.2033 | 2664029.7088 | 1216704.8294
32 | 2663928.4318 | 1216656.7846 | 2663918.3795 | 1216670.7784
33 | 2663977.2731 | 1216667.2837 | 2663958.2423 | 1216654.6651
34 | 2663996.5313 | 1216680.0531 | 2664002.8412 | 1216684.2234 | 2664003.107 | 1216687.0391 | 2664011.7089 | 1216692.7917
35 | 2663996.5313 | 1216680.0531 | 2663988.0615 | 1216690.9798
36 | 2663996.5313 | 1216680.0531 | 2663979.4917 | 1216668.7548
37 | 2664013.897 | 1216694.2551 | 2664011.7089 | 1216692.7917
38 | 2663981.0919 | 1216699.9711 | 2663988.0615 | 1216690.9798
39 | 2663979.4917 | 1216668.7548 | 2663977.2731 | 1216667.2837
40 | 2664099.1625 | 1216616.5493 | 2664085.9842 | 1216612.8387 | 2664063.5976 | 1216615.3774 | 2664039.6605 | 1216620.9015 | 2664019.2652 | 1216623.9622 | 2664011.8685 | 1216623.5984
41 | 2664099.1625 | 1216616.5493 | 2664099.9282 | 1216623.7064 | 2664086.8421 | 1216643.9006 | 2664086.2576 | 1216644.7697
42 | 2663776.3173 | 1216695.8811 | 2663767.3657 | 1216676.7624 | 2663757.004 | 1216660.6748
43 | 2663776.3173 | 1216695.8811 | 2663781.9258 | 1216696.0746
44 | 2663802.6229 | 1216708.9484 | 2663781.9258 | 1216696.0746
45 | 2663802.6229 | 1216708.9484 | 2663812.4531 | 1216715.0629
46 | 2663813.7113 | 1216756.608 | 2663813.1929 | 1216752.5554 | 2663794.4974 | 1216728.1213
47 | 2663813.7113 | 1216756.608 | 2663817.043 | 1216759.5566
48 | 2663813.7113 | 1216756.608 | 2663808.6274 | 1216752.0952 | 2663789.8198 | 1216733.1266 | 2663757.2987 | 1216699.4466 | 2663742.6414 | 1216684.4393
49 | 2663829.5114 | 1216725.6733 | 2663812.4531 | 1216715.0629
50 | 2663816.18 | 1216769.9538 | 2663811.6583 | 1216766.1141 | 2663812.5507 | 1216765.023 | 2663814.4967 | 1216762.6646 | 2663816.4661 | 1216760.2619 | 2663817.043 | 1216759.5566
51 | 2663818.4469 | 1216771.668 | 2663816.18 | 1216769.9538
52 | 2663818.4469 | 1216771.668 | 2663825.9252 | 1216777.3294
53 | 2663779.4108 | 1216733.1486 | 2663764.4315 | 1216717.5453
54 | 2663779.4108 | 1216733.1486 | 2663773.8649 | 1216740.0624
55 | 2663764.4315 | 1216717.5453 | 2663749.6707 | 1216731.9498
56 | 2663764.4315 | 1216717.5453 | 2663742.4715 | 1216695.1632 | 2663733.7814 | 1216686.3648 | 2663732.9788 | 1216685.6401
57 | 2663773.8649 | 1216740.0624 | 2663769.3306 | 1216745.7152 | 2663769.3306 | 1216745.7152
58 | 2663880.6625 | 1216800.1298 | 2663881.3975 | 1216798.848 | 2663898.0716 | 1216782.3831
59 | 2663876.5705 | 1216807.2015 | 2663877.0888 | 1216806.3065 | 2663878.6668 | 1216803.5772 | 2663880.1211 | 1216801.0579 | 2663880.6625 | 1216800.1298
60 | 2663880.6625 | 1216800.1298 | 2663868.8723 | 1216793.6702
61 | 2663903.9597 | 1216784.1139 | 2663898.0716 | 1216782.3831
62 | 2663876.5705 | 1216807.2015 | 2663862.7708 | 1216799.4678
63 | 2663876.5705 | 1216807.2015 | 2663878.2681 | 1216808.1422
64 | 2663840.0914 | 1216786.7578 | 2663862.7708 | 1216799.4678
65 | 2663890.5026 | 1216814.9222 | 2663878.2681 | 1216808.1422
66 | 2663825.9252 | 1216777.3294 | 2663805.557 | 1216819.8018
67 | 2663825.9252 | 1216777.3294 | 2663834.7239 | 1216783.7498 | 2663840.0914 | 1216786.7578
68 | 2663799.3441 | 1216832.7572 | 2663805.557 | 1216819.8018
69 | 2663881.9474 | 1216830.4069 | 2663890.5026 | 1216814.9222
70 | 2663890.5026 | 1216814.9222 | 2663923.8047 | 1216833.4325
71 | 2663881.9474 | 1216830.4069 | 2663874.3874 | 1216844.0023
72 | 2663881.9474 | 1216830.4069 | 2663893.6928 | 1216836.748
73 | 2663935.2111 | 1216839.7725 | 2663923.8047 | 1216833.4325
74 | 2663935.2111 | 1216839.7725 | 2663951.1261 | 1216848.8379
75 | 2663935.2111 | 1216839.7725 | 2663919.5166 | 1216866.8807
76 | 2663983.5872 | 1216867.4752 | 2663982.4783 | 1216866.6964 | 2663951.1261 | 1216848.8379
77 | 2663915.7881 | 1216873.3205 | 2663919.5166 | 1216866.8807
78 | 2664010.3131 | 1216890.4766 | 2664013.1086 | 1216887.4937 | 2664015.9348 | 1216884.4777
79 | 2664015.9348 | 1216884.4777 | 2664029.9678 | 1216899.7379 | 2664054.8027 | 1216928.5226 | 2664070.4027 | 1216945.9451
80 | 2664027.4591 | 1216909.228 | 2664010.3131 | 1216890.4766
81 | 2664010.3131 | 1216890.4766 | 2664006.0205 | 1216885.8165 | 2663997.4207 | 1216878.0741
82 | 2664070.4027 | 1216945.9451 | 2664087.0461 | 1216964.533
83 | 2664027.4591 | 1216909.228 | 2664009.992 | 1216929.5531
84 | 2664027.4591 | 1216909.228 | 2664060.544 | 1216946.5336
85 | 2664027.4591 | 1216909.228 | 2664029.9731 | 1216906.3087 | 2664021.8337 | 1216897.2045 | 2664033.2922 | 1216886.3875
86 | 2663983.5872 | 1216867.4752 | 2663992.9596 | 1216874.0579 | 2663997.4207 | 1216878.0741
87 | 2663738.1568 | 1216747.9055 | 2663739.4848 | 1216745.1179 | 2663740.2363 | 1216743.714 | 2663744.1691 | 1216737.3187 | 2663749.6707 | 1216731.9498
88 | 2663903.9597 | 1216784.1139 | 2663909.1974 | 1216788.1582
89 | 2663903.9597 | 1216784.1139 | 2663910.9188 | 1216775.0646
90 | 2664033.2922 | 1216886.3875 | 2664052.438 | 1216897.6629
91 | 2664033.2922 | 1216886.3875 | 2664014.8989 | 1216871.6979
92 | 2664052.438 | 1216897.6629 | 2664061.002 | 1216902.7065 | 2664067.1053 | 1216906.9969
93 | 2664014.8989 | 1216871.6979 | 2664008.0756 | 1216866.2486 | 2663985.8418 | 1216853.0341
94 | 2664060.544 | 1216946.5336 | 2664069.6259 | 1216956.7741
95 | 2663792.4312 | 1216852.9958 | 2663799.3441 | 1216832.7572
96 | 2663777.2335 | 1216820.2351 | 2663786.0551 | 1216825.2326 | 2663799.3441 | 1216832.7572
97 | 2663855.6009 | 1216864.6238 | 2663858.471 | 1216865.2994 | 2663861.3694 | 1216864.7523 | 2663863.7866 | 1216863.066 | 2663874.3874 | 1216844.0023
98 | 2663893.6928 | 1216836.748 | 2663905.7271 | 1216843.2451
99 | 2663915.7881 | 1216873.3205 | 2663912.3567 | 1216879.2474
100 | 2664103.0669 | 1216982.4255 | 2664087.0461 | 1216964.533
101 | 2663733.8774 | 1216756.176 | 2663738.1568 | 1216747.9055
102 | 2663732.5006 | 1216745.0655 | 2663738.1568 | 1216747.9055
103 | 2663733.8774 | 1216756.176 | 2663745.121 | 1216761.8886
104 | 2663733.8774 | 1216756.176 | 2663733.3731 | 1216757.1935 | 2663712.7437 | 1216745.2767
105 | 2663726.1718 | 1216771.7589 | 2663733.3731 | 1216757.1935 | 2663733.8774 | 1216756.176
106 | 2663712.7437 | 1216745.2767 | 2663703.5606 | 1216761.8745
107 | 2663712.7437 | 1216745.2767 | 2663704.6556 | 1216740.6006
108 | 2663726.1718 | 1216771.7589 | 2663719.3231 | 1216768.2724
109 | 2663726.1718 | 1216771.7589 | 2663724.3328 | 1216775.4749
110 | 2663698.3364 | 1216771.3167 | 2663703.5606 | 1216761.8745
111 | 2663698.4155 | 1216737.9169 | 2663700.9879 | 1216738.4802 | 2663704.6556 | 1216740.6006
112 | 2663724.3328 | 1216775.4749 | 2663730.7295 | 1216778.6341
113 | 2663724.3328 | 1216775.4749 | 2663718.6291 | 1216787.0211
114 | 2664069.0313 | 1216835.1951 | 2664071.9059 | 1216830.5119 | 2664076.8507 | 1216822.46
115 | 2664085.5601 | 1216808.2782 | 2664076.8507 | 1216822.46
116 | 2664066.3838 | 1216833.5879 | 2664069.0313 | 1216835.1951
117 | 2664069.0313 | 1216835.1951 | 2664071.8296 | 1216836.904 | 2664084.4794 | 1216844.5225 | 2664090.6874 | 1216848.2582
118 | 2664085.5601 | 1216808.2782 | 2664088.3812 | 1216809.9873
119 | 2664056.3474 | 1216851.9248 | 2664065.1292 | 1216835.8869 | 2664066.3838 | 1216833.5879
120 | 2664066.3838 | 1216833.5879 | 2664038.1276 | 1216816.3595
121 | 2664090.6874 | 1216848.2582 | 2664093.9242 | 1216843.0787
122 | 2664090.6874 | 1216848.2582 | 2664112.1702 | 1216861.1972
123 | 2664088.3812 | 1216809.9873 | 2664090.5309 | 1216811.289 | 2664101.924 | 1216818.1701
124 | 2664056.3474 | 1216851.9248 | 2664062.4688 | 1216855.2482
125 | 2664056.3474 | 1216851.9248 | 2664052.566 | 1216849.8606
126 | 2664025.5105 | 1216808.6666 | 2664038.1276 | 1216816.3595
127 | 2664111.3722 | 1216823.8765 | 2664101.924 | 1216818.1701
128 | 2664112.1702 | 1216861.1972 | 2664129.7735 | 1216871.7972
129 | 2664110.8398 | 1216863.4844 | 2664112.1702 | 1216861.1972
130 | 2664106.1209 | 1216871.6387 | 2664110.8398 | 1216863.4844
131 | 2664106.1209 | 1216871.6387 | 2664101.9748 | 1216878.7875 | 2664106.8175 | 1216881.5538
132 | 2664106.1209 | 1216871.6387 | 2664094.2451 | 1216865.0008
133 | 2664045.0855 | 1216746.9606 | 2664053.4087 | 1216733.1409
134 | 2664013.897 | 1216694.2551 | 2664029.7088 | 1216704.8294
135 | 2664083.0189 | 1216769.9603 | 2664070.042 | 1216762.0922
136 | 2664083.0189 | 1216769.9603 | 2664077.4648 | 1216779.0226
137 | 2664062.4642 | 1216757.4976 | 2664070.042 | 1216762.0922
138 | 2664072.8478 | 1216786.556 | 2664077.4648 | 1216779.0226
139 | 2664149.5149 | 1216781.527 | 2664137.3241 | 1216802.4978
140 | 2664149.5149 | 1216781.527 | 2664140.0519 | 1216775.5357
141 | 2664137.3241 | 1216802.4978 | 2664134.9573 | 1216806.5527 | 2664125.5512 | 1216800.8702
142 | 2664137.3241 | 1216802.4978 | 2664160.7528 | 1216816.4826
143 | 2664025.5105 | 1216808.6666 | 2664017.245 | 1216822.5976
144 | 2664025.5105 | 1216808.6666 | 2664017.1529 | 1216803.5736
145 | 2664111.3722 | 1216823.8765 | 2664120.7724 | 1216808.624
146 | 2664111.3722 | 1216823.8765 | 2664126.606 | 1216833.0741
147 | 2664151.2358 | 1216884.721 | 2664129.7735 | 1216871.7972
148 | 2664108.8186 | 1216882.6968 | 2664106.8175 | 1216881.5538
149 | 2664149.8524 | 1216886.9853 | 2664139.5759 | 1216880.7948
150 | 2664149.8524 | 1216886.9853 | 2664184.7593 | 1216908.0098
151 | 2664156.8818 | 1216902.5707 | 2664159.0597 | 1216899.1364 | 2664159.3822 | 1216898.0948 | 2664159.1994 | 1216896.7364 | 2664158.6632 | 1216895.7634 | 2664155.4204 | 1216893.7494 | 2664148.3455 | 1216889.4484 | 2664149.8524 | 1216886.9853
152 | 2664149.8524 | 1216886.9853 | 2664151.2358 | 1216884.721
153 | 2664045.0855 | 1216746.9606 | 2664062.4642 | 1216757.4976
154 | 2664045.0855 | 1216746.9606 | 2664043.2379 | 1216750.0427 | 2664032.658 | 1216743.7075
155 | 2664066.9657 | 1216673.4508 | 2664070.1862 | 1216668.6629
156 | 2664125.5512 | 1216800.8702 | 2664125.5512 | 1216800.8702 | 2664120.7724 | 1216808.624
157 | 2664160.7528 | 1216816.4826 | 2664168.3163 | 1216820.9974
158 | 2664001.4648 | 1216794.0137 | 2664017.1529 | 1216803.5736
159 | 2663986.1 | 1216784.6508 | 2664001.4648 | 1216794.0137
160 | 2663986.1 | 1216784.6508 | 2663978.2449 | 1216797.8414
161 | 2663986.1 | 1216784.6508 | 2663983.7769 | 1216783.2361 | 2663981.6591 | 1216782.0131
162 | 2663968.1808 | 1216774.2298 | 2663981.6591 | 1216782.0131
163 | 2663968.1808 | 1216774.2298 | 2663968.1808 | 1216774.2298 | 2663972.5319 | 1216767.7835 | 2663965.2501 | 1216761.1044
164 | 2663962.4502 | 1216758.5363 | 2663962.4502 | 1216758.5363 | 2663965.2501 | 1216761.1044
165 | 2664169.8527 | 1216895.9328 | 2664188.951 | 1216907.433
166 | 2664152.8877 | 1216885.7172 | 2664169.8527 | 1216895.9328
167 | 2664188.951 | 1216907.433 | 2664196.3496 | 1216911.8881
168 | 2664152.8877 | 1216885.7172 | 2664157.3883 | 1216878.0942
169 | 2664152.8877 | 1216885.7172 | 2664151.2358 | 1216884.721
170 | 2663962.4502 | 1216758.5363 | 2663957.0596 | 1216758.9986
171 | 2663940.9846 | 1216751.7129 | 2663951.8494 | 1216759.4454 | 2663957.0596 | 1216758.9986
172 | 2664029.3525 | 1216774.2532 | 2664016.8955 | 1216766.7924 | 2664022.7717 | 1216757.0331
173 | 2664027.0581 | 1216749.9142 | 2664022.7717 | 1216757.0331
174 | 2664036.4408 | 1216778.4985 | 2664029.3525 | 1216774.2532
175 | 2664027.0581 | 1216749.9142 | 2664031.2889 | 1216742.8876 | 2664032.658 | 1216743.7075
176 | 2663985.8418 | 1216853.0341 | 2663953.3989 | 1216833.7519
177 | 2664115.3428 | 1216943.1158 | 2664108.3515 | 1216935.9917 | 2664067.1053 | 1216906.9969
178 | 2664115.3428 | 1216943.1158 | 2664123.656 | 1216951.5771 | 2664130.5884 | 1216956.1468
179 | 2664115.3428 | 1216943.1158 | 2664117.8976 | 1216937.8177 | 2664117.7765 | 1216933.5471 | 2664116.3727 | 1216931.364 | 2664114.0416 | 1216929.9936 | 2664111.2771 | 1216929.3857 | 2664108.7834 | 1216927.6022 | 2664107.8905 | 1216924.5018 | 2664109.614 | 1216920.251 | 2664112.8957 | 1216919.3635 | 2664117.0006 | 1216919.5745 | 2664122.1214 | 1216922.6902
180 | 2664145.3719 | 1216936.8371 | 2664122.1214 | 1216922.6902
181 | 2663910.0132 | 1216883.2951 | 2663912.3567 | 1216879.2474
182 | 2663852.6875 | 1216854.5307 | 2663851.6633 | 1216857.2992 | 2663851.8672 | 1216860.2255 | 2663853.2591 | 1216862.8198 | 2663855.6009 | 1216864.6238
183 | 2663910.0132 | 1216883.2951 | 2663902.5352 | 1216896.2113
184 | 2663901.8433 | 1216897.4064 | 2663902.5352 | 1216896.2113
185 | 2663901.8433 | 1216897.4064 | 2663898.8648 | 1216902.5509
186 | 2663863.4894 | 1216950.1775 | 2663865.8259 | 1216945.6444
187 | 2663865.8259 | 1216945.6444 | 2663869.476 | 1216938.5629 | 2663879.5646 | 1216930.2929
188 | 2663886.4185 | 1216924.0486 | 2663885.7288 | 1216925.2398 | 2663879.5646 | 1216930.2929
189 | 2663886.4185 | 1216924.0486 | 2663887.73 | 1216921.7832
190 | 2663892.5973 | 1216913.3764 | 2663887.73 | 1216921.7832
191 | 2663892.5973 | 1216913.3764 | 2663898.8648 | 1216902.5509
192 | 2663773.2144 | 1216814.8332 | 2663781.3435 | 1216819.2784 | 2663784.5825 | 1216820.9119
193 | 2663773.2144 | 1216814.8332 | 2663758.3381 | 1216806.6786
194 | 2663753.0856 | 1216806.5461 | 2663772.1549 | 1216817.3567 | 2663773.2144 | 1216814.8332
195 | 2663773.2144 | 1216814.8332 | 2663772.1549 | 1216817.3567 | 2663777.2335 | 1216820.2351
196 | 2663773.2144 | 1216814.8332 | 2663785.1229 | 1216786.4161
197 | 2663921.3165 | 1216793.1834 | 2663919.1019 | 1216795.8057 | 2663909.1974 | 1216788.1582
198 | 2663911.1084 | 1216774.8181 | 2663910.9188 | 1216775.0646
199 | 2663792.4312 | 1216852.9958 | 2663803.6658 | 1216858.1081
200 | 2663791.6004 | 1216855.4329 | 2663792.4312 | 1216852.9958
201 | 2663777.2335 | 1216820.2351 | 2663771.3767 | 1216831.9019
202 | 2663673.9432 | 1216794.1988 | 2663664.9697 | 1216789.5069
203 | 2663685.8703 | 1216800.435 | 2663673.9432 | 1216794.1988
204 | 2663679.2507 | 1216810.3149 | 2663685.8703 | 1216800.435
205 | 2663685.8703 | 1216800.435 | 2663701.698 | 1216786.3954 | 2663708.4143 | 1216786.6451 | 2663718.6291 | 1216787.0211
206 | 2663729.4053 | 1216793.129 | 2663718.6291 | 1216787.0211
207 | 2663698.3364 | 1216771.3167 | 2663682.5689 | 1216762.3001
208 | 2663729.4053 | 1216793.129 | 2663725.0775 | 1216801.6769
209 | 2663729.4053 | 1216793.129 | 2663753.0856 | 1216806.5461
210 | 2663916.3615 | 1216673.5876 | 2663918.3795 | 1216670.7784
211 | 2663906.7112 | 1216687.0217 | 2663916.3615 | 1216673.5876
212 | 2664002.5358 | 1216672.3683 | 2664002.5358 | 1216672.3683 | 2664002.7036 | 1216675.1163 | 2664013.7908 | 1216682.4638
213 | 2663981.0919 | 1216699.9711 | 2663969.9796 | 1216714.3069
214 | 2663904.3765 | 1216690.272 | 2663906.7112 | 1216687.0217
215 | 2663930.8322 | 1216764.6121 | 2663939.1885 | 1216771.9285
216 | 2663921.3165 | 1216793.1834 | 2663936.4269 | 1216775.2898 | 2663939.1885 | 1216771.9285
217 | 2663938.6215 | 1216754.7228 | 2663930.8322 | 1216764.6121
218 | 2663930.8322 | 1216764.6121 | 2663930.7407 | 1216764.5519
219 | 2663921.3165 | 1216793.1834 | 2663928.6611 | 1216798.4535
220 | 2663940.9846 | 1216751.7129 | 2663938.6215 | 1216754.7228
221 | 2663938.6215 | 1216754.7228 | 2663933.4589 | 1216750.7868
222 | 2663934.5267 | 1216802.6624 | 2663928.6611 | 1216798.4535
223 | 2663940.9846 | 1216751.7129 | 2663950.783 | 1216739.0722
224 | 2663933.4589 | 1216750.7868 | 2663923.5454 | 1216743.2289
225 | 2663962.8793 | 1216723.4669 | 2663950.783 | 1216739.0722
226 | 2663921.8377 | 1216741.927 | 2663923.5454 | 1216743.2289
227 | 2663710.7944 | 1216983.0321 | 2663718.2131 | 1216973.0421
228 | 2663718.3628 | 1216972.8405 | 2663718.2131 | 1216973.0421
229 | 2663829.5114 | 1216725.6733 | 2663835.0998 | 1216729.1493
230 | 2663838.6438 | 1216731.3537 | 2663835.0998 | 1216729.1493
231 | 2663851.661 | 1216734.2336 | 2663851.661 | 1216734.2336 | 2663847.7218 | 1216735.5478 | 2663844.4181 | 1216734.9454 | 2663838.6438 | 1216731.3537
232 | 2663851.661 | 1216734.2336 | 2663857.8018 | 1216725.1209
233 | 2663863.9806 | 1216715.9519 | 2663857.8018 | 1216725.1209
234 | 2663863.9806 | 1216715.9519 | 2663864.1835 | 1216715.6508
235 | 2663718.3994 | 1216972.7913 | 2663718.3628 | 1216972.8405
236 | 2664076.8457 | 1216658.7622 | 2664086.2576 | 1216644.7697
237 | 2664073.5464 | 1216663.6673 | 2664076.8457 | 1216658.7622
238 | 2664073.5464 | 1216663.6673 | 2664070.1862 | 1216668.6629
239 | 2663800.4767 | 1216661.7406 | 2663807.699 | 1216650.4312
240 | 2663817.7116 | 1216634.7527 | 2663807.699 | 1216650.4312
241 | 2663800.4767 | 1216661.7406 | 2663816.6871 | 1216672.5778
242 | 2663800.4767 | 1216661.7406 | 2663799.2103 | 1216660.8941
243 | 2663817.044 | 1216672.8164 | 2663816.6871 | 1216672.5778
244 | 2663790.3241 | 1216654.9547 | 2663799.2103 | 1216660.8941
245 | 2663817.044 | 1216672.8164 | 2663825.6483 | 1216678.5688
246 | 2663768.6447 | 1216637.0448 | 2663782.9125 | 1216650.0009 | 2663790.3241 | 1216654.9547
247 | 2663836.8646 | 1216670.0082 | 2663829.1747 | 1216680.9263 | 2663825.6483 | 1216678.5688
248 | 2663969.238 | 1216715.2636 | 2663969.9796 | 1216714.3069
249 | 2663969.238 | 1216715.2636 | 2663968.9009 | 1216715.6986
250 | 2663968.9009 | 1216715.6986 | 2663964.3745 | 1216721.538
251 | 2663850.1053 | 1216651.2092 | 2663858.4077 | 1216639.4214
252 | 2663850.1053 | 1216651.2092 | 2663847.3706 | 1216655.0919
253 | 2663847.3706 | 1216655.0919 | 2663837.7004 | 1216668.8216
254 | 2663837.7004 | 1216668.8216 | 2663836.8646 | 1216670.0082
255 | 2663733.573 | 1216952.3586 | 2663747.4424 | 1216933.6819
256 | 2663749.7406 | 1216930.5873 | 2663747.4424 | 1216933.6819
257 | 2663733.573 | 1216952.3586 | 2663733.3027 | 1216952.7224
258 | 2663767.2861 | 1216906.9605 | 2663749.7406 | 1216930.5873
259 | 2663733.3027 | 1216952.7224 | 2663725.8419 | 1216962.7692
260 | 2663767.2861 | 1216906.9605 | 2663777.9337 | 1216914.4124
261 | 2663767.2861 | 1216906.9605 | 2663769.9227 | 1216903.4112
262 | 2663725.8419 | 1216962.7692 | 2663718.3994 | 1216972.7913
263 | 2663770.4569 | 1216902.692 | 2663769.9227 | 1216903.4112
264 | 2663781.772 | 1216884.2124 | 2663772.3007 | 1216900.2099 | 2663770.4569 | 1216902.692
265 | 2663741.13 | 1216863.0577 | 2663744.2711 | 1216864.693
266 | 2663750.5358 | 1216867.9543 | 2663744.2711 | 1216864.693
267 | 2663731.5537 | 1216858.0724 | 2663741.13 | 1216863.0577
268 | 2663756.8004 | 1216871.2156 | 2663750.5358 | 1216867.9543
269 | 2663730.7194 | 1216857.638 | 2663731.5537 | 1216858.0724
270 | 2663758.6315 | 1216872.1689 | 2663756.8004 | 1216871.2156
271 | 2663730.7194 | 1216857.638 | 2663724.4847 | 1216854.3923
272 | 2663773.6106 | 1216879.9669 | 2663758.6315 | 1216872.1689
273 | 2663718.2515 | 1216851.1473 | 2663724.4847 | 1216854.3923
274 | 2663773.6106 | 1216879.9669 | 2663781.772 | 1216884.2124
275 | 2663921.8377 | 1216741.927 | 2663918.4704 | 1216739.3598
276 | 2663909.1382 | 1216732.2449 | 2663918.4704 | 1216739.3598
277 | 2663909.1382 | 1216732.2449 | 2663901.6895 | 1216726.5662
278 | 2663886.5633 | 1216712.1604 | 2663889.0856 | 1216716.9571 | 2663901.6895 | 1216726.5662
279 | 2663886.5633 | 1216712.1604 | 2663883.3612 | 1216712.7042 | 2663876.1915 | 1216708.7027 | 2663873.0961 | 1216707.738
280 | 2663873.0961 | 1216707.738 | 2663871.7952 | 1216707.3325 | 2663871.7952 | 1216707.3325
281 | 2663808.7591 | 1216926.5547 | 2663803.5186 | 1216913.6856 | 2663794.031 | 1216897.4999
282 | 2663781.772 | 1216884.2124 | 2663791.9696 | 1216893.9831 | 2663794.031 | 1216897.4999
283 | 2663809.1557 | 1216927.5287 | 2663808.7591 | 1216926.5547
284 | 2663781.772 | 1216884.2124 | 2663787.8774 | 1216866.3443 | 2663791.6004 | 1216855.4329
285 | 2663809.1557 | 1216927.5287 | 2663813.0315 | 1216937.0465 | 2663825.2464 | 1216962.014
286 | 2663791.6004 | 1216855.4329 | 2663784.4429 | 1216852.4323
287 | 2663841.5787 | 1216989.7804 | 2663835.5048 | 1216982.9823 | 2663825.2464 | 1216962.014
288 | 2664034.3735 | 1216696.1042 | 2664013.7908 | 1216682.4638
289 | 2663962.8793 | 1216723.4669 | 2663964.0373 | 1216721.973
290 | 2663964.3745 | 1216721.538 | 2663964.0373 | 1216721.973
291 | 2663753.0856 | 1216806.5461 | 2663749.0141 | 1216814.552
292 | 2663871.7952 | 1216707.3325 | 2663868.4793 | 1216709.276 | 2663864.1835 | 1216715.6508
293 | 2664168.3163 | 1216820.9974 | 2664183.7773 | 1216830.2261 | 2664177.844 | 1216839.7581
294 | 2664173.1081 | 1216847.3664 | 2664177.844 | 1216839.7581
295 | 2664134.1144 | 1216837.6074 | 2664126.606 | 1216833.0741

## bus_geodata
| x | y | coords
0 | 2663504.262 | 1217262.3532
1 | 2663617.8797 | 1217104.4208
2 | 2663503.2167 | 1217263.8533
3 | 2663619.7121 | 1217105.5744
4 | 2663702.6255 | 1216994.0249
5 | 2663678.3921 | 1217149.6935
6 | 2663702.7267 | 1216993.8887
7 | 2663702.7271 | 1216993.8882
8 | 2663896.6875 | 1217104.3836
9 | 2663841.289 | 1217071.6218
10 | 2663861.4836 | 1217013.3078
11 | 2663857.5002 | 1217007.5999
12 | 2663847.6926 | 1216996.6231
13 | 2663850.297 | 1216512.2677
14 | 2663745.013 | 1216494.4877
15 | 2663868.2353 | 1216515.297
16 | 2663879.4043 | 1216608.7304
17 | 2663898.1385 | 1216618.9646
18 | 2663870.0672 | 1216622.8673
19 | 2663914.3839 | 1216628.3619
20 | 2663861.4595 | 1216635.0885
21 | 2663938.7332 | 1216642.4318
22 | 2663967.9502 | 1216651.4397
23 | 2663985.8559 | 1216662.554
24 | 2664047.5962 | 1216709.7421
25 | 2664063.7157 | 1216678.2825
26 | 2664059.6954 | 1216722.7024
27 | 2663928.4318 | 1216656.7846
28 | 2663958.2423 | 1216654.6651
29 | 2663996.5313 | 1216680.0531
30 | 2664011.7089 | 1216692.7917
31 | 2663988.0615 | 1216690.9798
32 | 2663979.4917 | 1216668.7548
33 | 2664011.8685 | 1216623.5984
34 | 2664099.1625 | 1216616.5493
35 | 2663757.004 | 1216660.6748
36 | 2663776.3173 | 1216695.8811
37 | 2663781.9258 | 1216696.0746
38 | 2663802.6229 | 1216708.9484
39 | 2663794.4974 | 1216728.1213
40 | 2663813.7113 | 1216756.608
41 | 2663812.4531 | 1216715.0629
42 | 2663817.043 | 1216759.5566
43 | 2663742.6414 | 1216684.4393
44 | 2663816.18 | 1216769.9538
45 | 2663818.4469 | 1216771.668
46 | 2663779.4108 | 1216733.1486
47 | 2663764.4315 | 1216717.5453
48 | 2663773.8649 | 1216740.0624
49 | 2663880.6625 | 1216800.1298
50 | 2663898.0716 | 1216782.3831
51 | 2663876.5705 | 1216807.2015
52 | 2663868.8723 | 1216793.6702
53 | 2663862.7708 | 1216799.4678
54 | 2663878.2681 | 1216808.1422
55 | 2663825.9252 | 1216777.3294
56 | 2663805.557 | 1216819.8018
57 | 2663840.0914 | 1216786.7578
58 | 2663890.5026 | 1216814.9222
59 | 2663881.9474 | 1216830.4069
60 | 2663923.8047 | 1216833.4325
61 | 2663935.2111 | 1216839.7725
62 | 2663951.1261 | 1216848.8379
63 | 2663919.5166 | 1216866.8807
64 | 2664015.9348 | 1216884.4777
65 | 2664010.3131 | 1216890.4766
66 | 2664070.4027 | 1216945.9451
67 | 2664027.4591 | 1216909.228
68 | 2663997.4207 | 1216878.0741
69 | 2663769.3306 | 1216745.7152
70 | 2663749.6707 | 1216731.9498
71 | 2663732.9788 | 1216685.6401
72 | 2663903.9597 | 1216784.1139
73 | 2664033.2922 | 1216886.3875
74 | 2664052.438 | 1216897.6629
75 | 2664014.8989 | 1216871.6979
76 | 2664009.992 | 1216929.5531
77 | 2664060.544 | 1216946.5336
78 | 2663799.3441 | 1216832.7572
79 | 2663874.3874 | 1216844.0023
80 | 2663893.6928 | 1216836.748
81 | 2663983.5872 | 1216867.4752
82 | 2663915.7881 | 1216873.3205
83 | 2664087.0461 | 1216964.533
84 | 2663738.1568 | 1216747.9055
85 | 2663733.8774 | 1216756.176
86 | 2663732.5006 | 1216745.0655
87 | 2663745.121 | 1216761.8886
88 | 2663712.7437 | 1216745.2767
89 | 2663726.1718 | 1216771.7589
90 | 2663703.5606 | 1216761.8745
91 | 2663704.6556 | 1216740.6006
92 | 2663719.3231 | 1216768.2724
93 | 2663724.3328 | 1216775.4749
94 | 2664076.8507 | 1216822.46
95 | 2664069.0313 | 1216835.1951
96 | 2664085.5601 | 1216808.2782
97 | 2664066.3838 | 1216833.5879
98 | 2664090.6874 | 1216848.2582
99 | 2664088.3812 | 1216809.9873
100 | 2664056.3474 | 1216851.9248
101 | 2664038.1276 | 1216816.3595
102 | 2664062.4688 | 1216855.2482
103 | 2664052.566 | 1216849.8606
104 | 2664101.924 | 1216818.1701
105 | 2664093.9242 | 1216843.0787
106 | 2664112.1702 | 1216861.1972
107 | 2664110.8398 | 1216863.4844
108 | 2664106.1209 | 1216871.6387
109 | 2664053.4087 | 1216733.1409
110 | 2664029.7088 | 1216704.8294
111 | 2664083.0189 | 1216769.9603
112 | 2664070.042 | 1216762.0922
113 | 2664077.4648 | 1216779.0226
114 | 2664149.5149 | 1216781.527
115 | 2664137.3241 | 1216802.4978
116 | 2664140.0519 | 1216775.5357
117 | 2664025.5105 | 1216808.6666
118 | 2664111.3722 | 1216823.8765
119 | 2664129.7735 | 1216871.7972
120 | 2664106.8175 | 1216881.5538
121 | 2664094.2451 | 1216865.0008
122 | 2664139.5759 | 1216880.7948
123 | 2664149.8524 | 1216886.9853
124 | 2664045.0855 | 1216746.9606
125 | 2664013.897 | 1216694.2551
126 | 2664066.9657 | 1216673.4508
127 | 2664062.4642 | 1216757.4976
128 | 2664072.8478 | 1216786.556
129 | 2664125.5512 | 1216800.8702
130 | 2664160.7528 | 1216816.4826
131 | 2664001.4648 | 1216794.0137
132 | 2664017.1529 | 1216803.5736
133 | 2663986.1 | 1216784.6508
134 | 2663978.2449 | 1216797.8414
135 | 2663981.6591 | 1216782.0131
136 | 2664017.245 | 1216822.5976
137 | 2663968.1808 | 1216774.2298
138 | 2663965.2501 | 1216761.1044
139 | 2664169.8527 | 1216895.9328
140 | 2664188.951 | 1216907.433
141 | 2664152.8877 | 1216885.7172
142 | 2664196.3496 | 1216911.8881
143 | 2664157.3883 | 1216878.0942
144 | 2664151.2358 | 1216884.721
145 | 2664184.7593 | 1216908.0098
146 | 2664156.8818 | 1216902.5707
147 | 2664108.8186 | 1216882.6968
148 | 2663962.4502 | 1216758.5363
149 | 2663957.0596 | 1216758.9986
150 | 2664022.7717 | 1216757.0331
151 | 2664029.3525 | 1216774.2532
152 | 2664027.0581 | 1216749.9142
153 | 2664036.4408 | 1216778.4985
154 | 2664032.658 | 1216743.7075
155 | 2663985.8418 | 1216853.0341
156 | 2663953.3989 | 1216833.7519
157 | 2664067.1053 | 1216906.9969
158 | 2664115.3428 | 1216943.1158
159 | 2664069.6259 | 1216956.7741
160 | 2664103.0669 | 1216982.4255
161 | 2664130.5884 | 1216956.1468
162 | 2664122.1214 | 1216922.6902
163 | 2664145.3719 | 1216936.8371
164 | 2663912.3567 | 1216879.2474
165 | 2663855.6009 | 1216864.6238
166 | 2663905.7271 | 1216843.2451
167 | 2663852.6875 | 1216854.5307
168 | 2663910.0132 | 1216883.2951
169 | 2663902.5352 | 1216896.2113
170 | 2663901.8433 | 1216897.4064
171 | 2663863.4894 | 1216950.1775
172 | 2663865.8259 | 1216945.6444
173 | 2663879.5646 | 1216930.2929
174 | 2663886.4185 | 1216924.0486
175 | 2663887.73 | 1216921.7832
176 | 2663898.8648 | 1216902.5509
177 | 2663892.5973 | 1216913.3764
178 | 2663784.5825 | 1216820.9119
179 | 2663773.2144 | 1216814.8332
180 | 2663909.1974 | 1216788.1582
181 | 2663910.9188 | 1216775.0646
182 | 2663792.4312 | 1216852.9958
183 | 2663777.2335 | 1216820.2351
184 | 2663664.9697 | 1216789.5069
185 | 2663673.9432 | 1216794.1988
186 | 2663685.8703 | 1216800.435
187 | 2663679.2507 | 1216810.3149
188 | 2663718.6291 | 1216787.0211
189 | 2663698.4155 | 1216737.9169
190 | 2663682.5689 | 1216762.3001
191 | 2663698.3364 | 1216771.3167
192 | 2663729.4053 | 1216793.129
193 | 2663977.2731 | 1216667.2837
194 | 2663918.3795 | 1216670.7784
195 | 2663916.3615 | 1216673.5876
196 | 2664002.5358 | 1216672.3683
197 | 2663981.0919 | 1216699.9711
198 | 2663906.7112 | 1216687.0217
199 | 2663904.3765 | 1216690.272
200 | 2663939.1885 | 1216771.9285
201 | 2663930.8322 | 1216764.6121
202 | 2663921.3165 | 1216793.1834
203 | 2663938.6215 | 1216754.7228
204 | 2663930.7407 | 1216764.5519
205 | 2663928.6611 | 1216798.4535
206 | 2663940.9846 | 1216751.7129
207 | 2663933.4589 | 1216750.7868
208 | 2663934.5267 | 1216802.6624
209 | 2663950.783 | 1216739.0722
210 | 2663923.5454 | 1216743.2289
211 | 2663911.1084 | 1216774.8181
212 | 2663710.7944 | 1216983.0321
213 | 2663718.2131 | 1216973.0421
214 | 2663835.0998 | 1216729.1493
215 | 2663829.5114 | 1216725.6733
216 | 2663838.6438 | 1216731.3537
217 | 2663851.661 | 1216734.2336
218 | 2663857.8018 | 1216725.1209
219 | 2663863.9806 | 1216715.9519
220 | 2663718.3628 | 1216972.8405
221 | 2664086.2576 | 1216644.7697
222 | 2664076.8457 | 1216658.7622
223 | 2664073.5464 | 1216663.6673
224 | 2664070.1862 | 1216668.6629
225 | 2663807.699 | 1216650.4312
226 | 2663800.4767 | 1216661.7406
227 | 2663817.7116 | 1216634.7527
228 | 2663816.6871 | 1216672.5778
229 | 2663799.2103 | 1216660.8941
230 | 2663817.044 | 1216672.8164
231 | 2663790.3241 | 1216654.9547
232 | 2663825.6483 | 1216678.5688
233 | 2663768.6447 | 1216637.0448
234 | 2663969.9796 | 1216714.3069
235 | 2663969.238 | 1216715.2636
236 | 2663968.9009 | 1216715.6986
237 | 2663858.4077 | 1216639.4214
238 | 2663850.1053 | 1216651.2092
239 | 2663847.3706 | 1216655.0919
240 | 2663837.7004 | 1216668.8216
241 | 2663836.8646 | 1216670.0082
242 | 2663747.4424 | 1216933.6819
243 | 2663733.573 | 1216952.3586
244 | 2663749.7406 | 1216930.5873
245 | 2663733.3027 | 1216952.7224
246 | 2663767.2861 | 1216906.9605
247 | 2663725.8419 | 1216962.7692
248 | 2663777.9337 | 1216914.4124
249 | 2663769.9227 | 1216903.4112
250 | 2663718.3994 | 1216972.7913
251 | 2663770.4569 | 1216902.692
252 | 2663744.2711 | 1216864.693
253 | 2663741.13 | 1216863.0578
254 | 2663750.5358 | 1216867.9543
255 | 2663731.5537 | 1216858.0724
256 | 2663756.8004 | 1216871.2156
257 | 2663730.7194 | 1216857.638
258 | 2663758.6315 | 1216872.1689
259 | 2663724.4847 | 1216854.3923
260 | 2663773.6106 | 1216879.9669
261 | 2663918.4704 | 1216739.3598
262 | 2663921.8377 | 1216741.927
263 | 2663909.1382 | 1216732.245
264 | 2663901.6895 | 1216726.5661
265 | 2663886.5633 | 1216712.1604
266 | 2663873.0961 | 1216707.738
267 | 2663794.031 | 1216897.4999
268 | 2663808.7591 | 1216926.5547
269 | 2663781.772 | 1216884.2124
270 | 2663809.1557 | 1216927.5287
271 | 2663791.6004 | 1216855.4329
272 | 2663825.2464 | 1216962.014
273 | 2663784.4429 | 1216852.4323
274 | 2663841.5787 | 1216989.7804
275 | 2663803.6658 | 1216858.1081
276 | 2664013.7908 | 1216682.4638
277 | 2664034.3735 | 1216696.1042
278 | 2663962.8793 | 1216723.4669
279 | 2663964.0373 | 1216721.973
280 | 2663964.3745 | 1216721.538
281 | 2663718.2515 | 1216851.1473
282 | 2663785.1229 | 1216786.4161
283 | 2663758.3381 | 1216806.6786
284 | 2663753.0856 | 1216806.5461
285 | 2663749.0141 | 1216814.552
286 | 2663771.3767 | 1216831.9019
287 | 2663725.0775 | 1216801.6769
288 | 2663871.7952 | 1216707.3325
289 | 2663864.1835 | 1216715.6508
290 | 2663730.7295 | 1216778.6341
291 | 2664168.3163 | 1216820.9974
292 | 2664177.844 | 1216839.7581
293 | 2664173.1081 | 1216847.3664
294 | 2664120.7724 | 1216808.624
295 | 2664126.606 | 1216833.0741
296 | 2664134.1144 | 1216837.6074
297 | 2663892.4692 | 1216811.3633

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98494 | -0.29026 | 0.00032747 | 8.2071e-05
1 | 0.98507 | -0.28769 | 0 | 0
2 | 0.98494 | -0.29028 | 0.00040583 | 0.00010171
3 | 0.98507 | -0.28766 | 0 | 0
4 | 0.98614 | -0.26678 | 0.0020068 | 0.00050294
5 | 0.98455 | -0.29772 | 0.0076284 | 0.0019119
6 | 0.98614 | -0.26674 | 0.0013574 | 0.00034021
7 | 0.98614 | -0.26674 | 0.0013596 | 0.00034075
8 | 0.98719 | -0.24631 | 0.0013813 | 0.0003462
9 | 0.98728 | -0.24463 | 0 | 0
10 | 0.98737 | -0.24292 | 0.0022081 | 0.0005534
11 | 0.98739 | -0.24248 | 0.0013899 | 0.00034835
12 | 0.98746 | -0.24117 | 0.0018718 | 0.00046911
13 | 0.97218 | -0.53681 | 0.0019651 | 0.00049249
14 | 0.97265 | -0.52741 | 0 | 0
15 | 0.97213 | -0.53775 | 0.0028063 | 0.00070333
16 | 0.97365 | -0.5077 | 0 | 0
17 | 0.9744 | -0.49293 | 0.0024335 | 0.0006099
18 | 0.97313 | -0.51795 | 0.0021994 | 0.00055122
19 | 0.9751 | -0.47913 | 0 | 0
20 | 0.9727 | -0.52639 | 0.0027224 | 0.00068231
21 | 0.97615 | -0.45853 | 0 | 0
22 | 0.97518 | -0.47773 | 0 | 0
23 | 0.97464 | -0.48828 | 0.0047742 | 0.0011965
24 | 0.97853 | -0.41222 | 0 | 0
25 | 0.97769 | -0.42872 | 0.0030164 | 0.00075597
26 | 0.97925 | -0.39802 | 0 | 0
27 | 0.9759 | -0.46358 | 0.004022 | 0.001008
28 | 0.97793 | -0.42363 | 0.0052596 | 0.0013182
29 | 0.98177 | -0.34882 | 0 | 0
30 | 0.98109 | -0.36207 | 0.00049156 | 0.0001232
31 | 0.9834 | -0.31722 | 0.0014057 | 0.0003523
32 | 0.98003 | -0.38263 | 0.0015576 | 0.00039036
33 | 0.97673 | -0.44757 | 0.0035121 | 0.00088023
34 | 0.97702 | -0.44187 | 0 | 0
35 | 0.9849 | -0.28959 | 0.0035716 | 0.00089514
36 | 0.98503 | -0.28701 | 0 | 0
37 | 0.98505 | -0.28665 | 0.0045744 | 0.0011464
38 | 0.98523 | -0.28308 | 0.0029379 | 0.00073631
39 | 0.99577 | -0.080527 | 0.0048376 | 0.0012124
40 | 0.99593 | -0.077564 | 0 | 0
41 | 0.98535 | -0.28078 | 0.0029348 | 0.00073552
42 | 0.99596 | -0.076938 | 0 | 0
43 | 0.99564 | -0.083208 | 0.003168 | 0.00079398
44 | 0.99607 | -0.074909 | 0 | 0
45 | 0.99609 | -0.07451 | 0 | 0
46 | 0.9889 | -0.21321 | 0 | 0
47 | 0.98897 | -0.21186 | 0 | 0
48 | 0.98887 | -0.21377 | 0.0020331 | 0.00050955
49 | 0.99774 | -0.042765 | 0 | 0
50 | 0.99608 | -0.074203 | 0.0016211 | 0.00040629
51 | 0.9983 | -0.032175 | 0 | 0
52 | 0.99764 | -0.044753 | 0.0084432 | 0.0021161
53 | 0.99771 | -0.04348 | 0.003962 | 0.00099297
54 | 0.99851 | -0.028276 | 0.0035839 | 0.00089821
55 | 0.99615 | -0.073193 | 0 | 0
56 | 0.99457 | -0.10354 | 0.003123 | 0.00078271
57 | 0.99676 | -0.061637 | 0.0048974 | 0.0012274
58 | 1 | 0 | -0.61208 | -0.15608
59 | 0.99962 | -0.0073623 | 0 | 0
60 | 0.99596 | -0.076919 | 0.0020773 | 0.00052063
61 | 0.99461 | -0.10293 | 0 | 0
62 | 0.99325 | -0.12895 | 0.0026593 | 0.00066649
63 | 0.99367 | -0.12103 | 0.001645 | 0.00041228
64 | 0.98808 | -0.22883 | 0 | 0
65 | 0.98818 | -0.22684 | 0 | 0
66 | 0.98705 | -0.24879 | 0.0042078 | 0.0010546
67 | 0.98684 | -0.25287 | 0 | 0
68 | 0.98935 | -0.20417 | 0.0049567 | 0.0012423
69 | 0.98886 | -0.21396 | 0.0014696 | 0.00036832
70 | 0.98908 | -0.2098 | 0.0020276 | 0.00050815
71 | 0.98888 | -0.21355 | 0.0021114 | 0.00052917
72 | 0.99567 | -0.081921 | 0 | 0
73 | 0.98546 | -0.27966 | 0 | 0
74 | 0.98506 | -0.28746 | 0.01135 | 0.0028446
75 | 0.98487 | -0.29126 | 0.0084216 | 0.0021106
76 | 0.98675 | -0.25464 | 0.0036865 | 0.00092393
77 | 0.98653 | -0.25888 | 0.0039174 | 0.00098178
78 | 0.99363 | -0.1217 | 0 | 0
79 | 0.99939 | -0.011806 | 0.0057226 | 0.0014342
80 | 0.99953 | -0.0091095 | 0.0035624 | 0.00089282
81 | 0.99057 | -0.18059 | 0.001913 | 0.00047945
82 | 0.99346 | -0.12511 | 0.0014599 | 0.00036588
83 | 0.98683 | -0.25297 | 0.004047 | 0.0010143
84 | 0.98922 | -0.20709 | 0 | 0
85 | 0.98929 | -0.20562 | 0 | 0
86 | 0.98921 | -0.20723 | 0.0012268 | 0.00030747
87 | 0.98928 | -0.20591 | 0.0012839 | 0.00032178
88 | 0.98915 | -0.20842 | 0 | 0
89 | 0.98955 | -0.20053 | 0 | 0
90 | 0.98908 | -0.20983 | 0.0020216 | 0.00050665
91 | 0.98913 | -0.20878 | 0.0010341 | 0.00025918
92 | 0.98954 | -0.20073 | 0.0014888 | 0.00037312
93 | 0.98962 | -0.1992 | 0 | 0
94 | 0.98079 | -0.36896 | 0.0060267 | 0.0015104
95 | 0.98098 | -0.36539 | 0 | 0
96 | 0.98068 | -0.37112 | 0 | 0
97 | 0.98111 | -0.36271 | 0 | 0
98 | 0.98016 | -0.38131 | 0 | 0
99 | 0.98066 | -0.37154 | 0 | 0
100 | 0.98101 | -0.36476 | 0 | 0
101 | 0.98275 | -0.33081 | 0.0027315 | 0.00068459
102 | 0.98099 | -0.36508 | 0.0025843 | 0.00064768
103 | 0.981 | -0.36498 | 0.0028265 | 0.00070838
104 | 0.98056 | -0.37359 | 0.00072843 | 0.00018256
105 | 0.98014 | -0.38166 | 0.0031358 | 0.0007859
106 | 0.97943 | -0.39566 | 0.0012256 | 0.00030717
107 | 0.97939 | -0.39647 | 0 | 0
108 | 0.97924 | -0.39935 | 0 | 0
109 | 0.97916 | -0.39982 | 0.00078499 | 0.00019674
110 | 0.9804 | -0.37555 | 0.00054393 | 0.00013632
111 | 0.97895 | -0.4041 | 0 | 0
112 | 0.97897 | -0.40364 | 0.00085951 | 0.00021541
113 | 0.97893 | -0.40442 | 0.00083464 | 0.00020918
114 | 0.98031 | -0.37854 | 0 | 0
115 | 0.98032 | -0.37823 | 0 | 0
116 | 0.9803 | -0.37868 | 0.00070785 | 0.0001774
117 | 0.98351 | -0.31588 | 0 | 0
118 | 0.98049 | -0.37488 | 0 | 0
119 | 0.97917 | -0.40072 | 0.00082583 | 0.00020697
120 | 0.97906 | -0.40288 | 0.013294 | 0.0033318
121 | 0.97921 | -0.40004 | 0.0027826 | 0.00069738
122 | 0.97885 | -0.40705 | 0.0010702 | 0.00026821
123 | 0.97886 | -0.40682 | 0 | 0
124 | 0.97905 | -0.40198 | 0 | 0
125 | 0.98101 | -0.36373 | 0.00052012 | 0.00013036
126 | 0.97757 | -0.43112 | 0.0028968 | 0.00072601
127 | 0.97899 | -0.40323 | 0.00086014 | 0.00021557
128 | 0.97892 | -0.40456 | 0.00083364 | 0.00020893
129 | 0.98037 | -0.37721 | 0.00070728 | 0.00017726
130 | 0.98025 | -0.37965 | 0.00070866 | 0.00017761
131 | 0.98513 | -0.2845 | 0.00054893 | 0.00013757
132 | 0.98407 | -0.30506 | 0.00083852 | 0.00021015
133 | 0.98617 | -0.26423 | 0 | 0
134 | 0.98607 | -0.26617 | 0.0070437 | 0.0017653
135 | 0.9865 | -0.25777 | 0.0017809 | 0.00044635
136 | 0.98343 | -0.31744 | 0.005352 | 0.0013413
137 | 0.98753 | -0.23782 | 0.0014641 | 0.00036693
138 | 0.98873 | -0.21479 | 0.0016117 | 0.00040392
139 | 0.97879 | -0.40831 | 0.0017709 | 0.00044383
140 | 0.97873 | -0.40937 | 0.0010429 | 0.00026137
141 | 0.97887 | -0.40673 | 0 | 0
142 | 0.97872 | -0.40961 | 0.0015608 | 0.00039118
143 | 0.97885 | -0.40706 | 0.0019913 | 0.00049906
144 | 0.97888 | -0.40651 | 0 | 0
145 | 0.97875 | -0.40903 | 0.0029897 | 0.0007493
146 | 0.97881 | -0.40776 | 0.0022832 | 0.00057222
147 | 0.97906 | -0.40291 | 0.00074344 | 0.00018632
148 | 0.98899 | -0.20973 | 0.0015437 | 0.00038688
149 | 0.98937 | -0.20238 | 0.0014594 | 0.00036575
150 | 0.97895 | -0.40407 | 0.00076059 | 0.00019062
151 | 0.97891 | -0.40485 | 0.00083297 | 0.00020876
152 | 0.97897 | -0.4037 | 0.00076067 | 0.00019064
153 | 0.9789 | -0.40498 | 0.0008317 | 0.00020844
154 | 0.97899 | -0.40313 | 0.00078433 | 0.00019657
155 | 0.98426 | -0.30308 | 0.0090909 | 0.0022784
156 | 0.98392 | -0.30982 | 0.0099186 | 0.0024858
157 | 0.98493 | -0.29002 | 0.0025398 | 0.00063653
158 | 0.98462 | -0.29615 | 0 | 0
159 | 0.98649 | -0.25957 | 0.0028139 | 0.00070523
160 | 0.98672 | -0.25527 | 0.0053367 | 0.0013375
161 | 0.98458 | -0.29689 | 0.0020324 | 0.00050936
162 | 0.98447 | -0.29892 | 0.0018042 | 0.00045217
163 | 0.98443 | -0.29981 | 0.0018084 | 0.00045323
164 | 0.99327 | -0.1287 | 0.0031641 | 0.00079301
165 | 0.99909 | -0.017507 | 0.0037599 | 0.00094232
166 | 0.99948 | -0.01005 | 0.003941 | 0.0009877
167 | 0.99902 | -0.018925 | 0.0068908 | 0.001727
168 | 0.99316 | -0.13089 | 0.0038602 | 0.00096745
169 | 0.99285 | -0.13686 | 0.00050819 | 0.00012736
170 | 0.99282 | -0.1374 | 0.00047773 | 0.00011973
171 | 0.99213 | -0.15083 | 0.0019371 | 0.00048549
172 | 0.99214 | -0.15066 | 0.0060726 | 0.0015219
173 | 0.99229 | -0.14768 | 0.0033766 | 0.00084627
174 | 0.99239 | -0.14579 | 0.00077348 | 0.00019385
175 | 0.99242 | -0.14523 | 0.0015403 | 0.00038603
176 | 0.99271 | -0.13967 | 0.0071771 | 0.0017988
177 | 0.99254 | -0.14287 | 0.00076104 | 0.00019073
178 | 0.99208 | -0.15151 | 0.0026026 | 0.00065228
179 | 0.99211 | -0.15092 | 0 | 0
180 | 0.99524 | -0.090155 | 0.0013737 | 0.00034428
181 | 0.99564 | -0.082573 | 0.0015668 | 0.00039269
182 | 0.99178 | -0.1573 | 0 | 0
183 | 0.99248 | -0.1438 | 0 | 0
184 | 0.98925 | -0.20636 | 0.0030051 | 0.00075315
185 | 0.98928 | -0.20582 | 0.0025551 | 0.00064036
186 | 0.98935 | -0.20449 | 0 | 0
187 | 0.98926 | -0.20634 | 0.0087676 | 0.0021974
188 | 0.98985 | -0.19477 | 0 | 0
189 | 0.98912 | -0.20891 | 0.0010989 | 0.00027542
190 | 0.98902 | -0.21094 | 0.0021482 | 0.00053839
191 | 0.98905 | -0.21025 | 0 | 0
192 | 0.99023 | -0.18737 | 0 | 0
193 | 0.97981 | -0.38697 | 0.0014718 | 0.00036888
194 | 0.97571 | -0.46724 | 0.0041629 | 0.0010433
195 | 0.97569 | -0.46771 | 0.0028377 | 0.00071119
196 | 0.97424 | -0.49628 | 0.0072054 | 0.0018059
197 | 0.98475 | -0.29101 | 0.0016059 | 0.00040248
198 | 0.97562 | -0.46911 | 0.0024397 | 0.00061145
199 | 0.97561 | -0.46926 | 0.0021598 | 0.00054129
200 | 0.99241 | -0.14411 | 0.0014641 | 0.00036693
201 | 0.9917 | -0.15774 | 0 | 0
202 | 0.9942 | -0.10993 | 0 | 0
203 | 0.9909 | -0.17304 | 0 | 0
204 | 0.9917 | -0.15774 | 0.0028514 | 0.00071463
205 | 0.99418 | -0.11039 | 0.0014741 | 0.00036945
206 | 0.9907 | -0.17673 | 0 | 0
207 | 0.99056 | -0.17955 | 0.0014341 | 0.00035942
208 | 0.99417 | -0.11058 | 0.0014452 | 0.0003622
209 | 0.98966 | -0.19666 | 0.001609 | 0.00040326
210 | 0.98993 | -0.19175 | 0.0015436 | 0.00038687
211 | 0.99564 | -0.082582 | 0.0016804 | 0.00042116
212 | 0.9863 | -0.26357 | 0.00094344 | 0.00023645
213 | 0.98646 | -0.26044 | 0.0008876 | 0.00022245
214 | 0.9857 | -0.2738 | 0.0045208 | 0.001133
215 | 0.98561 | -0.27572 | 0.0022204 | 0.00055649
216 | 0.98578 | -0.27225 | 0.0022192 | 0.00055618
217 | 0.98609 | -0.26635 | 0.006707 | 0.0016809
218 | 0.98639 | -0.2605 | 0.0062427 | 0.0015646
219 | 0.98675 | -0.25339 | 0.0021538 | 0.00053978
220 | 0.98647 | -0.26037 | 0.00068973 | 0.00017286
221 | 0.97713 | -0.43979 | 0.0072086 | 0.0018067
222 | 0.9773 | -0.43649 | 0.0028507 | 0.00071446
223 | 0.97737 | -0.43503 | 0.0031518 | 0.00078992
224 | 0.97746 | -0.43319 | 0.0029574 | 0.00074118
225 | 0.97096 | -0.56087 | 0.0030617 | 0.00076734
226 | 0.97103 | -0.55943 | 0 | 0
227 | 0.97091 | -0.56182 | 0.0027556 | 0.00069062
228 | 0.97128 | -0.55451 | 0.0013279 | 0.00033279
229 | 0.97102 | -0.55965 | 0.0021227 | 0.00053199
230 | 0.97129 | -0.55439 | 0.0021558 | 0.0005403
231 | 0.97096 | -0.56078 | 0.0021238 | 0.00053228
232 | 0.97145 | -0.55112 | 0.0013263 | 0.00033241
233 | 0.97087 | -0.56264 | 0.0035783 | 0.0008968
234 | 0.98694 | -0.24885 | 0.0015202 | 0.00038101
235 | 0.98709 | -0.24601 | 0.0015445 | 0.00038708
236 | 0.98716 | -0.24471 | 0.0015437 | 0.00038688
237 | 0.97257 | -0.52912 | 0.0021271 | 0.00053311
238 | 0.97222 | -0.53598 | 0.00218 | 0.00054635
239 | 0.97211 | -0.53805 | 0.0025258 | 0.00063302
240 | 0.97178 | -0.54459 | 0.001312 | 0.00032882
241 | 0.97176 | -0.54512 | 0.0013439 | 0.00033682
242 | 0.9873 | -0.24418 | 0.0097445 | 0.0024422
243 | 0.98687 | -0.25258 | 0.00094697 | 0.00023733
244 | 0.9874 | -0.24211 | 0.0013722 | 0.00034391
245 | 0.98686 | -0.25273 | 0.0014981 | 0.00037547
246 | 0.98825 | -0.22566 | 0 | 0
247 | 0.98666 | -0.25671 | 0.0014334 | 0.00035925
248 | 0.98821 | -0.22645 | 0.0034198 | 0.00085709
249 | 0.98839 | -0.22292 | 0.0021673 | 0.00054319
250 | 0.98647 | -0.26036 | 0.00068973 | 0.00017286
251 | 0.98842 | -0.22233 | 0.0021673 | 0.00054319
252 | 0.98839 | -0.22307 | 0.0025582 | 0.00064114
253 | 0.98834 | -0.22391 | 0.0029072 | 0.00072862
254 | 0.98849 | -0.22107 | 0.0025593 | 0.00064142
255 | 0.98824 | -0.22592 | 0.0030605 | 0.00076703
256 | 0.98861 | -0.21875 | 0.0025582 | 0.00064114
257 | 0.98823 | -0.22604 | 0.0024475 | 0.00061339
258 | 0.98865 | -0.21798 | 0.0021655 | 0.00054272
259 | 0.9882 | -0.22665 | 0.0024455 | 0.0006129
260 | 0.98901 | -0.21101 | 0 | 0
261 | 0.98962 | -0.19772 | 0.0014092 | 0.00035318
262 | 0.98982 | -0.1938 | 0.0014599 | 0.00036589
263 | 0.98907 | -0.20831 | 0.0028773 | 0.00072113
264 | 0.98866 | -0.21628 | 0.0048971 | 0.0012273
265 | 0.98782 | -0.23256 | 0 | 0
266 | 0.98724 | -0.24383 | 0.0013456 | 0.00033724
267 | 0.98882 | -0.2146 | 0.0042456 | 0.001064
268 | 0.98827 | -0.22536 | 0.0036552 | 0.00091608
269 | 0.9892 | -0.20723 | 0 | 0
270 | 0.98825 | -0.22563 | 0.00090237 | 0.00022616
271 | 0.99157 | -0.16133 | 0 | 0
272 | 0.98777 | -0.23509 | 0.0053842 | 0.0013494
273 | 0.99155 | -0.16179 | 0.0033172 | 0.00083136
274 | 0.98751 | -0.24004 | 0.0016728 | 0.00041925
275 | 0.99171 | -0.15859 | 0.0058821 | 0.0014742
276 | 0.97401 | -0.50079 | 0.0077348 | 0.0019385
277 | 0.97383 | -0.50423 | 0.007574 | 0.0018982
278 | 0.98839 | -0.22103 | 0.0013932 | 0.00034918
279 | 0.98815 | -0.22565 | 0.0014594 | 0.00036576
280 | 0.98808 | -0.22698 | 0.0014599 | 0.0003659
281 | 0.98819 | -0.22696 | 0.002444 | 0.00061252
282 | 0.99207 | -0.15176 | 0.0015397 | 0.00038589
283 | 0.99209 | -0.15136 | 0.0014595 | 0.00036579
284 | 0.99118 | -0.16896 | 0 | 0
285 | 0.99116 | -0.16946 | 0.003121 | 0.00078219
286 | 0.99246 | -0.14434 | 0.0023216 | 0.00058185
287 | 0.99019 | -0.18813 | 0.0044788 | 0.0011225
288 | 0.98719 | -0.24484 | 0.0012987 | 0.00032549
289 | 0.98677 | -0.25314 | 0.0021513 | 0.00053916
290 | 0.98961 | -0.19938 | 0.0013997 | 0.00035081
291 | 0.98023 | -0.37999 | 0.00070866 | 0.00017761
292 | 0.98019 | -0.38076 | 0.00072211 | 0.00018098
293 | 0.98019 | -0.38087 | 0.00072133 | 0.00018078
294 | 0.98041 | -0.37651 | 0.0007285 | 0.00018258
295 | 0.98047 | -0.37533 | 0.0007061 | 0.00017696
296 | 0.98046 | -0.37545 | 0.00070567 | 0.00017686
297 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.00073329 | -0.00018376 | 0.00073338 | 0.00018134 | 8.9557e-08 | -2.4215e-06 | 0.0011078 | 0.001107 | 0.0011078 | 0.98494 | -0.29026 | 0.98507 | -0.28769 | 0.30435
1 | 0.00040583 | 0.00010169 | -0.00040583 | -0.00010171 | 2.5775e-10 | -2.3104e-08 | 0.0006131 | 0.00061311 | 0.00061311 | 0.98494 | -0.29026 | 0.98494 | -0.29028 | 0.16844
2 | -0.00073338 | -0.00018134 | 0.00073339 | 0.00018131 | 9.93e-10 | -2.6875e-08 | 0.001107 | 0.0011069 | 0.001107 | 0.98507 | -0.28769 | 0.98507 | -0.28766 | 0.30411
3 | -0.0083654 | -0.0020946 | 0.0083737 | 0.0020981 | 8.3214e-06 | 3.5544e-06 | 0.012636 | 0.012635 | 0.012636 | 0.98507 | -0.28766 | 0.98614 | -0.26678 | 3.4714
4 | 0.007632 | 0.0019133 | -0.0076284 | -0.0019119 | 3.6599e-06 | 1.4081e-06 | 0.011529 | 0.011529 | 0.011529 | 0.98507 | -0.28766 | 0.98455 | -0.29772 | 3.1674
5 | -0.01038 | -0.0026011 | 0.010381 | 0.0026011 | 1.5617e-08 | 7.8293e-09 | 0.015663 | 0.015663 | 0.015663 | 0.98614 | -0.26678 | 0.98614 | -0.26674 | 4.3031
6 | -0.011738 | -0.0029413 | 0.011738 | 0.0029413 | 6.8024e-11 | 4.3536e-11 | 0.017712 | 0.017712 | 0.017712 | 0.98614 | -0.26674 | 0.98614 | -0.26674 | 4.8658
7 | -0.013098 | -0.003282 | 0.0131 | 0.0032831 | 1.981e-06 | 1.0953e-06 | 0.019763 | 0.019763 | 0.019763 | 0.98614 | -0.26674 | 0.9863 | -0.26357 | 5.4294
8 | -0.0013813 | -0.0003462 | 0.0013815 | 0.0003454 | 1.1047e-07 | -7.9832e-07 | 0.0020821 | 0.0020818 | 0.0020821 | 0.98719 | -0.24631 | 0.98728 | -0.24463 | 0.57201
9 | -0.0013815 | -0.0003454 | 0.0013816 | 0.00034459 | 1.1219e-07 | -8.1113e-07 | 0.0020818 | 0.0020815 | 0.0020818 | 0.98728 | -0.24463 | 0.98737 | -0.24292 | 0.57193
10 | -0.0035897 | -0.00089799 | 0.0035897 | 0.00089795 | 7.6373e-08 | -4.0147e-08 | 0.0054092 | 0.0054092 | 0.0054092 | 0.98737 | -0.24292 | 0.98739 | -0.24248 | 1.4861
11 | -0.0049797 | -0.0012463 | 0.00498 | 0.0012463 | 3.1082e-07 | 1.0634e-08 | 0.0075038 | 0.0075038 | 0.0075038 | 0.98739 | -0.24248 | 0.98746 | -0.24117 | 2.0615
12 | -0.0068517 | -0.0017154 | 0.0068521 | 0.0017155 | 3.6679e-07 | 1.1736e-07 | 0.010324 | 0.010324 | 0.010324 | 0.98746 | -0.24117 | 0.98751 | -0.24004 | 2.8364
13 | -0.0047715 | -0.0011957 | 0.0047736 | 0.0011957 | 2.1355e-06 | 4.2114e-08 | 0.0073032 | 0.0073027 | 0.0073032 | 0.97218 | -0.53681 | 0.97265 | -0.52741 | 2.0064
14 | 0.0028064 | 0.00070319 | -0.0028063 | -0.00070333 | 1.2588e-07 | -1.45e-07 | 0.0042955 | 0.0042956 | 0.0042956 | 0.97218 | -0.53681 | 0.97213 | -0.53775 | 1.1801
15 | -0.0047736 | -0.0011957 | 0.0047781 | 0.0011958 | 4.4814e-06 | 8.3603e-08 | 0.0073027 | 0.0073017 | 0.0073027 | 0.97265 | -0.52741 | 0.97365 | -0.5077 | 2.0062
16 | -0.037703 | -0.0094695 | 0.03773 | 0.0094863 | 2.6593e-05 | 1.6754e-05 | 0.057629 | 0.057629 | 0.057629 | 0.97365 | -0.5077 | 0.9744 | -0.49293 | 15.8321
17 | 0.032925 | 0.0082737 | -0.032909 | -0.0082636 | 1.6097e-05 | 1.0092e-05 | 0.050327 | 0.050327 | 0.050327 | 0.97365 | -0.5077 | 0.97313 | -0.51795 | 13.8261
18 | -0.040163 | -0.010096 | 0.04019 | 0.010113 | 2.6485e-05 | 1.6716e-05 | 0.061345 | 0.061345 | 0.061345 | 0.9744 | -0.49293 | 0.9751 | -0.47913 | 16.853
19 | 0.03071 | 0.0077124 | -0.030697 | -0.0077047 | 1.2364e-05 | 7.7272e-06 | 0.046964 | 0.046964 | 0.046964 | 0.97313 | -0.51795 | 0.9727 | -0.52639 | 12.9022
20 | -0.04019 | -0.010113 | 0.04023 | 0.010138 | 3.9599e-05 | 2.4993e-05 | 0.061345 | 0.061345 | 0.061345 | 0.9751 | -0.47913 | 0.97615 | -0.45853 | 16.8529
21 | 0.027975 | 0.0070224 | -0.027971 | -0.0070201 | 3.6405e-06 | 2.2642e-06 | 0.042799 | 0.042799 | 0.042799 | 0.9727 | -0.52639 | 0.97257 | -0.52912 | 11.7581
22 | 0.015628 | 0.0039186 | -0.015625 | -0.0039164 | 3.7603e-06 | 2.1858e-06 | 0.023824 | 0.023824 | 0.023824 | 0.97615 | -0.45853 | 0.9759 | -0.46358 | 6.5451
23 | -0.083198 | -0.020927 | 0.083337 | 0.021016 | 0.00013898 | 8.8658e-05 | 0.12685 | 0.12685 | 0.12685 | 0.97615 | -0.45853 | 0.97793 | -0.42363 | 34.8495
24 | 0.02734 | 0.0068708 | -0.027315 | -0.0068553 | 2.5034e-05 | 1.5542e-05 | 0.041683 | 0.041684 | 0.041684 | 0.97615 | -0.45853 | 0.97518 | -0.47773 | 11.4515
25 | 0.027315 | 0.0068553 | -0.027302 | -0.0068468 | 1.3736e-05 | 8.528e-06 | 0.041684 | 0.041684 | 0.041684 | 0.97518 | -0.47773 | 0.97464 | -0.48828 | 11.4516
26 | 0.022527 | 0.0056502 | -0.022519 | -0.005645 | 8.5855e-06 | 5.2536e-06 | 0.034395 | 0.034395 | 0.034395 | 0.97464 | -0.48828 | 0.97424 | -0.49628 | 9.4491
27 | 0.025624 | 0.0064312 | -0.025604 | -0.0064188 | 2.0147e-05 | 1.245e-05 | 0.038969 | 0.038969 | 0.038969 | 0.97853 | -0.41222 | 0.97769 | -0.42872 | 10.7057
28 | -0.025624 | -0.0064312 | 0.025641 | 0.0064419 | 1.737e-05 | 1.0733e-05 | 0.038969 | 0.038969 | 0.038969 | 0.97853 | -0.41222 | 0.97925 | -0.39802 | 10.7057
29 | 0.022587 | 0.0056628 | -0.022585 | -0.0056612 | 2.5807e-06 | 1.5787e-06 | 0.034378 | 0.034378 | 0.034378 | 0.97769 | -0.42872 | 0.97757 | -0.43112 | 9.4445
30 | 0.0081454 | 0.0020403 | -0.0081447 | -0.00204 | 6.9999e-07 | 2.9471e-07 | 0.012377 | 0.012377 | 0.012377 | 0.97925 | -0.39802 | 0.97916 | -0.39982 | 3.4002
31 | -0.033787 | -0.0084822 | 0.033823 | 0.0085049 | 3.6246e-05 | 2.2736e-05 | 0.051345 | 0.051345 | 0.051345 | 0.97925 | -0.39802 | 0.9804 | -0.37555 | 14.1059
32 | 0.011603 | 0.0029084 | -0.011601 | -0.0029073 | 2.0223e-06 | 1.079e-06 | 0.017692 | 0.017692 | 0.017692 | 0.9759 | -0.46358 | 0.97571 | -0.46724 | 4.8603
33 | -0.088597 | -0.022334 | 0.088753 | 0.022434 | 0.00015572 | 9.9375e-05 | 0.13486 | 0.13485 | 0.13486 | 0.97793 | -0.42363 | 0.97981 | -0.38697 | 37.0481
34 | 0.035423 | 0.0089228 | -0.035401 | -0.0089087 | 2.2432e-05 | 1.4094e-05 | 0.053705 | 0.053705 | 0.053705 | 0.98177 | -0.34882 | 0.98109 | -0.36207 | 14.7542
35 | -0.12737 | -0.032223 | 0.12757 | 0.032346 | 0.00019343 | 0.00012362 | 0.19316 | 0.19316 | 0.19316 | 0.98177 | -0.34882 | 0.9834 | -0.31722 | 53.0659
36 | 0.09195 | 0.0233 | -0.091801 | -0.023205 | 0.0001491 | 9.5168e-05 | 0.13945 | 0.13946 | 0.13946 | 0.98177 | -0.34882 | 0.98003 | -0.38263 | 38.3118
37 | 0.034909 | 0.0087855 | -0.034906 | -0.0087838 | 2.7686e-06 | 1.7387e-06 | 0.05296 | 0.05296 | 0.05296 | 0.98109 | -0.36207 | 0.98101 | -0.36373 | 14.5493
38 | -0.12897 | -0.032699 | 0.12913 | 0.032803 | 0.0001627 | 0.00010398 | 0.19529 | 0.19529 | 0.19529 | 0.9834 | -0.31722 | 0.98475 | -0.29101 | 53.6502
39 | 0.090243 | 0.022814 | -0.090224 | -0.022802 | 1.8761e-05 | 1.1973e-05 | 0.13709 | 0.13709 | 0.13709 | 0.98003 | -0.38263 | 0.97981 | -0.38697 | 37.6621
40 | -0.0035121 | -0.00088023 | 0.0035131 | 0.00087972 | 9.5346e-07 | -5.0173e-07 | 0.0053506 | 0.0053502 | 0.0053506 | 0.97673 | -0.44757 | 0.97702 | -0.44187 | 1.47
41 | -0.0035131 | -0.00087972 | 0.0035134 | 0.00087954 | 3.468e-07 | -1.827e-07 | 0.0053502 | 0.0053501 | 0.0053502 | 0.97702 | -0.44187 | 0.97713 | -0.43979 | 1.4698
42 | -0.0035716 | -0.00089514 | 0.0035721 | 0.0008949 | 4.3945e-07 | -2.3099e-07 | 0.0053962 | 0.005396 | 0.0053962 | 0.9849 | -0.28959 | 0.98503 | -0.28701 | 1.4825
43 | -0.0035721 | -0.0008949 | 0.0035721 | 0.00089487 | 6.1274e-08 | -3.2222e-08 | 0.005396 | 0.0053959 | 0.005396 | 0.98503 | -0.28701 | 0.98505 | -0.28665 | 1.4824
44 | -0.0081465 | -0.0020413 | 0.0081479 | 0.0020419 | 1.3842e-06 | 5.7554e-07 | 0.012306 | 0.012306 | 0.012306 | 0.98505 | -0.28665 | 0.98523 | -0.28308 | 3.3808
45 | -0.011086 | -0.0027782 | 0.011087 | 0.0027788 | 1.217e-06 | 6.3143e-07 | 0.016743 | 0.016743 | 0.016743 | 0.98523 | -0.28308 | 0.98535 | -0.28078 | 4.5998
46 | -0.0048376 | -0.0012124 | 0.0048383 | 0.0012124 | 6.8297e-07 | -1.6343e-08 | 0.007229 | 0.0072288 | 0.007229 | 0.99577 | -0.080527 | 0.99593 | -0.077564 | 1.986
47 | -0.0080072 | -0.0020056 | 0.0080074 | 0.0020057 | 2.3839e-07 | 9.4769e-08 | 0.011963 | 0.011963 | 0.011963 | 0.99593 | -0.077564 | 0.99596 | -0.076938 | 3.2866
48 | 0.0031689 | 0.00079321 | -0.003168 | -0.00079398 | 8.5156e-07 | -7.7288e-07 | 0.0047343 | 0.0047347 | 0.0047347 | 0.99593 | -0.077564 | 0.99564 | -0.083208 | 1.3008
49 | -0.014022 | -0.0035144 | 0.014025 | 0.0035163 | 3.3778e-06 | 1.9058e-06 | 0.021175 | 0.021175 | 0.021175 | 0.98535 | -0.28078 | 0.98561 | -0.27572 | 5.8173
50 | -0.0080074 | -0.0020057 | 0.0080082 | 0.002006 | 7.7374e-07 | 3.0756e-07 | 0.011963 | 0.011963 | 0.011963 | 0.99596 | -0.076938 | 0.99607 | -0.074909 | 3.2866
51 | -0.0080082 | -0.002006 | 0.0080083 | 0.0020061 | 1.5226e-07 | 6.0515e-08 | 0.011963 | 0.011963 | 0.011963 | 0.99607 | -0.074909 | 0.99609 | -0.07451 | 3.2865
52 | -0.0080083 | -0.0020061 | 0.0080088 | 0.0020063 | 5.0243e-07 | 1.9969e-07 | 0.011963 | 0.011963 | 0.011963 | 0.99609 | -0.07451 | 0.99615 | -0.073193 | 3.2865
53 | -0.0035028 | -0.00087773 | 0.0035031 | 0.00087759 | 2.2503e-07 | -1.3314e-07 | 0.0052707 | 0.0052706 | 0.0052707 | 0.9889 | -0.21321 | 0.98897 | -0.21186 | 1.448
54 | 0.0035028 | 0.00087773 | -0.0035027 | -0.00087778 | 9.2335e-08 | -5.4616e-08 | 0.0052707 | 0.0052707 | 0.0052707 | 0.9889 | -0.21321 | 0.98887 | -0.21377 | 1.448
55 | -0.0056146 | -0.0014063 | 0.0056152 | 0.0014064 | 5.5191e-07 | 8.855e-08 | 0.0084475 | 0.0084474 | 0.0084475 | 0.98897 | -0.21186 | 0.98908 | -0.2098 | 2.3207
56 | 0.0021116 | 0.0005287 | -0.0021114 | -0.00052917 | 1.6958e-07 | -4.6632e-07 | 0.0031769 | 0.0031771 | 0.0031771 | 0.98897 | -0.21186 | 0.98888 | -0.21355 | 0.87284
57 | 0.0014696 | 0.00036823 | -0.0014696 | -0.00036832 | 1.3289e-08 | -8.4461e-08 | 0.0022114 | 0.0022114 | 0.0022114 | 0.98887 | -0.21377 | 0.98886 | -0.21396 | 0.60753
58 | 0.29239 | 0.075049 | -0.29194 | -0.074766 | 0.00044537 | 0.00028374 | 0.4367 | 0.4367 | 0.4367 | 0.99774 | -0.042765 | 0.99608 | -0.074203 | 29.9929
59 | -0.30083 | -0.077166 | 0.30099 | 0.077264 | 0.00015462 | 9.8528e-05 | 0.44929 | 0.44929 | 0.44929 | 0.99774 | -0.042765 | 0.9983 | -0.032175 | 30.8577
60 | 0.008444 | 0.0021164 | -0.0084432 | -0.0021161 | 7.9953e-07 | 3.3614e-07 | 0.012593 | 0.012593 | 0.012593 | 0.99774 | -0.042765 | 0.99764 | -0.044753 | 3.4597
61 | 0.29032 | 0.074359 | -0.29021 | -0.07429 | 0.00010851 | 6.9127e-05 | 0.43427 | 0.43427 | 0.43427 | 0.99608 | -0.074203 | 0.99567 | -0.081921 | 29.8265
62 | 0.16462 | 0.041747 | -0.16453 | -0.041691 | 8.9414e-05 | 5.6398e-05 | 0.24554 | 0.24554 | 0.24554 | 0.9983 | -0.032175 | 0.99771 | -0.04348 | 16.8642
63 | -0.4656 | -0.11901 | 0.46569 | 0.11907 | 8.7842e-05 | 5.6117e-05 | 0.69483 | 0.69483 | 0.69483 | 0.9983 | -0.032175 | 0.99851 | -0.028276 | 47.7219
64 | 0.16057 | 0.040698 | -0.16043 | -0.04061 | 0.00013996 | 8.8219e-05 | 0.23963 | 0.23963 | 0.23963 | 0.99771 | -0.04348 | 0.99676 | -0.061637 | 16.4584
65 | -0.46928 | -0.11997 | 0.46992 | 0.12038 | 0.00064287 | 0.0004107 | 0.70017 | 0.70017 | 0.70017 | 0.99851 | -0.028276 | 1 | 0 | 48.0887
66 | 0.14743 | 0.037322 | -0.14722 | -0.037187 | 0.00021444 | 0.00013479 | 0.22036 | 0.22036 | 0.22036 | 0.99615 | -0.073193 | 0.99457 | -0.10354 | 15.1347
67 | -0.15544 | -0.039328 | 0.15553 | 0.039382 | 8.6249e-05 | 5.4311e-05 | 0.23232 | 0.23232 | 0.23232 | 0.99615 | -0.073193 | 0.99676 | -0.061637 | 15.9563
68 | 0.1441 | 0.036404 | -0.14397 | -0.036324 | 0.00012533 | 7.9839e-05 | 0.21569 | 0.21569 | 0.21569 | 0.99457 | -0.10354 | 0.99363 | -0.1217 | 29.6276
69 | 0.023893 | 0.005993 | -0.023884 | -0.0059878 | 8.3821e-06 | 5.1326e-06 | 0.035554 | 0.035555 | 0.035555 | 1 | 0 | 0.99962 | -0.0073623 | 9.7677
70 | 0.11661 | 0.029714 | -0.11618 | -0.029439 | 0.00043107 | 0.00027539 | 0.1737 | 0.1737 | 0.1737 | 1 | 0 | 0.99596 | -0.076919 | 47.719
71 | 0.01638 | 0.0041071 | -0.016377 | -0.0041051 | 3.4685e-06 | 2.0159e-06 | 0.024384 | 0.024384 | 0.024384 | 0.99962 | -0.0073623 | 0.99939 | -0.011806 | 6.6989
72 | 0.0075042 | 0.0018807 | -0.0075036 | -0.0018805 | 6.2459e-07 | 2.2478e-07 | 0.011171 | 0.011171 | 0.011171 | 0.99962 | -0.0073623 | 0.99953 | -0.0091095 | 3.0689
73 | 0.11411 | 0.028918 | -0.11396 | -0.028827 | 0.00014242 | 9.0979e-05 | 0.17059 | 0.17059 | 0.17059 | 0.99596 | -0.076919 | 0.99461 | -0.10293 | 46.8664
74 | 0.081153 | 0.020583 | -0.081051 | -0.020518 | 0.00010139 | 6.4652e-05 | 0.1215 | 0.1215 | 0.1215 | 0.99461 | -0.10293 | 0.99325 | -0.12895 | 33.3786
75 | 0.032811 | 0.0082441 | -0.032783 | -0.0082264 | 2.8313e-05 | 1.7714e-05 | 0.049096 | 0.049096 | 0.049096 | 0.99461 | -0.10293 | 0.99367 | -0.12103 | 13.4879
76 | 0.078392 | 0.019852 | -0.078198 | -0.019728 | 0.00019387 | 0.00012359 | 0.11751 | 0.11751 | 0.11751 | 0.99325 | -0.12895 | 0.99057 | -0.18059 | 32.2842
77 | 0.031138 | 0.0078141 | -0.031132 | -0.0078103 | 6.0681e-06 | 3.7872e-06 | 0.046633 | 0.046633 | 0.046633 | 0.99367 | -0.12103 | 0.99346 | -0.12511 | 12.8111
78 | -0.013607 | -0.0034145 | 0.013608 | 0.0034152 | 1.2948e-06 | 7.2333e-07 | 0.020493 | 0.020493 | 0.020493 | 0.98808 | -0.22883 | 0.98818 | -0.22684 | 5.63
79 | 0.013607 | 0.0034145 | -0.013594 | -0.0034073 | 1.2935e-05 | 7.2278e-06 | 0.020493 | 0.020493 | 0.020493 | 0.98808 | -0.22883 | 0.98705 | -0.24879 | 5.6301
80 | 0.057557 | 0.014487 | -0.057486 | -0.014442 | 7.1522e-05 | 4.5449e-05 | 0.086693 | 0.086693 | 0.086693 | 0.98818 | -0.22684 | 0.98684 | -0.25287 | 23.8167
81 | -0.071165 | -0.017902 | 0.071242 | 0.017952 | 7.715e-05 | 4.9147e-05 | 0.10719 | 0.10719 | 0.10719 | 0.98818 | -0.22684 | 0.98935 | -0.20417 | 29.4466
82 | 0.0093861 | 0.0023527 | -0.0093843 | -0.0023518 | 1.8734e-06 | 8.8013e-07 | 0.01415 | 0.01415 | 0.01415 | 0.98705 | -0.24879 | 0.98683 | -0.25297 | 3.8874
83 | 0.0036869 | 0.00092379 | -0.0036865 | -0.00092393 | 3.1025e-07 | -1.4343e-07 | 0.0055592 | 0.0055593 | 0.0055593 | 0.98684 | -0.25287 | 0.98675 | -0.25464 | 1.5273
84 | 0.0067333 | 0.0016875 | -0.0067313 | -0.0016869 | 1.9275e-06 | 5.9674e-07 | 0.010153 | 0.010153 | 0.010153 | 0.98684 | -0.25287 | 0.98653 | -0.25888 | 2.7893
85 | 0.047066 | 0.011831 | -0.047005 | -0.011792 | 6.0124e-05 | 3.8073e-05 | 0.070981 | 0.070981 | 0.070981 | 0.98684 | -0.25287 | 0.98546 | -0.27966 | 19.5003
86 | -0.076199 | -0.019194 | 0.076285 | 0.019249 | 8.6029e-05 | 5.4834e-05 | 0.11464 | 0.11464 | 0.11464 | 0.98935 | -0.20417 | 0.99057 | -0.18059 | 31.4947
87 | -0.0076427 | -0.0019145 | 0.0076437 | 0.0019149 | 9.8529e-07 | 3.7547e-07 | 0.011498 | 0.011498 | 0.011498 | 0.98908 | -0.2098 | 0.98922 | -0.20709 | 3.1587
88 | 0.28697 | 0.073477 | -0.28685 | -0.073404 | 0.0001144 | 7.2872e-05 | 0.42942 | 0.42942 | 0.42942 | 0.99567 | -0.081921 | 0.99524 | -0.090155 | 29.4932
89 | 0.0032474 | 0.00081376 | -0.0032473 | -0.00081384 | 1.0083e-07 | -8.3938e-08 | 0.0048531 | 0.0048532 | 0.0048532 | 0.99567 | -0.081921 | 0.99564 | -0.082573 | 1.3333
90 | 0.019545 | 0.0049002 | -0.019538 | -0.0048958 | 7.2578e-06 | 4.362e-06 | 0.029513 | 0.029514 | 0.029514 | 0.98546 | -0.27966 | 0.98506 | -0.28746 | 8.1081
91 | 0.02746 | 0.0068923 | -0.027445 | -0.0068828 | 1.5179e-05 | 9.4148e-06 | 0.041468 | 0.041468 | 0.041468 | 0.98546 | -0.27966 | 0.98487 | -0.29126 | 11.3922
92 | 0.008188 | 0.0020512 | -0.008187 | -0.0020508 | 9.9813e-07 | 4.1734e-07 | 0.012368 | 0.012368 | 0.012368 | 0.98506 | -0.28746 | 0.98493 | -0.29002 | 3.3979
93 | 0.019023 | 0.0047722 | -0.019013 | -0.0047658 | 1.0719e-05 | 6.4201e-06 | 0.028744 | 0.028744 | 0.028744 | 0.98487 | -0.29126 | 0.98426 | -0.30308 | 7.8966
94 | 0.002814 | 0.00070511 | -0.0028139 | -0.00070523 | 9.2468e-08 | -1.1558e-07 | 0.0042444 | 0.0042444 | 0.0042444 | 0.98653 | -0.25888 | 0.98649 | -0.25957 | 1.1661
95 | 0.094604 | 0.023893 | -0.094443 | -0.02379 | 0.0001611 | 0.00010283 | 0.14174 | 0.14174 | 0.14174 | 0.99363 | -0.1217 | 0.99178 | -0.1573 | 38.9397
96 | 0.049365 | 0.012431 | -0.049313 | -0.012398 | 5.2108e-05 | 3.302e-05 | 0.073949 | 0.073949 | 0.073949 | 0.99363 | -0.1217 | 0.99248 | -0.1438 | 20.3156
97 | 0.010654 | 0.0026709 | -0.010651 | -0.0026695 | 2.8932e-06 | 1.45e-06 | 0.015863 | 0.015864 | 0.015864 | 0.99939 | -0.011806 | 0.99909 | -0.017507 | 4.3581
98 | 0.0039412 | 0.00098764 | -0.003941 | -0.0009877 | 1.7655e-07 | -6.625e-08 | 0.0058673 | 0.0058673 | 0.0058673 | 0.99953 | -0.0091095 | 0.99948 | -0.01005 | 1.6119
99 | 0.029672 | 0.0074444 | -0.029667 | -0.0074413 | 5.0733e-06 | 3.1583e-06 | 0.044446 | 0.044446 | 0.044446 | 0.99346 | -0.12511 | 0.99327 | -0.1287 | 12.2104
100 | 0.0053373 | 0.0013376 | -0.0053367 | -0.0013375 | 5.8334e-07 | 6.6529e-08 | 0.0080479 | 0.008048 | 0.008048 | 0.98683 | -0.25297 | 0.98672 | -0.25527 | 2.211
101 | -0.0088705 | -0.0022223 | 0.0088712 | 0.0022226 | 6.2144e-07 | 2.7822e-07 | 0.013343 | 0.013343 | 0.013343 | 0.98922 | -0.20709 | 0.98929 | -0.20562 | 3.6657
102 | 0.0012268 | 0.00030739 | -0.0012268 | -0.00030747 | 8.0635e-09 | -7.5897e-08 | 0.0018454 | 0.0018454 | 0.0018454 | 0.98922 | -0.20709 | 0.98921 | -0.20723 | 0.50699
103 | 0.0012839 | 0.00032163 | -0.0012839 | -0.00032178 | 1.7596e-08 | -1.5029e-07 | 0.0019311 | 0.0019312 | 0.0019312 | 0.98929 | -0.20562 | 0.98928 | -0.20591 | 0.53055
104 | 0.0063041 | 0.0015793 | -0.0063032 | -0.0015791 | 8.4152e-07 | 2.1814e-07 | 0.0094819 | 0.009482 | 0.009482 | 0.98929 | -0.20562 | 0.98915 | -0.20842 | 2.6049
105 | -0.016459 | -0.0041235 | 0.016463 | 0.0041259 | 3.9952e-06 | 2.3337e-06 | 0.024756 | 0.024756 | 0.024756 | 0.98929 | -0.20562 | 0.98955 | -0.20053 | 6.8011
106 | 0.0041701 | 0.0010447 | -0.0041699 | -0.0010447 | 2.7993e-07 | -6.4313e-08 | 0.0062732 | 0.0062732 | 0.0062732 | 0.98915 | -0.20842 | 0.98908 | -0.20983 | 1.7234
107 | 0.0021331 | 0.00053441 | -0.0021331 | -0.00053451 | 3.6074e-08 | -9.6832e-08 | 0.0032088 | 0.0032089 | 0.0032089 | 0.98915 | -0.20842 | 0.98913 | -0.20878 | 0.88156
108 | 0.0014888 | 0.00037304 | -0.0014888 | -0.00037312 | 1.441e-08 | -8.9272e-08 | 0.0022387 | 0.0022387 | 0.0022387 | 0.98955 | -0.20053 | 0.98954 | -0.20073 | 0.61504
109 | -0.017952 | -0.0044989 | 0.017953 | 0.0044996 | 1.1327e-06 | 6.7167e-07 | 0.026995 | 0.026995 | 0.026995 | 0.98955 | -0.20053 | 0.98962 | -0.1992 | 7.4161
110 | 0.0021483 | 0.00053809 | -0.0021483 | -0.0005382 | 4.2269e-08 | -1.1144e-07 | 0.0032319 | 0.003232 | 0.003232 | 0.98908 | -0.20983 | 0.98905 | -0.21025 | 0.8879
111 | 0.0010989 | 0.00027533 | -0.0010989 | -0.00027542 | 7.0408e-09 | -8.3673e-08 | 0.0016532 | 0.0016532 | 0.0016532 | 0.98913 | -0.20878 | 0.98912 | -0.20891 | 0.45417
112 | 0.0013998 | 0.00035072 | -0.0013997 | -0.00035081 | 1.1824e-08 | -8.3887e-08 | 0.0021047 | 0.0021047 | 0.0021047 | 0.98962 | -0.1992 | 0.98961 | -0.19938 | 0.57821
113 | -0.019353 | -0.0048503 | 0.019357 | 0.0048527 | 4.0877e-06 | 2.4507e-06 | 0.029099 | 0.029099 | 0.029099 | 0.98962 | -0.1992 | 0.98985 | -0.19477 | 7.9943
114 | -0.013174 | -0.0033001 | 0.013176 | 0.0033013 | 2.2386e-06 | 1.2441e-06 | 0.019987 | 0.019987 | 0.019987 | 0.98079 | -0.36896 | 0.98098 | -0.36539 | 5.4909
115 | 0.0071476 | 0.0017897 | -0.0071469 | -0.0017894 | 7.3382e-07 | 2.5963e-07 | 0.010843 | 0.010843 | 0.010843 | 0.98079 | -0.36896 | 0.98068 | -0.37112 | 2.979
116 | -0.047954 | -0.012038 | 0.04796 | 0.012042 | 6.1342e-06 | 3.8869e-06 | 0.072747 | 0.072747 | 0.072747 | 0.98098 | -0.36539 | 0.98111 | -0.36271 | 19.9855
117 | 0.034777 | 0.0087364 | -0.034751 | -0.0087198 | 2.6401e-05 | 1.6577e-05 | 0.05276 | 0.05276 | 0.05276 | 0.98098 | -0.36539 | 0.98016 | -0.38131 | 14.4946
118 | 0.0071469 | 0.0017894 | -0.0071467 | -0.0017894 | 1.4511e-07 | 5.1348e-08 | 0.010843 | 0.010843 | 0.010843 | 0.98068 | -0.37112 | 0.98066 | -0.37154 | 2.979
119 | 0.0054113 | 0.001356 | -0.0054108 | -0.001356 | 5.2801e-07 | 7.3974e-08 | 0.0082071 | 0.0082072 | 0.0082072 | 0.98111 | -0.36271 | 0.98101 | -0.36476 | 2.2547
120 | -0.053371 | -0.013398 | 0.053453 | 0.013449 | 8.1332e-05 | 5.1634e-05 | 0.080954 | 0.080954 | 0.080954 | 0.98111 | -0.36271 | 0.98275 | -0.33081 | 22.2402
121 | 0.0031358 | 0.00078585 | -0.0031358 | -0.0007859 | 5.1876e-08 | -4.3733e-08 | 0.0047606 | 0.0047606 | 0.0047606 | 0.98016 | -0.38131 | 0.98014 | -0.38166 | 1.3079
122 | 0.031615 | 0.007934 | -0.031594 | -0.0079204 | 2.1622e-05 | 1.3523e-05 | 0.048 | 0.048 | 0.048 | 0.98016 | -0.38131 | 0.97943 | -0.39566 | 13.1868
123 | 0.0071467 | 0.0017894 | -0.007146 | -0.0017891 | 6.9769e-07 | 2.4691e-07 | 0.010843 | 0.010844 | 0.010844 | 0.98066 | -0.37154 | 0.98056 | -0.37359 | 2.979
124 | 0.0025843 | 0.00064762 | -0.0025843 | -0.00064768 | 4.0047e-08 | -6.2117e-08 | 0.0039199 | 0.00392 | 0.00392 | 0.98101 | -0.36476 | 0.98099 | -0.36508 | 1.0769
125 | 0.0028265 | 0.00070835 | -0.0028265 | -0.00070838 | 2.9625e-08 | -3.5304e-08 | 0.0042873 | 0.0042873 | 0.0042873 | 0.98101 | -0.36476 | 0.981 | -0.36498 | 1.1778
126 | -0.056184 | -0.014134 | 0.056224 | 0.014159 | 4.0122e-05 | 2.5491e-05 | 0.08509 | 0.08509 | 0.08509 | 0.98275 | -0.33081 | 0.98351 | -0.31588 | 23.3764
127 | 0.0064176 | 0.0016066 | -0.0064172 | -0.0016064 | 3.9253e-07 | 1.1199e-07 | 0.0097382 | 0.0097382 | 0.0097382 | 0.98056 | -0.37359 | 0.98049 | -0.37488 | 2.6753
128 | 0.013543 | 0.0033949 | -0.013539 | -0.003393 | 3.2621e-06 | 1.8292e-06 | 0.020575 | 0.020575 | 0.020575 | 0.97943 | -0.39566 | 0.97917 | -0.40072 | 5.6526
129 | 0.016825 | 0.0042184 | -0.016825 | -0.004218 | 6.479e-07 | 3.8138e-07 | 0.025563 | 0.025563 | 0.025563 | 0.97943 | -0.39566 | 0.97939 | -0.39647 | 7.0227
130 | 0.016825 | 0.004218 | -0.016822 | -0.0042167 | 2.3074e-06 | 1.3582e-06 | 0.025563 | 0.025563 | 0.025563 | 0.97939 | -0.39647 | 0.97924 | -0.39935 | 7.0227
131 | 0.01404 | 0.0035194 | -0.014037 | -0.0035181 | 2.3625e-06 | 1.3379e-06 | 0.021334 | 0.021335 | 0.021335 | 0.97924 | -0.39935 | 0.97906 | -0.40288 | 5.8611
132 | 0.0027827 | 0.00069726 | -0.0027826 | -0.00069738 | 9.1218e-08 | -1.1277e-07 | 0.0042284 | 0.0042284 | 0.0042284 | 0.97924 | -0.39935 | 0.97921 | -0.40004 | 1.1617
133 | 0.0073597 | 0.0018432 | -0.0073589 | -0.0018429 | 7.567e-07 | 2.8139e-07 | 0.011184 | 0.011184 | 0.011184 | 0.97916 | -0.39982 | 0.97905 | -0.40198 | 3.0725
134 | -0.034367 | -0.0086413 | 0.034386 | 0.0086534 | 1.9415e-05 | 1.2186e-05 | 0.052171 | 0.052171 | 0.052171 | 0.9804 | -0.37555 | 0.98101 | -0.36373 | 14.3326
135 | -0.0016683 | -0.00041789 | 0.0016683 | 0.00041772 | 3.6593e-08 | -1.6739e-07 | 0.0025358 | 0.0025357 | 0.0025358 | 0.97895 | -0.4041 | 0.97897 | -0.40364 | 0.69664
136 | 0.0016683 | 0.00041789 | -0.0016683 | -0.000418 | 2.563e-08 | -1.1723e-07 | 0.0025358 | 0.0025358 | 0.0025358 | 0.97895 | -0.4041 | 0.97893 | -0.40442 | 0.69666
137 | -0.0025279 | -0.00063313 | 0.0025279 | 0.00063305 | 4.9058e-08 | -8.0029e-08 | 0.0038422 | 0.0038421 | 0.0038422 | 0.97897 | -0.40364 | 0.97899 | -0.40323 | 1.0555
138 | 0.00083365 | 0.00020882 | -0.00083364 | -0.00020893 | 5.3203e-09 | -1.0768e-07 | 0.0012671 | 0.0012672 | 0.0012672 | 0.97893 | -0.40442 | 0.97892 | -0.40456 | 0.34813
139 | -0.00070786 | -0.00017727 | 0.00070787 | 0.00017697 | 1.0493e-08 | -2.9894e-07 | 0.0010744 | 0.0010743 | 0.0010744 | 0.98031 | -0.37854 | 0.98032 | -0.37823 | 0.29517
140 | 0.00070786 | 0.00017727 | -0.00070785 | -0.0001774 | 4.8486e-09 | -1.381e-07 | 0.0010744 | 0.0010745 | 0.0010745 | 0.98031 | -0.37854 | 0.9803 | -0.37868 | 0.29518
141 | -0.0035689 | -0.00089319 | 0.0035691 | 0.0008931 | 1.7257e-07 | -8.7314e-08 | 0.0054168 | 0.0054167 | 0.0054168 | 0.98032 | -0.37823 | 0.98037 | -0.37721 | 1.4881
142 | 0.002861 | 0.00071622 | -0.0028609 | -0.00071644 | 1.9295e-07 | -2.205e-07 | 0.0043424 | 0.0043426 | 0.0043426 | 0.98032 | -0.37823 | 0.98025 | -0.37965 | 1.193
143 | 0.0053524 | 0.0013414 | -0.005352 | -0.0013413 | 3.9811e-07 | 4.9365e-08 | 0.0080979 | 0.008098 | 0.008098 | 0.98351 | -0.31588 | 0.98343 | -0.31744 | 2.2247
144 | -0.061577 | -0.015501 | 0.061609 | 0.015521 | 3.1872e-05 | 2.0274e-05 | 0.093188 | 0.093188 | 0.093188 | 0.98351 | -0.31588 | 0.98407 | -0.30506 | 25.601
145 | 0.0050054 | 0.0012529 | -0.005005 | -0.0012529 | 3.8764e-07 | 2.2139e-08 | 0.0075957 | 0.0075958 | 0.0075958 | 0.98049 | -0.37488 | 0.98041 | -0.37651 | 2.0868
146 | 0.0014118 | 0.00035351 | -0.0014118 | -0.00035371 | 3.0632e-08 | -2.0483e-07 | 0.0021425 | 0.0021425 | 0.0021425 | 0.98049 | -0.37488 | 0.98047 | -0.37533 | 0.58861
147 | 0.012714 | 0.0031861 | -0.01271 | -0.0031841 | 3.5069e-06 | 1.9294e-06 | 0.01932 | 0.01932 | 0.01932 | 0.97917 | -0.40072 | 0.97888 | -0.40651 | 5.3078
148 | 0.00074344 | 0.0001863 | -0.00074344 | -0.00018632 | 1.1033e-09 | -2.8275e-08 | 0.0011299 | 0.0011299 | 0.0011299 | 0.97906 | -0.40288 | 0.97906 | -0.40291 | 0.31041
149 | -0.0010702 | -0.00026821 | 0.0010702 | 0.00026807 | 1.1907e-08 | -1.4319e-07 | 0.0016268 | 0.0016268 | 0.0016268 | 0.97885 | -0.40705 | 0.97886 | -0.40682 | 0.44694
150 | 0.0029901 | 0.00074899 | -0.0029897 | -0.0007493 | 3.157e-07 | -3.1014e-07 | 0.0045452 | 0.0045454 | 0.0045454 | 0.97886 | -0.40682 | 0.97875 | -0.40903 | 1.2487
151 | 0.0022833 | 0.000572 | -0.0022832 | -0.00057222 | 1.0206e-07 | -2.1866e-07 | 0.0034709 | 0.003471 | 0.003471 | 0.97886 | -0.40682 | 0.97881 | -0.40776 | 0.95356
152 | -0.0063435 | -0.0015891 | 0.0063436 | 0.0015891 | 9.2473e-08 | 2.5845e-08 | 0.0096428 | 0.0096428 | 0.0096428 | 0.97886 | -0.40682 | 0.97888 | -0.40651 | 2.6491
153 | 0.0033883 | 0.0008485 | -0.003388 | -0.00084862 | 2.0209e-07 | -1.2622e-07 | 0.0051494 | 0.0051495 | 0.0051495 | 0.97905 | -0.40198 | 0.97899 | -0.40323 | 1.4147
154 | 0.0039707 | 0.00099445 | -0.0039705 | -0.00099451 | 2.1748e-07 | -6.1067e-08 | 0.0060346 | 0.0060347 | 0.0060347 | 0.97905 | -0.40198 | 0.97899 | -0.40313 | 1.6579
155 | 0.019688 | 0.0049352 | -0.019686 | -0.004934 | 1.9434e-06 | 1.1714e-06 | 0.029969 | 0.029969 | 0.029969 | 0.97757 | -0.43112 | 0.97746 | -0.43319 | 8.2332
156 | -0.0042764 | -0.0010704 | 0.0042765 | 0.0010703 | 1.4387e-07 | -2.2775e-08 | 0.0064902 | 0.0064901 | 0.0064902 | 0.98037 | -0.37721 | 0.98041 | -0.37651 | 1.783
157 | 0.0021522 | 0.00053883 | -0.0021522 | -0.00053892 | 3.5253e-08 | -8.8479e-08 | 0.0032668 | 0.0032669 | 0.0032669 | 0.98025 | -0.37965 | 0.98023 | -0.37999 | 0.89749
158 | 0.062509 | 0.01577 | -0.062447 | -0.015731 | 6.1465e-05 | 3.9104e-05 | 0.094456 | 0.094456 | 0.094456 | 0.98513 | -0.2845 | 0.98407 | -0.30506 | 25.9494
159 | -0.063058 | -0.015908 | 0.063119 | 0.015947 | 6.126e-05 | 3.8977e-05 | 0.095285 | 0.095285 | 0.095285 | 0.98513 | -0.2845 | 0.98617 | -0.26423 | 26.1771
160 | 0.0070444 | 0.0017655 | -0.0070437 | -0.0017653 | 6.5005e-07 | 2.2029e-07 | 0.010629 | 0.010629 | 0.010629 | 0.98617 | -0.26423 | 0.98607 | -0.26617 | 2.9201
161 | -0.070163 | -0.017712 | 0.070185 | 0.017726 | 2.173e-05 | 1.3841e-05 | 0.10591 | 0.10591 | 0.10591 | 0.98617 | -0.26423 | 0.9865 | -0.25777 | 29.0972
162 | -0.071966 | -0.018173 | 0.072035 | 0.018216 | 6.8837e-05 | 4.3856e-05 | 0.1086 | 0.1086 | 0.1086 | 0.9865 | -0.25777 | 0.98753 | -0.23782 | 29.8352
163 | -0.073499 | -0.018583 | 0.07358 | 0.018635 | 8.1303e-05 | 5.1808e-05 | 0.11081 | 0.11081 | 0.11081 | 0.98753 | -0.23782 | 0.98873 | -0.21479 | 30.4412
164 | -0.075192 | -0.019039 | 0.07521 | 0.019051 | 1.8267e-05 | 1.1642e-05 | 0.11323 | 0.11323 | 0.11323 | 0.98873 | -0.21479 | 0.98899 | -0.20973 | 31.1076
165 | 0.0026039 | 0.00065226 | -0.0026037 | -0.00065245 | 1.31e-07 | -1.9634e-07 | 0.0039584 | 0.0039585 | 0.0039585 | 0.97879 | -0.40831 | 0.97873 | -0.40937 | 1.0875
166 | -0.0043747 | -0.0010961 | 0.0043751 | 0.001096 | 3.2847e-07 | -3.8701e-08 | 0.0066507 | 0.0066506 | 0.0066507 | 0.97879 | -0.40831 | 0.97887 | -0.40673 | 1.8271
167 | 0.0015609 | 0.00039109 | -0.0015608 | -0.00039118 | 1.8238e-08 | -9.6862e-08 | 0.002373 | 0.0023731 | 0.0023731 | 0.97873 | -0.40937 | 0.97872 | -0.40961 | 0.65194
168 | 0.0019913 | 0.00049897 | -0.0019913 | -0.00049906 | 3.04e-08 | -9.1755e-08 | 0.0030271 | 0.0030271 | 0.0030271 | 0.97887 | -0.40673 | 0.97885 | -0.40706 | 0.83162
169 | -0.0063664 | -0.001595 | 0.0063665 | 0.001595 | 6.7608e-08 | 1.907e-08 | 0.0096776 | 0.0096776 | 0.0096776 | 0.97887 | -0.40673 | 0.97888 | -0.40651 | 2.6587
170 | -0.076754 | -0.019438 | 0.076781 | 0.019455 | 2.7091e-05 | 1.7269e-05 | 0.11555 | 0.11555 | 0.11555 | 0.98899 | -0.20973 | 0.98937 | -0.20238 | 31.7456
171 | -0.07824 | -0.019821 | 0.078337 | 0.019882 | 9.6524e-05 | 6.1537e-05 | 0.11775 | 0.11775 | 0.11775 | 0.98937 | -0.20238 | 0.9907 | -0.17673 | 32.3486
172 | 0.0016647 | 0.00041682 | -0.0016647 | -0.0004171 | 6.2215e-08 | -2.8596e-07 | 0.0025303 | 0.0025304 | 0.0025304 | 0.97895 | -0.40407 | 0.97891 | -0.40485 | 0.69516
173 | -0.0024253 | -0.00060744 | 0.0024254 | 0.00060736 | 4.2346e-08 | -7.7375e-08 | 0.0036864 | 0.0036864 | 0.0036864 | 0.97895 | -0.40407 | 0.97897 | -0.4037 | 1.0127
174 | 0.0008317 | 0.00020834 | -0.0008317 | -0.00020844 | 4.9521e-09 | -1.007e-07 | 0.0012642 | 0.0012643 | 0.0012643 | 0.97891 | -0.40485 | 0.9789 | -0.40498 | 0.34732
175 | -0.003186 | -0.00079801 | 0.0031861 | 0.00079794 | 8.6161e-08 | -6.8051e-08 | 0.0048426 | 0.0048425 | 0.0048426 | 0.97897 | -0.4037 | 0.97899 | -0.40313 | 1.3304
176 | 0.0099218 | 0.0024874 | -0.0099186 | -0.0024858 | 3.1844e-06 | 1.5585e-06 | 0.015 | 0.015 | 0.015 | 0.98426 | -0.30308 | 0.98392 | -0.30982 | 4.121
177 | 0.0056472 | 0.0014143 | -0.0056456 | -0.001414 | 1.6486e-06 | 2.8665e-07 | 0.0085313 | 0.0085316 | 0.0085316 | 0.98493 | -0.29002 | 0.98462 | -0.29615 | 2.3439
178 | 0.0020324 | 0.00050915 | -0.0020324 | -0.00050936 | 7.134e-08 | -2.108e-07 | 0.0030715 | 0.0030716 | 0.0030716 | 0.98462 | -0.29615 | 0.98458 | -0.29689 | 0.84383
179 | 0.0036131 | 0.00090486 | -0.0036127 | -0.0009051 | 4.7704e-07 | -2.3729e-07 | 0.0054602 | 0.0054603 | 0.0054603 | 0.98462 | -0.29615 | 0.98447 | -0.29892 | 1.5001
180 | 0.0018085 | 0.00045293 | -0.0018084 | -0.00045323 | 7.6256e-08 | -2.9724e-07 | 0.0027334 | 0.0027335 | 0.0027335 | 0.98447 | -0.29892 | 0.98443 | -0.29981 | 0.75096
181 | 0.026503 | 0.0066482 | -0.0265 | -0.0066465 | 2.7652e-06 | 1.7092e-06 | 0.039706 | 0.039706 | 0.039706 | 0.99327 | -0.1287 | 0.99316 | -0.13089 | 10.9082
182 | 0.0068913 | 0.0017271 | -0.0068908 | -0.001727 | 4.6557e-07 | 1.4364e-07 | 0.010264 | 0.010264 | 0.010264 | 0.99909 | -0.017507 | 0.99902 | -0.018925 | 2.8197
183 | 0.02264 | 0.0056791 | -0.022633 | -0.0056751 | 6.4403e-06 | 3.9287e-06 | 0.033922 | 0.033922 | 0.033922 | 0.99316 | -0.13089 | 0.99285 | -0.13686 | 9.3193
184 | 0.022125 | 0.0055478 | -0.022125 | -0.0055474 | 5.6944e-07 | 3.4659e-07 | 0.033161 | 0.033161 | 0.033161 | 0.99285 | -0.13686 | 0.99282 | -0.1374 | 9.1101
185 | 0.021647 | 0.0054277 | -0.021645 | -0.0054263 | 2.3466e-06 | 1.4249e-06 | 0.032445 | 0.032445 | 0.032445 | 0.99282 | -0.1374 | 0.99271 | -0.13967 | 8.9134
186 | -0.0019371 | -0.00048549 | 0.0019372 | 0.00048544 | 1.6143e-08 | -5.5526e-08 | 0.0029054 | 0.0029054 | 0.0029054 | 0.99213 | -0.15083 | 0.99214 | -0.15066 | 0.79818
187 | -0.0080097 | -0.0020074 | 0.0080109 | 0.0020078 | 1.1371e-06 | 4.5636e-07 | 0.012013 | 0.012013 | 0.012013 | 0.99214 | -0.15066 | 0.99229 | -0.14768 | 3.3003
188 | -0.011388 | -0.0028541 | 0.011389 | 0.0028546 | 1.0221e-06 | 5.3341e-07 | 0.017076 | 0.017076 | 0.017076 | 0.99229 | -0.14768 | 0.99239 | -0.14579 | 4.6913
189 | -0.012162 | -0.0030485 | 0.012162 | 0.0030487 | 3.2644e-07 | 1.751e-07 | 0.018236 | 0.018236 | 0.018236 | 0.99239 | -0.14579 | 0.99242 | -0.14523 | 5.0099
190 | -0.013703 | -0.0034347 | 0.013704 | 0.0034355 | 1.5377e-06 | 8.586e-07 | 0.020546 | 0.020546 | 0.020546 | 0.99242 | -0.14523 | 0.99254 | -0.14287 | 5.6444
191 | 0.014467 | 0.0036275 | -0.014465 | -0.0036263 | 2.2061e-06 | 1.2502e-06 | 0.021687 | 0.021687 | 0.021687 | 0.99271 | -0.13967 | 0.99254 | -0.14287 | 5.9578
192 | -0.0026026 | -0.00065228 | 0.0026027 | 0.00065216 | 7.3674e-08 | -1.1933e-07 | 0.0039037 | 0.0039036 | 0.0039037 | 0.99208 | -0.15151 | 0.99211 | -0.15092 | 1.0724
193 | 0.0014595 | 0.00036559 | -0.0014595 | -0.00036579 | 3.0485e-08 | -1.9955e-07 | 0.002189 | 0.0021891 | 0.0021891 | 0.99211 | -0.15092 | 0.99209 | -0.15136 | 0.6014
194 | 0.041374 | 0.010403 | -0.041338 | -0.010381 | 3.562e-05 | 2.2478e-05 | 0.062066 | 0.062066 | 0.062066 | 0.99211 | -0.15092 | 0.99118 | -0.16896 | 17.0511
195 | -0.046976 | -0.011807 | 0.046992 | 0.011817 | 1.5967e-05 | 1.0108e-05 | 0.070468 | 0.070468 | 0.070468 | 0.99211 | -0.15092 | 0.99248 | -0.1438 | 19.3593
196 | 0.0015398 | 0.00038553 | -0.0015397 | -0.00038589 | 6.1621e-08 | -3.5842e-07 | 0.0023093 | 0.0023094 | 0.0023094 | 0.99211 | -0.15092 | 0.99207 | -0.15176 | 0.63446
197 | 0.28548 | 0.073059 | -0.28521 | -0.072885 | 0.00027304 | 0.00017391 | 0.42737 | 0.42737 | 0.42737 | 0.99524 | -0.090155 | 0.9942 | -0.10993 | 29.3522
198 | 0.0016804 | 0.00042115 | -0.0016804 | -0.00042116 | 7.3573e-10 | -3.5742e-09 | 0.0025115 | 0.0025115 | 0.0025115 | 0.99564 | -0.082573 | 0.99564 | -0.082582 | 0.68997
199 | 0.0058825 | 0.0014743 | -0.0058821 | -0.0014742 | 3.5967e-07 | 7.1307e-08 | 0.0088258 | 0.0088259 | 0.0088259 | 0.99178 | -0.1573 | 0.99171 | -0.15859 | 2.4247
200 | 0.088561 | 0.022316 | -0.088544 | -0.022305 | 1.7059e-05 | 1.0885e-05 | 0.13291 | 0.13291 | 0.13291 | 0.99178 | -0.1573 | 0.99157 | -0.16133 | 36.515
201 | 0.0023217 | 0.00058172 | -0.0023216 | -0.00058185 | 5.9289e-08 | -1.3068e-07 | 0.0034808 | 0.0034809 | 0.0034809 | 0.99248 | -0.1438 | 0.99246 | -0.14434 | 0.95628
202 | -0.0030051 | -0.00075315 | 0.0030052 | 0.00075307 | 7.7587e-08 | -8.0356e-08 | 0.0045202 | 0.0045202 | 0.0045202 | 0.98925 | -0.20636 | 0.98928 | -0.20582 | 1.2418
203 | -0.0055603 | -0.0013934 | 0.0055606 | 0.0013935 | 3.5302e-07 | 5.3114e-08 | 0.0083633 | 0.0083633 | 0.0083633 | 0.98928 | -0.20582 | 0.98935 | -0.20449 | 2.2976
204 | 0.0087684 | 0.0021977 | -0.0087676 | -0.0021974 | 7.7509e-07 | 3.4346e-07 | 0.013188 | 0.013188 | 0.013188 | 0.98935 | -0.20449 | 0.98926 | -0.20634 | 3.6231
205 | -0.014329 | -0.0035912 | 0.014336 | 0.0035949 | 6.6358e-06 | 3.7574e-06 | 0.021551 | 0.021551 | 0.021551 | 0.98935 | -0.20449 | 0.98985 | -0.19477 | 5.9207
206 | -0.033693 | -0.0084477 | 0.033704 | 0.0084551 | 1.1891e-05 | 7.4512e-06 | 0.05065 | 0.05065 | 0.05065 | 0.98985 | -0.19477 | 0.99023 | -0.18737 | 13.9149
207 | -0.0021482 | -0.00053839 | 0.0021483 | 0.0005382 | 7.115e-08 | -1.8756e-07 | 0.003232 | 0.003232 | 0.003232 | 0.98902 | -0.21094 | 0.98905 | -0.21025 | 0.88792
208 | 0.004479 | 0.0011225 | -0.0044788 | -0.0011225 | 1.6269e-07 | -1.9074e-08 | 0.0067305 | 0.0067306 | 0.0067306 | 0.99023 | -0.18737 | 0.99019 | -0.18813 | 1.8491
209 | -0.038183 | -0.0095776 | 0.038217 | 0.0095987 | 3.3531e-05 | 2.111e-05 | 0.057381 | 0.057381 | 0.057381 | 0.99023 | -0.18737 | 0.99118 | -0.16896 | 15.764
210 | 0.0074377 | 0.0018639 | -0.0074375 | -0.0018639 | 1.6689e-07 | 6.3607e-08 | 0.011343 | 0.011343 | 0.011343 | 0.97571 | -0.46724 | 0.97569 | -0.46771 | 3.1162
211 | 0.0045998 | 0.0011527 | -0.0045995 | -0.0011527 | 3.0526e-07 | -1.1201e-08 | 0.0070151 | 0.0070152 | 0.0070152 | 0.97569 | -0.46771 | 0.97562 | -0.46911 | 1.9273
212 | 0.015313 | 0.0038391 | -0.01531 | -0.0038372 | 3.2935e-06 | 1.908e-06 | 0.02339 | 0.02339 | 0.02339 | 0.97424 | -0.49628 | 0.97401 | -0.50079 | 6.4257
213 | -0.13074 | -0.033205 | 0.13101 | 0.033375 | 0.00026589 | 0.00016994 | 0.19771 | 0.19771 | 0.19771 | 0.98475 | -0.29101 | 0.98694 | -0.24885 | 54.3169
214 | 0.0021598 | 0.00054125 | -0.0021598 | -0.00054129 | 1.6285e-08 | -3.955e-08 | 0.0032941 | 0.0032941 | 0.0032941 | 0.97562 | -0.46911 | 0.97561 | -0.46926 | 0.90498
215 | 0.28036 | 0.07149 | -0.28017 | -0.071373 | 0.00018438 | 0.00011743 | 0.4208 | 0.4208 | 0.4208 | 0.99241 | -0.14411 | 0.9917 | -0.15774 | 28.9014
216 | -0.28182 | -0.071857 | 0.28229 | 0.072154 | 0.00046584 | 0.0002967 | 0.423 | 0.423 | 0.423 | 0.99241 | -0.14411 | 0.9942 | -0.10993 | 29.0521
217 | 0.27732 | 0.070658 | -0.27712 | -0.070528 | 0.00020455 | 0.00013026 | 0.41653 | 0.41653 | 0.41653 | 0.9917 | -0.15774 | 0.9909 | -0.17304 | 28.6076
218 | 0.0028514 | 0.00071463 | -0.0028514 | -0.00071463 | 7.5138e-10 | -9.3228e-10 | 0.0042785 | 0.0042785 | 0.0042785 | 0.9917 | -0.15774 | 0.9917 | -0.15774 | 1.1754
219 | 0.0029194 | 0.00073149 | -0.0029193 | -0.00073156 | 6.4719e-08 | -7.5801e-08 | 0.0043694 | 0.0043694 | 0.0043694 | 0.9942 | -0.10993 | 0.99418 | -0.11039 | 1.2004
220 | 0.2204 | 0.05623 | -0.22036 | -0.056205 | 3.9344e-05 | 2.4983e-05 | 0.33132 | 0.33132 | 0.33132 | 0.9909 | -0.17304 | 0.9907 | -0.17673 | 22.7556
221 | 0.05672 | 0.014298 | -0.056702 | -0.014287 | 1.7674e-05 | 1.1227e-05 | 0.085204 | 0.085204 | 0.085204 | 0.9909 | -0.17304 | 0.99056 | -0.17955 | 23.4078
222 | 0.0014452 | 0.00036212 | -0.0014452 | -0.0003622 | 1.2667e-08 | -8.5506e-08 | 0.0021631 | 0.0021631 | 0.0021631 | 0.99418 | -0.11039 | 0.99417 | -0.11058 | 0.59426
223 | 0.14202 | 0.036323 | -0.14188 | -0.036236 | 0.00013679 | 8.7131e-05 | 0.21357 | 0.21357 | 0.21357 | 0.9907 | -0.17673 | 0.98966 | -0.19666 | 29.337
224 | 0.055268 | 0.013927 | -0.055236 | -0.013907 | 3.2243e-05 | 2.0475e-05 | 0.08305 | 0.08305 | 0.08305 | 0.99056 | -0.17955 | 0.98993 | -0.19175 | 22.816
225 | 0.14028 | 0.035833 | -0.14011 | -0.035727 | 0.00016506 | 0.00010513 | 0.21115 | 0.21115 | 0.21115 | 0.98966 | -0.19666 | 0.98839 | -0.22103 | 29.0047
226 | 0.053692 | 0.01352 | -0.053687 | -0.013517 | 5.2481e-06 | 3.3312e-06 | 0.08073 | 0.08073 | 0.08073 | 0.98993 | -0.19175 | 0.98982 | -0.1938 | 22.1785
227 | -0.014043 | -0.0035196 | 0.014045 | 0.0035208 | 2.0945e-06 | 1.1817e-06 | 0.021186 | 0.021186 | 0.021186 | 0.9863 | -0.26357 | 0.98646 | -0.26044 | 5.8204
228 | -0.014933 | -0.0037432 | 0.014933 | 0.0037432 | 4.7774e-08 | 2.7369e-08 | 0.022525 | 0.022525 | 0.022525 | 0.98646 | -0.26044 | 0.98647 | -0.26037 | 6.1883
229 | 0.016247 | 0.0040736 | -0.016246 | -0.0040727 | 1.4847e-06 | 8.6631e-07 | 0.024527 | 0.024527 | 0.024527 | 0.9857 | -0.2738 | 0.98561 | -0.27572 | 6.7382
230 | -0.020768 | -0.0052066 | 0.020769 | 0.0052076 | 1.5384e-06 | 9.3137e-07 | 0.031352 | 0.031352 | 0.031352 | 0.9857 | -0.2738 | 0.98578 | -0.27225 | 8.6131
231 | -0.022989 | -0.0057637 | 0.022995 | 0.0057677 | 6.4624e-06 | 3.9534e-06 | 0.034701 | 0.034701 | 0.034701 | 0.98578 | -0.27225 | 0.98609 | -0.26635 | 9.5334
232 | -0.029702 | -0.0074486 | 0.02971 | 0.0074538 | 8.2787e-06 | 5.1582e-06 | 0.044822 | 0.044822 | 0.044822 | 0.98609 | -0.26635 | 0.98639 | -0.2605 | 12.3138
233 | -0.035953 | -0.0090183 | 0.035965 | 0.009026 | 1.2198e-05 | 7.6655e-06 | 0.05424 | 0.05424 | 0.05424 | 0.98639 | -0.2605 | 0.98675 | -0.25339 | 14.901
234 | -0.038119 | -0.0095658 | 0.038119 | 0.0095661 | 4.4998e-07 | 2.8335e-07 | 0.057487 | 0.057487 | 0.057487 | 0.98675 | -0.25339 | 0.98677 | -0.25314 | 15.7932
235 | -0.015622 | -0.0039161 | 0.015622 | 0.0039161 | 1.2774e-08 | 7.3927e-09 | 0.023566 | 0.023566 | 0.023566 | 0.98647 | -0.26037 | 0.98647 | -0.26036 | 6.4741
236 | -0.010722 | -0.0026862 | 0.010724 | 0.0026871 | 1.6859e-06 | 8.6769e-07 | 0.016328 | 0.016328 | 0.016328 | 0.97713 | -0.43979 | 0.9773 | -0.43649 | 4.4856
237 | -0.013575 | -0.0034015 | 0.013575 | 0.0034021 | 9.4696e-07 | 5.3197e-07 | 0.020668 | 0.020668 | 0.020668 | 0.9773 | -0.43649 | 0.97737 | -0.43503 | 5.6781
238 | -0.016727 | -0.004192 | 0.016729 | 0.0041928 | 1.4642e-06 | 8.6165e-07 | 0.025467 | 0.025467 | 0.025467 | 0.97737 | -0.43503 | 0.97746 | -0.43319 | 6.9963
239 | -0.0058174 | -0.0014578 | 0.0058178 | 0.0014579 | 3.9996e-07 | 8.9992e-08 | 0.0089153 | 0.0089152 | 0.0089153 | 0.97096 | -0.56087 | 0.97103 | -0.55943 | 2.4493
240 | 0.0027557 | 0.00069047 | -0.0027556 | -0.00069062 | 1.2442e-07 | -1.5045e-07 | 0.0042232 | 0.0042233 | 0.0042233 | 0.97096 | -0.56087 | 0.97091 | -0.56182 | 1.1602
241 | -0.013643 | -0.0034189 | 0.013647 | 0.0034207 | 3.1962e-06 | 1.8043e-06 | 0.020907 | 0.020907 | 0.020907 | 0.97103 | -0.55943 | 0.97128 | -0.55451 | 5.7437
242 | 0.0078255 | 0.001961 | -0.0078254 | -0.001961 | 8.2143e-08 | 3.3729e-08 | 0.011992 | 0.011992 | 0.011992 | 0.97103 | -0.55943 | 0.97102 | -0.55965 | 3.2944
243 | -0.014974 | -0.0037535 | 0.014974 | 0.0037536 | 8.4724e-08 | 4.891e-08 | 0.022941 | 0.022941 | 0.022941 | 0.97128 | -0.55451 | 0.97129 | -0.55439 | 6.3025
244 | 0.0057027 | 0.001429 | -0.0057024 | -0.0014289 | 3.061e-07 | 6.3695e-08 | 0.0087389 | 0.008739 | 0.008739 | 0.97102 | -0.55965 | 0.97096 | -0.56078 | 2.4008
245 | -0.01713 | -0.0042939 | 0.017133 | 0.0042955 | 2.6732e-06 | 1.5827e-06 | 0.026244 | 0.026244 | 0.026244 | 0.97129 | -0.55439 | 0.97145 | -0.55112 | 7.2099
246 | 0.0035786 | 0.00089666 | -0.0035783 | -0.0008968 | 3.1792e-07 | -1.4513e-07 | 0.0054842 | 0.0054843 | 0.0054843 | 0.97096 | -0.56078 | 0.97087 | -0.56264 | 1.5067
247 | -0.018459 | -0.0046279 | 0.018465 | 0.004631 | 5.2756e-06 | 3.1585e-06 | 0.028275 | 0.028275 | 0.028275 | 0.97145 | -0.55112 | 0.97176 | -0.54512 | 7.768
248 | -0.13253 | -0.033756 | 0.13254 | 0.033768 | 1.8158e-05 | 1.1605e-05 | 0.20001 | 0.20001 | 0.20001 | 0.98694 | -0.24885 | 0.98709 | -0.24601 | 54.9465
249 | -0.13409 | -0.034155 | 0.1341 | 0.03416 | 8.4488e-06 | 5.4002e-06 | 0.20233 | 0.20233 | 0.20233 | 0.98709 | -0.24601 | 0.98716 | -0.24471 | 55.5862
250 | -0.13564 | -0.034547 | 0.13576 | 0.034621 | 0.00011605 | 7.4177e-05 | 0.20466 | 0.20466 | 0.20466 | 0.98716 | -0.24471 | 0.98808 | -0.22698 | 56.2254
251 | 0.025844 | 0.006487 | -0.025836 | -0.0064818 | 8.4551e-06 | 5.2324e-06 | 0.039545 | 0.039545 | 0.039545 | 0.97257 | -0.52912 | 0.97222 | -0.53598 | 10.864
252 | 0.023656 | 0.0059354 | -0.023653 | -0.005934 | 2.3349e-06 | 1.4354e-06 | 0.036208 | 0.036208 | 0.036208 | 0.97222 | -0.53598 | 0.97211 | -0.53805 | 9.9474
253 | 0.021128 | 0.005301 | -0.021121 | -0.005297 | 6.5873e-06 | 4.0078e-06 | 0.032342 | 0.032342 | 0.032342 | 0.97211 | -0.53805 | 0.97178 | -0.54459 | 8.8852
254 | 0.019809 | 0.0049681 | -0.019808 | -0.0049678 | 5.0078e-07 | 3.0252e-07 | 0.030333 | 0.030333 | 0.030333 | 0.97178 | -0.54459 | 0.97176 | -0.54512 | 8.3333
255 | 0.020205 | 0.0050696 | -0.020197 | -0.0050648 | 8.0911e-06 | 4.8809e-06 | 0.030454 | 0.030455 | 0.030455 | 0.9873 | -0.24418 | 0.98687 | -0.25258 | 8.3666
256 | -0.02995 | -0.0075118 | 0.029953 | 0.0075137 | 2.9455e-06 | 1.8358e-06 | 0.045141 | 0.045141 | 0.045141 | 0.9873 | -0.24418 | 0.9874 | -0.24211 | 12.4014
257 | 0.01925 | 0.0048274 | -0.01925 | -0.0048273 | 1.432e-07 | 8.5859e-08 | 0.029027 | 0.029027 | 0.029027 | 0.98687 | -0.25258 | 0.98686 | -0.25273 | 7.9744
258 | -0.031325 | -0.0078576 | 0.031349 | 0.0078729 | 2.4595e-05 | 1.5364e-05 | 0.047209 | 0.047209 | 0.047209 | 0.9874 | -0.24211 | 0.98825 | -0.22566 | 12.9695
259 | 0.017752 | 0.0044519 | -0.017748 | -0.0044499 | 3.3625e-06 | 1.9921e-06 | 0.026768 | 0.026768 | 0.026768 | 0.98686 | -0.25273 | 0.98666 | -0.25671 | 7.3538
260 | 0.00342 | 0.00085701 | -0.0034198 | -0.00085709 | 1.2898e-07 | -8.3641e-08 | 0.0051494 | 0.0051495 | 0.0051495 | 0.98825 | -0.22566 | 0.98821 | -0.22645 | 1.4147
261 | -0.034769 | -0.00873 | 0.034774 | 0.0087328 | 4.5453e-06 | 2.8523e-06 | 0.052358 | 0.052358 | 0.052358 | 0.98825 | -0.22566 | 0.98839 | -0.22292 | 14.3841
262 | 0.016315 | 0.0040906 | -0.016312 | -0.004089 | 2.8343e-06 | 1.6545e-06 | 0.024606 | 0.024606 | 0.024606 | 0.98666 | -0.25671 | 0.98647 | -0.26036 | 6.7599
263 | -0.036941 | -0.009276 | 0.036942 | 0.0092766 | 1.0394e-06 | 6.537e-07 | 0.055621 | 0.055621 | 0.055621 | 0.98839 | -0.22292 | 0.98842 | -0.22233 | 15.2805
264 | -0.03911 | -0.0098198 | 0.039138 | 0.0098376 | 2.8193e-05 | 1.7765e-05 | 0.058884 | 0.058884 | 0.058884 | 0.98842 | -0.22233 | 0.9892 | -0.20723 | 16.1769
265 | 0.013306 | 0.0033352 | -0.013306 | -0.0033349 | 5.3294e-07 | 2.957e-07 | 0.020033 | 0.020033 | 0.020033 | 0.98839 | -0.22307 | 0.98834 | -0.22391 | 5.5035
266 | -0.015865 | -0.0039763 | 0.015866 | 0.0039772 | 1.5109e-06 | 8.7642e-07 | 0.023884 | 0.023884 | 0.023884 | 0.98839 | -0.22307 | 0.98849 | -0.22107 | 6.5616
267 | 0.010399 | 0.0026063 | -0.010398 | -0.0026058 | 9.9235e-07 | 4.9676e-07 | 0.015656 | 0.015656 | 0.015656 | 0.98834 | -0.22391 | 0.98824 | -0.22592 | 4.3011
268 | -0.018425 | -0.0046186 | 0.018427 | 0.0046198 | 2.0376e-06 | 1.2135e-06 | 0.027737 | 0.027737 | 0.027737 | 0.98849 | -0.22107 | 0.98861 | -0.21875 | 7.62
269 | 0.0073372 | 0.0018388 | -0.0073371 | -0.0018387 | 4.305e-08 | 1.5501e-08 | 0.011048 | 0.011048 | 0.011048 | 0.98824 | -0.22592 | 0.98823 | -0.22604 | 3.0351
270 | -0.020986 | -0.005261 | 0.020986 | 0.0052615 | 7.7243e-07 | 4.6789e-07 | 0.031587 | 0.031587 | 0.031587 | 0.98861 | -0.21875 | 0.98865 | -0.21798 | 8.6778
271 | 0.0048897 | 0.0012254 | -0.0048895 | -0.0012254 | 1.4288e-07 | 1.389e-09 | 0.0073625 | 0.0073625 | 0.0073625 | 0.98823 | -0.22604 | 0.9882 | -0.22665 | 2.0227
272 | -0.023152 | -0.0058042 | 0.02316 | 0.0058089 | 7.6897e-06 | 4.7048e-06 | 0.034847 | 0.034846 | 0.034847 | 0.98865 | -0.21798 | 0.98901 | -0.21101 | 9.5732
273 | 0.002444 | 0.00061245 | -0.002444 | -0.00061252 | 3.569e-08 | -6.7188e-08 | 0.0036801 | 0.0036801 | 0.0036801 | 0.9882 | -0.22665 | 0.98819 | -0.22696 | 1.011
274 | -0.02316 | -0.0058089 | 0.023164 | 0.0058114 | 4.1797e-06 | 2.5572e-06 | 0.034846 | 0.034846 | 0.034846 | 0.98901 | -0.21101 | 0.9892 | -0.20723 | 9.5732
275 | -0.052217 | -0.013144 | 0.052227 | 0.013151 | 9.7936e-06 | 6.2135e-06 | 0.078535 | 0.078535 | 0.078535 | 0.98962 | -0.19772 | 0.98982 | -0.1938 | 21.5756
276 | 0.050808 | 0.012791 | -0.050782 | -0.012775 | 2.5697e-05 | 1.6296e-05 | 0.076416 | 0.076416 | 0.076416 | 0.98962 | -0.19772 | 0.98907 | -0.20831 | 20.9935
277 | 0.047905 | 0.012054 | -0.047886 | -0.012042 | 1.8253e-05 | 1.1562e-05 | 0.072087 | 0.072088 | 0.072088 | 0.98907 | -0.20831 | 0.98866 | -0.21628 | 19.8043
278 | 0.042989 | 0.010815 | -0.042956 | -0.010794 | 3.3404e-05 | 2.1106e-05 | 0.064717 | 0.064717 | 0.064717 | 0.98866 | -0.21628 | 0.98782 | -0.23256 | 17.7794
279 | 0.042956 | 0.010794 | -0.042933 | -0.010779 | 2.3089e-05 | 1.4589e-05 | 0.064717 | 0.064717 | 0.064717 | 0.98782 | -0.23256 | 0.98724 | -0.24383 | 17.7794
280 | 0.041587 | 0.010442 | -0.041585 | -0.010441 | 2.0082e-06 | 1.2678e-06 | 0.062689 | 0.062689 | 0.062689 | 0.98724 | -0.24383 | 0.98719 | -0.24484 | 17.2222
281 | 0.018485 | 0.0046366 | -0.018475 | -0.0046309 | 9.4765e-06 | 5.6463e-06 | 0.027818 | 0.027818 | 0.027818 | 0.98882 | -0.2146 | 0.98827 | -0.22536 | 7.6423
282 | -0.02273 | -0.0057006 | 0.022738 | 0.0057055 | 7.9856e-06 | 4.8772e-06 | 0.034207 | 0.034207 | 0.034207 | 0.98882 | -0.2146 | 0.9892 | -0.20723 | 9.3974
283 | 0.01482 | 0.0037148 | -0.01482 | -0.0037147 | 1.9637e-07 | 1.122e-07 | 0.022314 | 0.022314 | 0.022314 | 0.98827 | -0.22536 | 0.98825 | -0.22563 | 6.1303
284 | -0.08504 | -0.021355 | 0.085226 | 0.021474 | 0.00018666 | 0.00011907 | 0.12794 | 0.12794 | 0.12794 | 0.9892 | -0.20723 | 0.99157 | -0.16133 | 35.1475
285 | 0.013917 | 0.0034886 | -0.013911 | -0.0034851 | 6.2696e-06 | 3.525e-06 | 0.020956 | 0.020956 | 0.020956 | 0.98825 | -0.22563 | 0.98777 | -0.23509 | 5.7571
286 | 0.0033172 | 0.0008313 | -0.0033172 | -0.00083136 | 7.1945e-08 | -5.3818e-08 | 0.004978 | 0.0049781 | 0.0049781 | 0.99157 | -0.16133 | 0.99155 | -0.16179 | 1.3676
287 | 0.0085269 | 0.0021357 | -0.0085249 | -0.0021348 | 2.0083e-06 | 8.6995e-07 | 0.012845 | 0.012845 | 0.012845 | 0.98777 | -0.23509 | 0.98751 | -0.24004 | 3.5288
288 | 0.0075752 | 0.0018987 | -0.007574 | -0.0018982 | 1.2402e-06 | 4.8644e-07 | 0.011573 | 0.011573 | 0.011573 | 0.97401 | -0.50079 | 0.97383 | -0.50423 | 3.1794
289 | 0.13872 | 0.035378 | -0.13869 | -0.035358 | 3.0979e-05 | 1.9802e-05 | 0.20906 | 0.20906 | 0.20906 | 0.98839 | -0.22103 | 0.98815 | -0.22565 | 57.4332
290 | 0.13723 | 0.034993 | -0.13722 | -0.034987 | 8.832e-06 | 5.6454e-06 | 0.20686 | 0.20686 | 0.20686 | 0.98815 | -0.22565 | 0.98808 | -0.22698 | 56.8294
291 | 0.003121 | 0.00078212 | -0.003121 | -0.00078219 | 7.3912e-08 | -6.841e-08 | 0.0046855 | 0.0046855 | 0.0046855 | 0.99118 | -0.16896 | 0.99116 | -0.16946 | 1.2872
292 | 0.040287 | 0.010115 | -0.040271 | -0.010105 | 1.5948e-05 | 1.0059e-05 | 0.060731 | 0.060731 | 0.060731 | 0.98719 | -0.24484 | 0.98677 | -0.25314 | 16.6845
293 | 0.0014435 | 0.00036131 | -0.0014434 | -0.00036165 | 5.2633e-08 | -3.3481e-07 | 0.0021911 | 0.0021912 | 0.0021912 | 0.98023 | -0.37999 | 0.98019 | -0.38076 | 0.60199
294 | 0.00072134 | 0.00018067 | -0.00072133 | -0.00018078 | 4.0298e-09 | -1.1038e-07 | 0.001095 | 0.001095 | 0.001095 | 0.98019 | -0.38076 | 0.98019 | -0.38087 | 0.30084
295 | 0.00070567 | 0.00017675 | -0.00070567 | -0.00017686 | 3.7723e-09 | -1.082e-07 | 0.0010709 | 0.001071 | 0.001071 | 0.98047 | -0.37533 | 0.98046 | -0.37545 | 0.29422

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.61208 | 0.15608

## res_load
| p_mw | q_mvar
0 | 0.00032747 | 8.2071e-05
1 | 0.00040583 | 0.00010171
2 | 0.0020068 | 0.00050294
3 | 0.0076284 | 0.0019119
4 | 0.0013574 | 0.00034021
5 | 0.0013596 | 0.00034075
6 | 0.0013813 | 0.0003462
7 | 0.0022081 | 0.0005534
8 | 0.0013899 | 0.00034835
9 | 0.0018718 | 0.00046911
10 | 0.0019651 | 0.00049249
11 | 0.0028063 | 0.00070333
12 | 0.0024335 | 0.0006099
13 | 0.0021994 | 0.00055122
14 | 0.0027224 | 0.00068231
15 | 0.0047742 | 0.0011965
16 | 0.0030164 | 0.00075597
17 | 0.004022 | 0.001008
18 | 0.0052596 | 0.0013182
19 | 0.00049156 | 0.0001232
20 | 0.0014057 | 0.0003523
21 | 0.0015576 | 0.00039036
22 | 0.0035121 | 0.00088023
23 | 0.0035716 | 0.00089514
24 | 0.0045744 | 0.0011464
25 | 0.0029379 | 0.00073631
26 | 0.0048376 | 0.0012124
27 | 0.0029348 | 0.00073552
28 | 0.003168 | 0.00079398
29 | 0.0020331 | 0.00050955
30 | 0.0016211 | 0.00040629
31 | 0.0084432 | 0.0021161
32 | 0.003962 | 0.00099297
33 | 0.0035839 | 0.00089821
34 | 0.003123 | 0.00078271
35 | 0.0048974 | 0.0012274
36 | 0.0020773 | 0.00052063
37 | 0.0026593 | 0.00066649
38 | 0.001645 | 0.00041228
39 | 0.0042078 | 0.0010546
40 | 0.0049567 | 0.0012423
41 | 0.0014696 | 0.00036832
42 | 0.0020276 | 0.00050815
43 | 0.0021114 | 0.00052917
44 | 0.01135 | 0.0028446
45 | 0.0084216 | 0.0021106
46 | 0.0036865 | 0.00092393
47 | 0.0039174 | 0.00098178
48 | 0.0057226 | 0.0014342
49 | 0.0035624 | 0.00089282
50 | 0.001913 | 0.00047945
51 | 0.0014599 | 0.00036588
52 | 0.004047 | 0.0010143
53 | 0.0012268 | 0.00030747
54 | 0.0012839 | 0.00032178
55 | 0.0020216 | 0.00050665
56 | 0.0010341 | 0.00025918
57 | 0.0014888 | 0.00037312
58 | 0.0060267 | 0.0015104
59 | 0.0027315 | 0.00068459
60 | 0.0025843 | 0.00064768
61 | 0.0028265 | 0.00070838
62 | 0.00072843 | 0.00018256
63 | 0.0031358 | 0.0007859
64 | 0.0012256 | 0.00030717
65 | 0.00078499 | 0.00019674
66 | 0.00054393 | 0.00013632
67 | 0.00085951 | 0.00021541
68 | 0.00083464 | 0.00020918
69 | 0.00070785 | 0.0001774
70 | 0.00082583 | 0.00020697
71 | 0.013294 | 0.0033318
72 | 0.0027826 | 0.00069738
73 | 0.0010702 | 0.00026821
74 | 0.00052012 | 0.00013036
75 | 0.0028968 | 0.00072601
76 | 0.00086014 | 0.00021557
77 | 0.00083364 | 0.00020893
78 | 0.00070728 | 0.00017726
79 | 0.00070866 | 0.00017761
80 | 0.00054893 | 0.00013757
81 | 0.00083852 | 0.00021015
82 | 0.0070437 | 0.0017653
83 | 0.0017809 | 0.00044635
84 | 0.005352 | 0.0013413
85 | 0.0014641 | 0.00036693
86 | 0.0016117 | 0.00040392
87 | 0.0017709 | 0.00044383
88 | 0.0010429 | 0.00026137
89 | 0.0015608 | 0.00039118
90 | 0.0019913 | 0.00049906
91 | 0.0029897 | 0.0007493
92 | 0.0022832 | 0.00057222
93 | 0.00074344 | 0.00018632
94 | 0.0015437 | 0.00038688
95 | 0.0014594 | 0.00036575
96 | 0.00076059 | 0.00019062
97 | 0.00083297 | 0.00020876
98 | 0.00076067 | 0.00019064
99 | 0.0008317 | 0.00020844
100 | 0.00078433 | 0.00019657
101 | 0.0090909 | 0.0022784
102 | 0.0099186 | 0.0024858
103 | 0.0025398 | 0.00063653
104 | 0.0028139 | 0.00070523
105 | 0.0053367 | 0.0013375
106 | 0.0020324 | 0.00050936
107 | 0.0018042 | 0.00045217
108 | 0.0018084 | 0.00045323
109 | 0.0031641 | 0.00079301
110 | 0.0037599 | 0.00094232
111 | 0.003941 | 0.0009877
112 | 0.0068908 | 0.001727
113 | 0.0038602 | 0.00096745
114 | 0.00050819 | 0.00012736
115 | 0.00047773 | 0.00011973
116 | 0.0019371 | 0.00048549
117 | 0.0060726 | 0.0015219
118 | 0.0033766 | 0.00084627
119 | 0.00077348 | 0.00019385
120 | 0.0015403 | 0.00038603
121 | 0.0071771 | 0.0017988
122 | 0.00076104 | 0.00019073
123 | 0.0026026 | 0.00065228
124 | 0.0013737 | 0.00034428
125 | 0.0015668 | 0.00039269
126 | 0.0030051 | 0.00075315
127 | 0.0025551 | 0.00064036
128 | 0.0087676 | 0.0021974
129 | 0.0010989 | 0.00027542
130 | 0.0021482 | 0.00053839
131 | 0.0014718 | 0.00036888
132 | 0.0041629 | 0.0010433
133 | 0.0028377 | 0.00071119
134 | 0.0072054 | 0.0018059
135 | 0.0016059 | 0.00040248
136 | 0.0024397 | 0.00061145
137 | 0.0021598 | 0.00054129
138 | 0.0014641 | 0.00036693
139 | 0.0028514 | 0.00071463
140 | 0.0014741 | 0.00036945
141 | 0.0014341 | 0.00035942
142 | 0.0014452 | 0.0003622
143 | 0.001609 | 0.00040326
144 | 0.0015436 | 0.00038687
145 | 0.0016804 | 0.00042116
146 | 0.00094344 | 0.00023645
147 | 0.0008876 | 0.00022245
148 | 0.0045208 | 0.001133
149 | 0.0022204 | 0.00055649
150 | 0.0022192 | 0.00055618
151 | 0.006707 | 0.0016809
152 | 0.0062427 | 0.0015646
153 | 0.0021538 | 0.00053978
154 | 0.00068973 | 0.00017286
155 | 0.0072086 | 0.0018067
156 | 0.0028507 | 0.00071446
157 | 0.0031518 | 0.00078992
158 | 0.0029574 | 0.00074118
159 | 0.0030617 | 0.00076734
160 | 0.0027556 | 0.00069062
161 | 0.0013279 | 0.00033279
162 | 0.0021227 | 0.00053199
163 | 0.0021558 | 0.0005403
164 | 0.0021238 | 0.00053228
165 | 0.0013263 | 0.00033241
166 | 0.0035783 | 0.0008968
167 | 0.0015202 | 0.00038101
168 | 0.0015445 | 0.00038708
169 | 0.0015437 | 0.00038688
170 | 0.0021271 | 0.00053311
171 | 0.00218 | 0.00054635
172 | 0.0025258 | 0.00063302
173 | 0.001312 | 0.00032882
174 | 0.0013439 | 0.00033682
175 | 0.0097445 | 0.0024422
176 | 0.00094697 | 0.00023733
177 | 0.0013722 | 0.00034391
178 | 0.0014981 | 0.00037547
179 | 0.0014334 | 0.00035925
180 | 0.0034198 | 0.00085709
181 | 0.0021673 | 0.00054319
182 | 0.00068973 | 0.00017286
183 | 0.0021673 | 0.00054319
184 | 0.0025582 | 0.00064114
185 | 0.0029072 | 0.00072862
186 | 0.0025593 | 0.00064142
187 | 0.0030605 | 0.00076703
188 | 0.0025582 | 0.00064114
189 | 0.0024475 | 0.00061339
190 | 0.0021655 | 0.00054272
191 | 0.0024455 | 0.0006129
192 | 0.0014092 | 0.00035318
193 | 0.0014599 | 0.00036589
194 | 0.0028773 | 0.00072113
195 | 0.0048971 | 0.0012273
196 | 0.0013456 | 0.00033724
197 | 0.0042456 | 0.001064
198 | 0.0036552 | 0.00091608
199 | 0.00090237 | 0.00022616
200 | 0.0053842 | 0.0013494
201 | 0.0033172 | 0.00083136
202 | 0.0016728 | 0.00041925
203 | 0.0058821 | 0.0014742
204 | 0.0077348 | 0.0019385
205 | 0.007574 | 0.0018982
206 | 0.0013932 | 0.00034918
207 | 0.0014594 | 0.00036576
208 | 0.0014599 | 0.0003659
209 | 0.002444 | 0.00061252
210 | 0.0015397 | 0.00038589
211 | 0.0014595 | 0.00036579
212 | 0.003121 | 0.00078219
213 | 0.0023216 | 0.00058185
214 | 0.0044788 | 0.0011225
215 | 0.0012987 | 0.00032549
216 | 0.0021513 | 0.00053916
217 | 0.0013997 | 0.00035081
218 | 0.00070866 | 0.00017761
219 | 0.00072211 | 0.00018098
220 | 0.00072133 | 0.00018078
221 | 0.0007285 | 0.00018258
222 | 0.0007061 | 0.00017696
223 | 0.00070567 | 0.00017686

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1