## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1040-6_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1040-6_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1040-6_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1040-6_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1040-6_0_3_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_1040-6_0_3_node_26 | 0.4 | n |  | TRUE
6 | bus_LV_1040-6_0_3_node_37 | 0.4 | n |  | TRUE
7 | bus_LV_1040-6_0_3_node_35 | 0.4 | n |  | TRUE
8 | bus_LV_1040-6_0_3_node_36 | 0.4 | n |  | TRUE
9 | bus_LV_1040-6_0_3_node_4 | 0.4 | n |  | TRUE
10 | bus_LV_1040-6_0_3_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_1040-6_0_3_node_23 | 0.4 | n |  | TRUE
12 | bus_LV_1040-6_0_3_node_22 | 0.4 | n |  | TRUE
13 | bus_LV_1040-6_0_3_node_6 | 0.4 | n |  | TRUE
14 | bus_LV_1040-6_0_3_node_15 | 0.4 | n |  | TRUE
15 | bus_LV_1040-6_0_3_node_29 | 0.4 | n |  | TRUE
16 | bus_LV_1040-6_0_3_node_25 | 0.4 | n |  | TRUE
17 | bus_LV_1040-6_0_3_node_27 | 0.4 | n |  | TRUE
18 | bus_LV_1040-6_0_3_node_31 | 0.4 | n |  | TRUE
19 | bus_LV_1040-6_0_3_node_24 | 0.4 | n |  | TRUE
20 | bus_LV_1040-6_0_3_node_20 | 0.4 | n |  | TRUE
21 | bus_LV_1040-6_0_3_node_18 | 0.4 | n |  | TRUE
22 | bus_LV_1040-6_0_3_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_1040-6_0_3_node_17 | 0.4 | n |  | TRUE
24 | bus_LV_1040-6_0_3_node_33 | 0.4 | n |  | TRUE
25 | bus_LV_1040-6_0_3_node_39 | 0.4 | n |  | TRUE
26 | bus_LV_1040-6_0_3_node_34 | 0.4 | n |  | TRUE
27 | bus_LV_1040-6_0_3_node_32 | 0.4 | n |  | TRUE
28 | bus_LV_1040-6_0_3_node_19 | 0.4 | n |  | TRUE
29 | bus_LV_1040-6_0_3_node_12 | 0.4 | n |  | TRUE
30 | bus_LV_1040-6_0_3_node_13 | 0.4 | n |  | TRUE
31 | bus_LV_1040-6_0_3_node_40 | 0.4 | n |  | TRUE
32 | bus_LV_1040-6_0_3_node_10 | 0.4 | n |  | TRUE
33 | bus_LV_1040-6_0_3_node_9 | 0.4 | n |  | TRUE
34 | bus_LV_1040-6_0_3_node_11 | 0.4 | n |  | TRUE
35 | bus_LV_1040-6_0_3_node_14 | 0.4 | n |  | TRUE
36 | bus_LV_1040-6_0_3_node_21 | 0.4 | n |  | TRUE
37 | bus_MV_3_0_node_77 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1040-6_0_3_load_0 | 0 | 0.00043071 | 0.00010795 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1040-6_0_3_load_1 | 1 | 0.00084916 | 0.00021282 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1040-6_0_3_load_3 | 3 | 0.0016325 | 0.00040914 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1040-6_0_3_load_37 | 6 | 0.00024553 | 6.1534e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1040-6_0_3_load_35 | 7 | 0.0035464 | 0.00088882 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1040-6_0_3_load_8 | 10 | 0.0010796 | 0.00027057 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1040-6_0_3_load_23 | 11 | 0.002654 | 0.00066515 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1040-6_0_3_load_22 | 12 | 0.018088 | 0.0045333 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1040-6_0_3_load_25 | 16 | 0.00019715 | 4.941e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1040-6_0_3_load_31 | 18 | 0.0022924 | 0.00057454 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1040-6_0_3_load_24 | 19 | 0.00066318 | 0.00016621 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1040-6_0_3_load_20 | 20 | 0.043311 | 0.010855 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1040-6_0_3_load_33 | 24 | 0.010041 | 0.0025164 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1040-6_0_3_load_39 | 25 | 0.0010309 | 0.00025837 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1040-6_0_3_load_34 | 26 | 0.054598 | 0.013684 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1040-6_0_3_load_32 | 27 | 0.021079 | 0.0052829 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1040-6_0_3_load_40 | 31 | 0.015116 | 0.0037885 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1040-6_0_3_load_9 | 33 | 0.0064585 | 0.0016186 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1040-6_0_3_load_14 | 35 | 0.017352 | 0.0043488 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1040-6_0_3_load_21 | 36 | 0.060847 | 0.01525 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 27 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1040-6_0_3_line_0 |  | 0 | 1 | 0.034904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1040-6_0_3_line_1 |  | 0 | 2 | 0.0011649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1040-6_0_3_line_2 |  | 1 | 3 | 0.034179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1040-6_0_3_line_3 |  | 2 | 4 | 0.009012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1040-6_0_3_line_4 |  | 2 | 5 | 0.043674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1040-6_0_3_line_5 |  | 3 | 6 | 0.15094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1040-6_0_3_line_6 |  | 4 | 11 | 0.092888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_1040-6_0_3_line_7 |  | 4 | 12 | 0.12823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_1040-6_0_3_line_8 |  | 4 | 9 | 0.039561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1040-6_0_3_line_9 |  | 5 | 16 | 0.011974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1040-6_0_3_line_10 |  | 6 | 8 | 0.039105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1040-6_0_3_line_11 |  | 7 | 8 | 0.010662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1040-6_0_3_line_12 |  | 9 | 10 | 0.00966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1040-6_0_3_line_13 |  | 11 | 19 | 0.042356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_1040-6_0_3_line_14 |  | 12 | 20 | 0.099562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1040-6_0_3_line_15 |  | 13 | 14 | 0.004118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_1040-6_0_3_line_16 |  | 13 | 15 | 0.12765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_1040-6_0_3_line_17 |  | 14 | 21 | 0.029597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_1040-6_0_3_line_18 |  | 14 | 19 | 0.05033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_1040-6_0_3_line_19 |  | 15 | 25 | 0.17376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
20 | LV_1040-6_0_3_line_20 |  | 16 | 17 | 0.01308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1040-6_0_3_line_21 |  | 17 | 18 | 0.006354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1040-6_0_3_line_22 |  | 20 | 36 | 0.018429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1040-6_0_3_line_23 |  | 21 | 27 | 0.024378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
24 | LV_1040-6_0_3_line_24 |  | 22 | 23 | 0.080185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
25 | LV_1040-6_0_3_line_25 |  | 22 | 24 | 0.062448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1040-6_0_3_line_26 |  | 22 | 25 | 0.20066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_1040-6_0_3_line_27 |  | 23 | 26 | 0.015688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_1040-6_0_3_line_28 |  | 26 | 28 | 2.616e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1040-6_0_3_line_29 |  | 28 | 29 | 0.050239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1040-6_0_3_line_30 |  | 29 | 31 | 0.027537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1040-6_0_3_line_31 |  | 30 | 31 | 0.037405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1040-6_0_3_line_32 |  | 30 | 32 | 0.10434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1040-6_0_3_line_33 |  | 32 | 33 | 0.011934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1040-6_0_3_line_34 |  | 33 | 34 | 0.013953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1040-6_0_3_line_35 |  | 34 | 35 | 0.011811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1040-6_0_3_trafo_32 | 0.63 MVA 20/0.4 kV | 37 | 27 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2661413.5891 | 1215661.6997 | 2661388.5095 | 1215683.4934 | 2661387.223 | 1215684.5717
1 | 2661414.4684 | 1215660.9356 | 2661413.5891 | 1215661.6997
2 | 2661361.0286 | 1215706.5273 | 2661387.223 | 1215684.5717
3 | 2661408.5778 | 1215654.1152 | 2661409.1781 | 1215654.8107 | 2661411.2717 | 1215657.2338 | 2661414.0781 | 1215660.4869 | 2661414.4684 | 1215660.9356
4 | 2661414.4684 | 1215660.9356 | 2661447.8319 | 1215689.1189
5 | 2661361.0286 | 1215706.5273 | 2661447.4047 | 1215830.3095
6 | 2661408.5778 | 1215654.1152 | 2661345.867 | 1215706.9024 | 2661337.8523 | 1215714.316
7 | 2661408.5778 | 1215654.1152 | 2661309.3854 | 1215572.8557
8 | 2661408.5778 | 1215654.1152 | 2661417.4863 | 1215646.6135 | 2661432.7546 | 1215635.0302 | 2661440.4308 | 1215630.6844
9 | 2661447.8319 | 1215689.1189 | 2661455.756 | 1215698.0956
10 | 2661476.2034 | 1215820.6369 | 2661447.9072 | 1215819.5335 | 2661447.4047 | 1215830.3095
11 | 2661476.2034 | 1215820.6369 | 2661486.8373 | 1215819.8652
12 | 2661440.4308 | 1215630.6844 | 2661447.8406 | 1215624.4867
13 | 2661308.506 | 1215744.8302 | 2661310.315 | 1215743.059 | 2661331.8759 | 1215719.8442 | 2661337.8523 | 1215714.316
14 | 2661309.3854 | 1215572.8557 | 2661288.7371 | 1215575.2116 | 2661264.6282 | 1215586.2373 | 2661252.6105 | 1215597.7765 | 2661222.272 | 1215616.4197
15 | 2661273.6012 | 1215781.4721 | 2661271.576 | 1215779.0386 | 2661270.9686 | 1215778.2986
16 | 2661273.6012 | 1215781.4721 | 2661290.0905 | 1215908.0529
17 | 2661249.558 | 1215783.2262 | 2661255.7362 | 1215790.8832 | 2661270.9686 | 1215778.2986
18 | 2661270.9686 | 1215778.2986 | 2661283.1223 | 1215768.2617 | 2661293.7849 | 1215759.2435 | 2661308.506 | 1215744.8302
19 | 2661290.0905 | 1215908.0529 | 2661279.2516 | 1215918.7259 | 2661271.3643 | 1215928.8844 | 2661262.8884 | 1215943.851 | 2661256.0557 | 1215957.0445 | 2661246.5186 | 1215984.4079 | 2661243.295 | 1215995.1592 | 2661223.5695 | 1216065.8864
20 | 2661464.412 | 1215707.9014 | 2661455.756 | 1215698.0956
21 | 2661469.4635 | 1215704.0288 | 2661464.412 | 1215707.9014
22 | 2661206.5706 | 1215626.0682 | 2661222.272 | 1215616.4197
23 | 2661249.558 | 1215783.2262 | 2661234.2472 | 1215764.2561
24 | 2661063.8532 | 1215944.4211 | 2661071.8886 | 1215951.6412 | 2661086.8693 | 1215936.1295 | 2661099.6095 | 1215923.6301 | 2661091.5206 | 1215912.7405 | 2661081.7313 | 1215899.5765
25 | 2661063.8532 | 1215944.4211 | 2661043.1372 | 1215954.2706 | 2661039.0989 | 1215954.8963 | 2661034.8523 | 1215954.3525 | 2661021.2236 | 1215948.3427 | 2661006.9261 | 1215942.3927 | 2661006.2235 | 1215942.1003
26 | 2661063.8532 | 1215944.4211 | 2661223.5695 | 1216065.8864
27 | 2661081.7313 | 1215899.5765 | 2661072.3772 | 1215886.9827
28 | 2661072.3772 | 1215886.9827 | 2661072.3616 | 1215886.9617
29 | 2661042.3721 | 1215846.5964 | 2661072.3616 | 1215886.9617
30 | 2661042.3721 | 1215846.5964 | 2661064.5558 | 1215830.2812
31 | 2661094.6888 | 1215808.1196 | 2661064.5558 | 1215830.2812
32 | 2661030.0274 | 1215726.2959 | 2661045.1851 | 1215743.9508 | 2661048.0519 | 1215747.26 | 2661052.4268 | 1215752.3301 | 2661054.2116 | 1215754.5164 | 2661094.6888 | 1215808.1196
33 | 2661030.0274 | 1215726.2959 | 2661039.5595 | 1215719.1155
34 | 2661050.7042 | 1215710.7202 | 2661039.5595 | 1215719.1155
35 | 2661050.7042 | 1215710.7202 | 2661060.1404 | 1215703.6164

## bus_geodata
| x | y | coords
0 | 2661413.5891 | 1215661.6997
1 | 2661387.223 | 1215684.5717
2 | 2661414.4684 | 1215660.9356
3 | 2661361.0286 | 1215706.5273
4 | 2661408.5778 | 1215654.1152
5 | 2661447.8319 | 1215689.1189
6 | 2661447.4047 | 1215830.3095
7 | 2661486.8373 | 1215819.8652
8 | 2661476.2034 | 1215820.6369
9 | 2661440.4308 | 1215630.6844
10 | 2661447.8406 | 1215624.4867
11 | 2661337.8523 | 1215714.316
12 | 2661309.3854 | 1215572.8557
13 | 2661273.6012 | 1215781.4721
14 | 2661270.9686 | 1215778.2986
15 | 2661290.0905 | 1215908.0529
16 | 2661455.756 | 1215698.0956
17 | 2661464.412 | 1215707.9014
18 | 2661469.4635 | 1215704.0288
19 | 2661308.506 | 1215744.8302
20 | 2661222.272 | 1215616.4197
21 | 2661249.558 | 1215783.2262
22 | 2661063.8532 | 1215944.4211
23 | 2661081.7313 | 1215899.5765
24 | 2661006.2235 | 1215942.1003
25 | 2661223.5695 | 1216065.8864
26 | 2661072.3772 | 1215886.9827
27 | 2661234.2472 | 1215764.2561
28 | 2661072.3616 | 1215886.9617
29 | 2661042.3721 | 1215846.5964
30 | 2661094.6888 | 1215808.1196
31 | 2661064.5558 | 1215830.2812
32 | 2661030.0274 | 1215726.2959
33 | 2661039.5595 | 1215719.1155
34 | 2661050.7042 | 1215710.7202
35 | 2661060.1404 | 1215703.6164
36 | 2661206.5706 | 1215626.0682
37 | 2661249.558 | 1215783.2262

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98817 | -0.22421 | 0.00043071 | 0.00010795
1 | 0.98797 | -0.22812 | 0.00084916 | 0.00021282
2 | 0.98818 | -0.22407 | 0 | 0
3 | 0.9878 | -0.23144 | 0.0016325 | 0.00040914
4 | 0.98826 | -0.22259 | 0 | 0
5 | 0.98808 | -0.22601 | 0 | 0
6 | 0.98728 | -0.24168 | 0.00024553 | 6.1534e-05
7 | 0.98711 | -0.24484 | 0.0035464 | 0.00088882
8 | 0.98715 | -0.24416 | 0 | 0
9 | 0.98822 | -0.22335 | 0 | 0
10 | 0.98821 | -0.22354 | 0.0010796 | 0.00027057
11 | 0.99207 | -0.14963 | 0.002654 | 0.00066515
12 | 0.98339 | -0.31631 | 0.018088 | 0.0045333
13 | 0.99584 | -0.078264 | 0 | 0
14 | 0.99597 | -0.075739 | 0 | 0
15 | 0.99169 | -0.15686 | 0 | 0
16 | 0.98805 | -0.22654 | 0.00019715 | 4.941e-05
17 | 0.98802 | -0.22708 | 0 | 0
18 | 0.98801 | -0.22734 | 0.0022924 | 0.00057454
19 | 0.99385 | -0.11588 | 0.00066318 | 0.00016621
20 | 0.97372 | -0.50507 | 0.043311 | 0.010855
21 | 0.99818 | -0.034132 | 0 | 0
22 | 0.97961 | -0.38991 | 0 | 0
23 | 0.97728 | -0.43543 | 0 | 0
24 | 0.97903 | -0.40131 | 0.010041 | 0.0025164
25 | 0.98605 | -0.26489 | 0.0010309 | 0.00025837
26 | 0.97683 | -0.44436 | 0.054598 | 0.013684
27 | 1 | 0 | -0.24757 | -0.06372
28 | 0.97682 | -0.44438 | 0 | 0
29 | 0.975 | -0.48018 | 0 | 0
30 | 0.97317 | -0.51623 | 0 | 0
31 | 0.974 | -0.49985 | 0.015116 | 0.0037885
32 | 0.97085 | -0.56207 | 0 | 0
33 | 0.97058 | -0.56732 | 0.0064585 | 0.0016186
34 | 0.97035 | -0.5718 | 0 | 0
35 | 0.97016 | -0.5756 | 0.017352 | 0.0043488
36 | 0.97268 | -0.52571 | 0.060847 | 0.01525
37 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.006278 | 0.0015717 | -0.0062768 | -0.0015714 | 1.1697e-06 | 3.0152e-07 | 0.009453 | 0.0094532 | 0.0094532 | 0.98817 | -0.22421 | 0.98797 | -0.22812 | 2.597
1 | -0.0067087 | -0.0016796 | 0.0067088 | 0.0016796 | 4.4575e-08 | 1.3605e-08 | 0.010102 | 0.010102 | 0.010102 | 0.98817 | -0.22421 | 0.98818 | -0.22407 | 2.7752
2 | 0.0054277 | 0.0013586 | -0.0054268 | -0.0013585 | 8.5642e-07 | 1.1051e-07 | 0.0081742 | 0.0081744 | 0.0081744 | 0.98797 | -0.22812 | 0.9878 | -0.23144 | 2.2457
3 | -0.0091987 | -0.0023029 | 0.0091994 | 0.0023032 | 6.4833e-07 | 2.9947e-07 | 0.013851 | 0.013851 | 0.013851 | 0.98818 | -0.22407 | 0.98826 | -0.22259 | 3.8051
4 | 0.00249 | 0.00062323 | -0.0024897 | -0.00062364 | 2.3022e-07 | -4.1211e-07 | 0.0037491 | 0.0037493 | 0.0037493 | 0.98818 | -0.22407 | 0.98808 | -0.22601 | 1.03
5 | 0.0037943 | 0.00094931 | -0.0037925 | -0.00095006 | 1.849e-06 | -7.4779e-07 | 0.0057152 | 0.0057159 | 0.0057159 | 0.9878 | -0.23144 | 0.98728 | -0.24168 | 1.5703
6 | -0.13409 | -0.034206 | 0.13457 | 0.034506 | 0.00047432 | 0.00029998 | 0.20212 | 0.20211 | 0.20212 | 0.98826 | -0.22259 | 0.99207 | -0.14963 | 18.5088
7 | 0.12381 | 0.031633 | -0.12325 | -0.031281 | 0.00055835 | 0.00035244 | 0.18664 | 0.18664 | 0.18664 | 0.98826 | -0.22259 | 0.98339 | -0.31631 | 17.0917
8 | 0.0010797 | 0.00026997 | -0.0010796 | -0.00027046 | 3.9199e-08 | -4.8179e-07 | 0.0016254 | 0.0016256 | 0.0016256 | 0.98826 | -0.22259 | 0.98822 | -0.22335 | 0.44659
9 | 0.0024897 | 0.00062364 | -0.0024897 | -0.00062376 | 6.3122e-08 | -1.1296e-07 | 0.0037493 | 0.0037494 | 0.0037494 | 0.98808 | -0.22601 | 0.98805 | -0.22654 | 1.0301
10 | 0.003547 | 0.00088852 | -0.0035465 | -0.00088875 | 4.1909e-07 | -2.3178e-07 | 0.0053458 | 0.005346 | 0.005346 | 0.98728 | -0.24168 | 0.98715 | -0.24416 | 1.4687
11 | -0.0035464 | -0.00088882 | 0.0035465 | 0.00088875 | 1.1427e-07 | -6.3168e-08 | 0.005346 | 0.005346 | 0.005346 | 0.98711 | -0.24484 | 0.98715 | -0.24416 | 1.4687
12 | 0.0010796 | 0.00027046 | -0.0010796 | -0.00027057 | 9.573e-09 | -1.1764e-07 | 0.0016256 | 0.0016256 | 0.0016256 | 0.98822 | -0.22335 | 0.98821 | -0.22354 | 0.4466
13 | -0.13722 | -0.035172 | 0.13744 | 0.035314 | 0.00022488 | 0.00014228 | 0.2061 | 0.20609 | 0.2061 | 0.99207 | -0.14963 | 0.99385 | -0.11588 | 18.8732
14 | 0.10517 | 0.026748 | -0.10422 | -0.026143 | 0.00094712 | 0.0006049 | 0.15927 | 0.15927 | 0.15927 | 0.98339 | -0.31631 | 0.97372 | -0.50507 | 43.756
15 | -0.10662 | -0.027482 | 0.10663 | 0.02749 | 1.3109e-05 | 8.2293e-06 | 0.15959 | 0.15959 | 0.15959 | 0.99584 | -0.078264 | 0.99597 | -0.075739 | 14.6141
16 | 0.10662 | 0.027482 | -0.10621 | -0.027227 | 0.00040637 | 0.00025512 | 0.15959 | 0.15959 | 0.15959 | 0.99584 | -0.078264 | 0.99169 | -0.15686 | 14.6143
17 | -0.24501 | -0.063141 | 0.24551 | 0.063458 | 0.00049741 | 0.00031719 | 0.36667 | 0.36667 | 0.36667 | 0.99597 | -0.075739 | 0.99818 | -0.034132 | 33.5781
18 | 0.13838 | 0.035651 | -0.13811 | -0.03548 | 0.0002698 | 0.00017071 | 0.20709 | 0.20709 | 0.20709 | 0.99597 | -0.075739 | 0.99385 | -0.11588 | 18.964
19 | 0.10621 | 0.027227 | -0.10566 | -0.02688 | 0.00055317 | 0.00034734 | 0.15959 | 0.15959 | 0.15959 | 0.99169 | -0.15686 | 0.98605 | -0.26489 | 14.6145
20 | 0.0022925 | 0.00057435 | -0.0022925 | -0.00057448 | 5.8466e-08 | -1.301e-07 | 0.0034525 | 0.0034525 | 0.0034525 | 0.98805 | -0.22654 | 0.98802 | -0.22708 | 0.9485
21 | 0.0022925 | 0.00057448 | -0.0022924 | -0.00057454 | 2.8403e-08 | -6.3196e-08 | 0.0034525 | 0.0034526 | 0.0034526 | 0.98802 | -0.22708 | 0.98801 | -0.22734 | 0.94851
22 | 0.060907 | 0.015288 | -0.060847 | -0.01525 | 5.9881e-05 | 3.8095e-05 | 0.093085 | 0.093085 | 0.093085 | 0.97372 | -0.50507 | 0.97268 | -0.52571 | 25.5728
23 | -0.24551 | -0.063458 | 0.24592 | 0.06372 | 0.0004097 | 0.00026125 | 0.36667 | 0.36667 | 0.36667 | 0.99818 | -0.034132 | 1 | 0 | 33.578
24 | 0.093956 | 0.023709 | -0.093752 | -0.023581 | 0.00020433 | 0.00012775 | 0.14278 | 0.14278 | 0.14278 | 0.97961 | -0.38991 | 0.97728 | -0.43543 | 13.0749
25 | 0.010046 | 0.0025191 | -0.010041 | -0.0025164 | 5.4536e-06 | 2.7046e-06 | 0.01526 | 0.015261 | 0.015261 | 0.97961 | -0.38991 | 0.97903 | -0.40131 | 4.1925
26 | -0.104 | -0.026228 | 0.10463 | 0.026621 | 0.00062643 | 0.00039329 | 0.15804 | 0.15803 | 0.15804 | 0.97961 | -0.38991 | 0.98605 | -0.26489 | 14.4723
27 | 0.093752 | 0.023581 | -0.093712 | -0.023556 | 3.9975e-05 | 2.4995e-05 | 0.14278 | 0.14278 | 0.14278 | 0.97728 | -0.43543 | 0.97683 | -0.44436 | 13.0749
28 | 0.039114 | 0.0098726 | -0.039114 | -0.0098726 | 3.4854e-08 | 2.1988e-08 | 0.059608 | 0.059608 | 0.059608 | 0.97683 | -0.44436 | 0.97682 | -0.44438 | 16.3759
29 | 0.039114 | 0.0098726 | -0.039047 | -0.0098304 | 6.694e-05 | 4.2214e-05 | 0.059608 | 0.059608 | 0.059608 | 0.97682 | -0.44438 | 0.975 | -0.48018 | 16.3759
30 | 0.039047 | 0.0098304 | -0.03901 | -0.0098073 | 3.6692e-05 | 2.314e-05 | 0.059608 | 0.059609 | 0.059609 | 0.975 | -0.48018 | 0.974 | -0.49985 | 16.376
31 | -0.023875 | -0.0060073 | 0.023894 | 0.0060188 | 1.8703e-05 | 1.1505e-05 | 0.036515 | 0.036515 | 0.036515 | 0.97317 | -0.51623 | 0.974 | -0.49985 | 10.0316
32 | 0.023875 | 0.0060073 | -0.023823 | -0.0059752 | 5.2169e-05 | 3.2095e-05 | 0.036515 | 0.036516 | 0.036516 | 0.97317 | -0.51623 | 0.97085 | -0.56207 | 10.0317
33 | 0.023823 | 0.0059752 | -0.023817 | -0.0059715 | 5.9672e-06 | 3.6715e-06 | 0.036516 | 0.036516 | 0.036516 | 0.97085 | -0.56207 | 0.97058 | -0.56732 | 10.0318
34 | 0.017359 | 0.0043529 | -0.017355 | -0.0043507 | 3.7061e-06 | 2.1995e-06 | 0.026614 | 0.026614 | 0.026614 | 0.97058 | -0.56732 | 0.97035 | -0.5718 | 7.3115
35 | 0.017355 | 0.0043507 | -0.017352 | -0.0043488 | 3.1373e-06 | 1.862e-06 | 0.026614 | 0.026614 | 0.026614 | 0.97035 | -0.5718 | 0.97016 | -0.5756 | 7.3116

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.26865 | 0.069003

## res_load
| p_mw | q_mvar
0 | 0.00043071 | 0.00010795
1 | 0.00084916 | 0.00021282
2 | 0.0016325 | 0.00040914
3 | 0.00024553 | 6.1534e-05
4 | 0.0035464 | 0.00088882
5 | 0.0010796 | 0.00027057
6 | 0.002654 | 0.00066515
7 | 0.018088 | 0.0045333
8 | 0.00019715 | 4.941e-05
9 | 0.0022924 | 0.00057454
10 | 0.00066318 | 0.00016621
11 | 0.043311 | 0.010855
12 | 0.010041 | 0.0025164
13 | 0.0010309 | 0.00025837
14 | 0.054598 | 0.013684
15 | 0.021079 | 0.0052829
16 | 0.015116 | 0.0037885
17 | 0.0064585 | 0.0016186
18 | 0.017352 | 0.0043488
19 | 0.060847 | 0.01525

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1