## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1095-6_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1095-6_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1095-6_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1095-6_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1095-6_0_4_node_12 | 0.4 | n |  | TRUE
5 | bus_LV_1095-6_0_4_node_18 | 0.4 | n |  | TRUE
6 | bus_LV_1095-6_0_4_node_13 | 0.4 | n |  | TRUE
7 | bus_LV_1095-6_0_4_node_19 | 0.4 | n |  | TRUE
8 | bus_LV_1095-6_0_4_node_20 | 0.4 | n |  | TRUE
9 | bus_LV_1095-6_0_4_node_4 | 0.4 | n |  | TRUE
10 | bus_LV_1095-6_0_4_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_1095-6_0_4_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_1095-6_0_4_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_1095-6_0_4_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_1095-6_0_4_node_23 | 0.4 | n |  | TRUE
15 | bus_LV_1095-6_0_4_node_29 | 0.4 | n |  | TRUE
16 | bus_LV_1095-6_0_4_node_25 | 0.4 | n |  | TRUE
17 | bus_LV_1095-6_0_4_node_21 | 0.4 | n |  | TRUE
18 | bus_LV_1095-6_0_4_node_30 | 0.4 | n |  | TRUE
19 | bus_LV_1095-6_0_4_node_9 | 0.4 | n |  | TRUE
20 | bus_LV_1095-6_0_4_node_10 | 0.4 | n |  | TRUE
21 | bus_LV_1095-6_0_4_node_11 | 0.4 | n |  | TRUE
22 | bus_LV_1095-6_0_4_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_1095-6_0_4_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_1095-6_0_4_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_1095-6_0_4_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_1095-6_0_4_node_26 | 0.4 | n |  | TRUE
27 | bus_LV_1095-6_0_4_node_27 | 0.4 | n |  | TRUE
28 | bus_LV_1095-6_0_4_node_28 | 0.4 | n |  | TRUE
29 | bus_LV_1095-6_0_4_node_24 | 0.4 | n |  | TRUE
30 | bus_LV_1095-6_0_4_node_55 | 0.4 | n |  | TRUE
31 | bus_LV_1095-6_0_4_node_56 | 0.4 | n |  | TRUE
32 | bus_LV_1095-6_0_4_node_32 | 0.4 | n |  | TRUE
33 | bus_LV_1095-6_0_4_node_31 | 0.4 | n |  | TRUE
34 | bus_LV_1095-6_0_4_node_35 | 0.4 | n |  | TRUE
35 | bus_LV_1095-6_0_4_node_36 | 0.4 | n |  | TRUE
36 | bus_LV_1095-6_0_4_node_22 | 0.4 | n |  | TRUE
37 | bus_LV_1095-6_0_4_node_67 | 0.4 | n |  | TRUE
38 | bus_LV_1095-6_0_4_node_66 | 0.4 | n |  | TRUE
39 | bus_LV_1095-6_0_4_node_72 | 0.4 | n |  | TRUE
40 | bus_LV_1095-6_0_4_node_54 | 0.4 | n |  | TRUE
41 | bus_LV_1095-6_0_4_node_53 | 0.4 | n |  | TRUE
42 | bus_LV_1095-6_0_4_node_37 | 0.4 | n |  | TRUE
43 | bus_LV_1095-6_0_4_node_39 | 0.4 | n |  | TRUE
44 | bus_LV_1095-6_0_4_node_40 | 0.4 | n |  | TRUE
45 | bus_LV_1095-6_0_4_node_41 | 0.4 | n |  | TRUE
46 | bus_LV_1095-6_0_4_node_57 | 0.4 | n |  | TRUE
47 | bus_LV_1095-6_0_4_node_58 | 0.4 | n |  | TRUE
48 | bus_LV_1095-6_0_4_node_59 | 0.4 | n |  | TRUE
49 | bus_LV_1095-6_0_4_node_61 | 0.4 | n |  | TRUE
50 | bus_LV_1095-6_0_4_node_42 | 0.4 | n |  | TRUE
51 | bus_LV_1095-6_0_4_node_43 | 0.4 | n |  | TRUE
52 | bus_LV_1095-6_0_4_node_44 | 0.4 | n |  | TRUE
53 | bus_LV_1095-6_0_4_node_45 | 0.4 | n |  | TRUE
54 | bus_LV_1095-6_0_4_node_46 | 0.4 | n |  | TRUE
55 | bus_LV_1095-6_0_4_node_91 | 0.4 | n |  | TRUE
56 | bus_LV_1095-6_0_4_node_92 | 0.4 | n |  | TRUE
57 | bus_LV_1095-6_0_4_node_88 | 0.4 | n |  | TRUE
58 | bus_LV_1095-6_0_4_node_89 | 0.4 | n |  | TRUE
59 | bus_LV_1095-6_0_4_node_47 | 0.4 | n |  | TRUE
60 | bus_LV_1095-6_0_4_node_48 | 0.4 | n |  | TRUE
61 | bus_LV_1095-6_0_4_node_49 | 0.4 | n |  | TRUE
62 | bus_LV_1095-6_0_4_node_50 | 0.4 | n |  | TRUE
63 | bus_LV_1095-6_0_4_node_51 | 0.4 | n |  | TRUE
64 | bus_LV_1095-6_0_4_node_81 | 0.4 | n |  | TRUE
65 | bus_LV_1095-6_0_4_node_79 | 0.4 | n |  | TRUE
66 | bus_LV_1095-6_0_4_node_65 | 0.4 | n |  | TRUE
67 | bus_LV_1095-6_0_4_node_63 | 0.4 | n |  | TRUE
68 | bus_LV_1095-6_0_4_node_124 | 0.4 | n |  | TRUE
69 | bus_LV_1095-6_0_4_node_80 | 0.4 | n |  | TRUE
70 | bus_LV_1095-6_0_4_node_69 | 0.4 | n |  | TRUE
71 | bus_LV_1095-6_0_4_node_70 | 0.4 | n |  | TRUE
72 | bus_LV_1095-6_0_4_node_68 | 0.4 | n |  | TRUE
73 | bus_LV_1095-6_0_4_node_64 | 0.4 | n |  | TRUE
74 | bus_LV_1095-6_0_4_node_52 | 0.4 | n |  | TRUE
75 | bus_LV_1095-6_0_4_node_74 | 0.4 | n |  | TRUE
76 | bus_LV_1095-6_0_4_node_73 | 0.4 | n |  | TRUE
77 | bus_LV_1095-6_0_4_node_60 | 0.4 | n |  | TRUE
78 | bus_LV_1095-6_0_4_node_62 | 0.4 | n |  | TRUE
79 | bus_LV_1095-6_0_4_node_71 | 0.4 | n |  | TRUE
80 | bus_LV_1095-6_0_4_node_77 | 0.4 | n |  | TRUE
81 | bus_LV_1095-6_0_4_node_78 | 0.4 | n |  | TRUE
82 | bus_LV_1095-6_0_4_node_75 | 0.4 | n |  | TRUE
83 | bus_LV_1095-6_0_4_node_76 | 0.4 | n |  | TRUE
84 | bus_LV_1095-6_0_4_node_83 | 0.4 | n |  | TRUE
85 | bus_LV_1095-6_0_4_node_82 | 0.4 | n |  | TRUE
86 | bus_LV_1095-6_0_4_node_87 | 0.4 | n |  | TRUE
87 | bus_LV_1095-6_0_4_node_84 | 0.4 | n |  | TRUE
88 | bus_LV_1095-6_0_4_node_85 | 0.4 | n |  | TRUE
89 | bus_LV_1095-6_0_4_node_93 | 0.4 | n |  | TRUE
90 | bus_LV_1095-6_0_4_node_137 | 0.4 | n |  | TRUE
91 | bus_LV_1095-6_0_4_node_90 | 0.4 | n |  | TRUE
92 | bus_LV_1095-6_0_4_node_94 | 0.4 | n |  | TRUE
93 | bus_LV_1095-6_0_4_node_95 | 0.4 | n |  | TRUE
94 | bus_LV_1095-6_0_4_node_138 | 0.4 | n |  | TRUE
95 | bus_LV_1095-6_0_4_node_125 | 0.4 | n |  | TRUE
96 | bus_LV_1095-6_0_4_node_96 | 0.4 | n |  | TRUE
97 | bus_LV_1095-6_0_4_node_97 | 0.4 | n |  | TRUE
98 | bus_LV_1095-6_0_4_node_123 | 0.4 | n |  | TRUE
99 | bus_LV_1095-6_0_4_node_98 | 0.4 | n |  | TRUE
100 | bus_LV_1095-6_0_4_node_128 | 0.4 | n |  | TRUE
101 | bus_LV_1095-6_0_4_node_99 | 0.4 | n |  | TRUE
102 | bus_LV_1095-6_0_4_node_100 | 0.4 | n |  | TRUE
103 | bus_LV_1095-6_0_4_node_104 | 0.4 | n |  | TRUE
104 | bus_LV_1095-6_0_4_node_103 | 0.4 | n |  | TRUE
105 | bus_LV_1095-6_0_4_node_105 | 0.4 | n |  | TRUE
106 | bus_LV_1095-6_0_4_node_101 | 0.4 | n |  | TRUE
107 | bus_LV_1095-6_0_4_node_102 | 0.4 | n |  | TRUE
108 | bus_LV_1095-6_0_4_node_121 | 0.4 | n |  | TRUE
109 | bus_LV_1095-6_0_4_node_122 | 0.4 | n |  | TRUE
110 | bus_LV_1095-6_0_4_node_119 | 0.4 | n |  | TRUE
111 | bus_LV_1095-6_0_4_node_106 | 0.4 | n |  | TRUE
112 | bus_LV_1095-6_0_4_node_107 | 0.4 | n |  | TRUE
113 | bus_LV_1095-6_0_4_node_108 | 0.4 | n |  | TRUE
114 | bus_LV_1095-6_0_4_node_109 | 0.4 | n |  | TRUE
115 | bus_LV_1095-6_0_4_node_111 | 0.4 | n |  | TRUE
116 | bus_LV_1095-6_0_4_node_136 | 0.4 | n |  | TRUE
117 | bus_LV_1095-6_0_4_node_140 | 0.4 | n |  | TRUE
118 | bus_LV_1095-6_0_4_node_110 | 0.4 | n |  | TRUE
119 | bus_LV_1095-6_0_4_node_112 | 0.4 | n |  | TRUE
120 | bus_LV_1095-6_0_4_node_141 | 0.4 | n |  | TRUE
121 | bus_LV_1095-6_0_4_node_134 | 0.4 | n |  | TRUE
122 | bus_LV_1095-6_0_4_node_139 | 0.4 | n |  | TRUE
123 | bus_LV_1095-6_0_4_node_113 | 0.4 | n |  | TRUE
124 | bus_LV_1095-6_0_4_node_114 | 0.4 | n |  | TRUE
125 | bus_LV_1095-6_0_4_node_115 | 0.4 | n |  | TRUE
126 | bus_LV_1095-6_0_4_node_116 | 0.4 | n |  | TRUE
127 | bus_LV_1095-6_0_4_node_117 | 0.4 | n |  | TRUE
128 | bus_LV_1095-6_0_4_node_118 | 0.4 | n |  | TRUE
129 | bus_LV_1095-6_0_4_node_120 | 0.4 | n |  | TRUE
130 | bus_LV_1095-6_0_4_node_129 | 0.4 | n |  | TRUE
131 | bus_LV_1095-6_0_4_node_135 | 0.4 | n |  | TRUE
132 | bus_LV_1095-6_0_4_node_127 | 0.4 | n |  | TRUE
133 | bus_LV_1095-6_0_4_node_126 | 0.4 | n |  | TRUE
134 | bus_LV_1095-6_0_4_node_131 | 0.4 | n |  | TRUE
135 | bus_LV_1095-6_0_4_node_132 | 0.4 | n |  | TRUE
136 | bus_LV_1095-6_0_4_node_133 | 0.4 | n |  | TRUE
137 | bus_MV_471_0_node_18 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1095-6_0_4_load_0 | 0 | 0.0044677 | 0.0011197 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1095-6_0_4_load_2 | 2 | 0.0036628 | 0.00091798 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1095-6_0_4_load_3 | 3 | 0.0039529 | 0.00099069 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1095-6_0_4_load_12 | 4 | 0.0011961 | 0.00029977 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1095-6_0_4_load_13 | 6 | 0.0032644 | 0.00081813 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1095-6_0_4_load_20 | 8 | 0.0032036 | 0.0008029 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1095-6_0_4_load_4 | 9 | 0.001959 | 0.00049097 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1095-6_0_4_load_5 | 10 | 0.0056587 | 0.0014182 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1095-6_0_4_load_6 | 11 | 0.0039584 | 0.00099206 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1095-6_0_4_load_7 | 12 | 0.0037742 | 0.00094591 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1095-6_0_4_load_8 | 13 | 0.0031731 | 0.00079526 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1095-6_0_4_load_25 | 16 | 0.0059381 | 0.0014882 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1095-6_0_4_load_21 | 17 | 0.0043436 | 0.0010886 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1095-6_0_4_load_9 | 19 | 0.002975 | 0.0007456 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1095-6_0_4_load_10 | 20 | 0.0033944 | 0.00085072 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1095-6_0_4_load_11 | 21 | 0.0027689 | 0.00069396 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1095-6_0_4_load_14 | 22 | 0.0021555 | 0.00054021 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1095-6_0_4_load_17 | 25 | 0.0032618 | 0.0008175 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1095-6_0_4_load_26 | 26 | 0.0027204 | 0.00068179 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1095-6_0_4_load_27 | 27 | 0.0014679 | 0.00036789 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1095-6_0_4_load_24 | 29 | 0.0018022 | 0.00045168 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1095-6_0_4_load_56 | 31 | 0.0013394 | 0.0003357 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1095-6_0_4_load_32 | 32 | 0.0029977 | 0.00075129 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1095-6_0_4_load_31 | 33 | 0.00221 | 0.00055387 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1095-6_0_4_load_35 | 34 | 0.0039756 | 0.00099637 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1095-6_0_4_load_36 | 35 | 0.002569 | 0.00064384 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1095-6_0_4_load_22 | 36 | 0.002441 | 0.00061176 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1095-6_0_4_load_67 | 37 | 0.0015677 | 0.00039291 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1095-6_0_4_load_66 | 38 | 0.012664 | 0.0031738 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1095-6_0_4_load_72 | 39 | 0.0073365 | 0.0018387 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1095-6_0_4_load_54 | 40 | 0.0029243 | 0.00073291 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1095-6_0_4_load_53 | 41 | 0.0023032 | 0.00057724 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1095-6_0_4_load_37 | 42 | 0.003219 | 0.00080676 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1095-6_0_4_load_39 | 43 | 0.011966 | 0.002999 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1095-6_0_4_load_40 | 44 | 0.0071281 | 0.0017865 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1095-6_0_4_load_57 | 46 | 0.0095471 | 0.0023927 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1095-6_0_4_load_58 | 47 | 0.0088017 | 0.0022059 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1095-6_0_4_load_59 | 48 | 0.012801 | 0.0032081 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1095-6_0_4_load_61 | 49 | 0.008953 | 0.0022438 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1095-6_0_4_load_42 | 50 | 0.0033124 | 0.00083017 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1095-6_0_4_load_43 | 51 | 0.0033622 | 0.00084265 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1095-6_0_4_load_44 | 52 | 0.003475 | 0.00087093 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1095-6_0_4_load_45 | 53 | 0.0037291 | 0.00093461 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1095-6_0_4_load_46 | 54 | 0.0030101 | 0.00075441 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1095-6_0_4_load_91 | 55 | 0.0038114 | 0.00095523 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1095-6_0_4_load_92 | 56 | 0.003968 | 0.00099448 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1095-6_0_4_load_47 | 59 | 0.00052935 | 0.00013267 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1095-6_0_4_load_48 | 60 | 0.0051049 | 0.0012794 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1095-6_0_4_load_49 | 61 | 0.00045468 | 0.00011395 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1095-6_0_4_load_79 | 65 | 0.00046339 | 0.00011614 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1095-6_0_4_load_63 | 67 | 0.00050344 | 0.00012617 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1095-6_0_4_load_124 | 68 | 0.0050838 | 0.0012741 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1095-6_0_4_load_80 | 69 | 0.00045212 | 0.00011331 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1095-6_0_4_load_69 | 70 | 0.0065445 | 0.0016402 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1095-6_0_4_load_70 | 71 | 0.009805 | 0.0024574 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1095-6_0_4_load_68 | 72 | 0.016555 | 0.004149 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1095-6_0_4_load_64 | 73 | 0.004696 | 0.0011769 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1095-6_0_4_load_52 | 74 | 0.0026683 | 0.00066874 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1095-6_0_4_load_74 | 75 | 0.0054734 | 0.0013718 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1095-6_0_4_load_73 | 76 | 0.00052465 | 0.00013149 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1095-6_0_4_load_60 | 77 | 0.0063226 | 0.0015846 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1095-6_0_4_load_62 | 78 | 0.0096698 | 0.0024235 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1095-6_0_4_load_77 | 80 | 0.018184 | 0.0045575 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1095-6_0_4_load_75 | 82 | 0.0041647 | 0.0010438 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1095-6_0_4_load_76 | 83 | 0.006917 | 0.0017336 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1095-6_0_4_load_83 | 84 | 0.010504 | 0.0026327 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1095-6_0_4_load_82 | 85 | 0.0053948 | 0.0013521 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1095-6_0_4_load_87 | 86 | 0.015618 | 0.0039143 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1095-6_0_4_load_84 | 87 | 0.0022687 | 0.0005686 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1095-6_0_4_load_85 | 88 | 0.001634 | 0.00040951 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1095-6_0_4_load_137 | 90 | 0.00063305 | 0.00015866 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1095-6_0_4_load_90 | 91 | 0.0017302 | 0.00043363 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1095-6_0_4_load_94 | 92 | 0.0012132 | 0.00030405 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1095-6_0_4_load_95 | 93 | 0.0011936 | 0.00029913 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1095-6_0_4_load_138 | 94 | 0.00057831 | 0.00014494 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1095-6_0_4_load_125 | 95 | 0.0013877 | 0.0003478 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1095-6_0_4_load_96 | 96 | 0.0001883 | 4.7191e-05 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1095-6_0_4_load_98 | 99 | 0.00022693 | 5.6874e-05 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1095-6_0_4_load_99 | 101 | 0.0010125 | 0.00025375 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1095-6_0_4_load_104 | 103 | 0.00015377 | 3.8538e-05 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1095-6_0_4_load_105 | 105 | 0.00026377 | 6.6108e-05 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1095-6_0_4_load_101 | 106 | 0.0014686 | 0.00036807 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1095-6_0_4_load_102 | 107 | 0.00028603 | 7.1685e-05 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1095-6_0_4_load_121 | 108 | 0.0026086 | 0.00065379 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1095-6_0_4_load_122 | 109 | 0.002275 | 0.00057017 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1095-6_0_4_load_106 | 111 | 0.015174 | 0.0038029 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1095-6_0_4_load_107 | 112 | 0.012415 | 0.0031115 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1095-6_0_4_load_136 | 116 | 0.00067775 | 0.00016986 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1095-6_0_4_load_140 | 117 | 0.0016316 | 0.00040891 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1095-6_0_4_load_110 | 118 | 0.001145 | 0.00028695 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1095-6_0_4_load_141 | 120 | 0.0019528 | 0.00048941 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1095-6_0_4_load_139 | 122 | 0.00063668 | 0.00015957 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1095-6_0_4_load_113 | 123 | 0.0016542 | 0.00041459 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1095-6_0_4_load_114 | 124 | 0.0028189 | 0.00070649 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1095-6_0_4_load_117 | 127 | 0.0022586 | 0.00056606 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1095-6_0_4_load_120 | 129 | 0.0027936 | 0.00070013 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1095-6_0_4_load_129 | 130 | 0.0021079 | 0.0005283 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1095-6_0_4_load_135 | 131 | 0.0023371 | 0.00058574 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1095-6_0_4_load_127 | 132 | 0.00068435 | 0.00017151 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1095-6_0_4_load_126 | 133 | 0.001034 | 0.00025915 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1095-6_0_4_load_131 | 134 | 0.00065507 | 0.00016418 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_1095-6_0_4_load_132 | 135 | 0.00068223 | 0.00017098 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_1095-6_0_4_load_133 | 136 | 0.00062712 | 0.00015717 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 77 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1095-6_0_4_line_0 |  | 0 | 1 | 0.017405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1095-6_0_4_line_1 |  | 1 | 2 | 0.02754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1095-6_0_4_line_2 |  | 1 | 3 | 0.035316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1095-6_0_4_line_3 |  | 2 | 4 | 0.020409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1095-6_0_4_line_4 |  | 3 | 5 | 0.016288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1095-6_0_4_line_5 |  | 4 | 6 | 0.015798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1095-6_0_4_line_6 |  | 5 | 7 | 0.006878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1095-6_0_4_line_7 |  | 5 | 8 | 0.024982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1095-6_0_4_line_8 |  | 6 | 24 | 0.025244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1095-6_0_4_line_9 |  | 7 | 32 | 0.021118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1095-6_0_4_line_10 |  | 7 | 33 | 0.041841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1095-6_0_4_line_11 |  | 8 | 34 | 0.0083146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1095-6_0_4_line_12 |  | 9 | 10 | 0.010884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1095-6_0_4_line_13 |  | 9 | 11 | 0.0094827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1095-6_0_4_line_14 |  | 10 | 12 | 0.025594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1095-6_0_4_line_15 |  | 11 | 13 | 0.023656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1095-6_0_4_line_16 |  | 12 | 14 | 0.01406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1095-6_0_4_line_17 |  | 13 | 15 | 0.042658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1095-6_0_4_line_18 |  | 14 | 16 | 0.021613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1095-6_0_4_line_19 |  | 14 | 17 | 0.0095003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1095-6_0_4_line_20 |  | 15 | 18 | 0.046484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1095-6_0_4_line_21 |  | 16 | 33 | 0.0014503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1095-6_0_4_line_22 |  | 17 | 36 | 0.023172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1095-6_0_4_line_23 |  | 18 | 40 | 0.047313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1095-6_0_4_line_24 |  | 19 | 20 | 0.0023817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1095-6_0_4_line_25 |  | 20 | 21 | 0.017326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1095-6_0_4_line_26 |  | 21 | 22 | 0.013681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1095-6_0_4_line_27 |  | 22 | 23 | 0.017852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1095-6_0_4_line_28 |  | 23 | 26 | 0.019092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1095-6_0_4_line_29 |  | 23 | 27 | 0.018438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1095-6_0_4_line_30 |  | 23 | 28 | 0.040665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1095-6_0_4_line_31 |  | 24 | 25 | 0.039362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1095-6_0_4_line_32 |  | 26 | 29 | 0.017872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1095-6_0_4_line_33 |  | 28 | 30 | 0.062182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
34 | LV_1095-6_0_4_line_34 |  | 28 | 31 | 0.038859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
35 | LV_1095-6_0_4_line_35 |  | 29 | 36 | 0.0088778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1095-6_0_4_line_36 |  | 30 | 37 | 0.01929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
37 | LV_1095-6_0_4_line_37 |  | 30 | 38 | 0.017965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1095-6_0_4_line_38 |  | 31 | 39 | 0.03744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
39 | LV_1095-6_0_4_line_39 |  | 32 | 35 | 0.025816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1095-6_0_4_line_40 |  | 35 | 42 | 0.0061457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1095-6_0_4_line_41 |  | 37 | 75 | 0.034169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
42 | LV_1095-6_0_4_line_42 |  | 39 | 76 | 0.0081191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
43 | LV_1095-6_0_4_line_43 |  | 40 | 41 | 0.027028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1095-6_0_4_line_44 |  | 41 | 74 | 0.026164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1095-6_0_4_line_45 |  | 43 | 44 | 0.0018897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1095-6_0_4_line_46 |  | 44 | 45 | 0.036013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1095-6_0_4_line_47 |  | 45 | 46 | 0.015047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1095-6_0_4_line_48 |  | 45 | 47 | 0.026083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1095-6_0_4_line_49 |  | 46 | 48 | 0.028579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1095-6_0_4_line_50 |  | 47 | 49 | 0.001226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1095-6_0_4_line_51 |  | 48 | 77 | 0.012994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1095-6_0_4_line_52 |  | 49 | 78 | 0.016549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1095-6_0_4_line_53 |  | 50 | 51 | 0.0056861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1095-6_0_4_line_54 |  | 50 | 52 | 0.0057623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1095-6_0_4_line_55 |  | 51 | 53 | 0.0059835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1095-6_0_4_line_56 |  | 52 | 54 | 0.0071279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1095-6_0_4_line_57 |  | 53 | 55 | 0.0088929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1095-6_0_4_line_58 |  | 54 | 56 | 0.0021247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1095-6_0_4_line_59 |  | 55 | 57 | 0.0059081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1095-6_0_4_line_60 |  | 56 | 58 | 0.0077937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1095-6_0_4_line_61 |  | 57 | 91 | 0.0002126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1095-6_0_4_line_62 |  | 58 | 86 | 0.011155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1095-6_0_4_line_63 |  | 58 | 64 | 0.018878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1095-6_0_4_line_64 |  | 59 | 60 | 0.012796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1095-6_0_4_line_65 |  | 59 | 61 | 0.021097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1095-6_0_4_line_66 |  | 60 | 62 | 0.00084782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1095-6_0_4_line_67 |  | 61 | 63 | 0.0019743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1095-6_0_4_line_68 |  | 62 | 64 | 0.059253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1095-6_0_4_line_69 |  | 62 | 65 | 0.025952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1095-6_0_4_line_70 |  | 63 | 66 | 0.025482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1095-6_0_4_line_71 |  | 63 | 67 | 0.016358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1095-6_0_4_line_72 |  | 64 | 68 | 0.017122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1095-6_0_4_line_73 |  | 65 | 69 | 0.013929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1095-6_0_4_line_74 |  | 66 | 70 | 0.016249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1095-6_0_4_line_75 |  | 66 | 71 | 0.017649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1095-6_0_4_line_76 |  | 66 | 72 | 0.036156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1095-6_0_4_line_77 |  | 67 | 73 | 0.023008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1095-6_0_4_line_78 |  | 70 | 82 | 0.022817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1095-6_0_4_line_79 |  | 71 | 75 | 0.0027748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1095-6_0_4_line_80 |  | 76 | 81 | 0.021904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
81 | LV_1095-6_0_4_line_81 |  | 77 | 79 | 0.02994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
82 | LV_1095-6_0_4_line_82 |  | 79 | 80 | 0.0075463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1095-6_0_4_line_83 |  | 79 | 81 | 0.01577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
84 | LV_1095-6_0_4_line_84 |  | 80 | 84 | 0.020726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1095-6_0_4_line_85 |  | 82 | 83 | 0.034618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1095-6_0_4_line_86 |  | 84 | 85 | 0.022138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1095-6_0_4_line_87 |  | 85 | 87 | 0.023206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1095-6_0_4_line_88 |  | 87 | 88 | 0.030913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1095-6_0_4_line_89 |  | 88 | 89 | 0.031931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1095-6_0_4_line_90 |  | 89 | 90 | 0.016004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1095-6_0_4_line_91 |  | 90 | 94 | 0.020386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1095-6_0_4_line_92 |  | 91 | 92 | 0.0058476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1095-6_0_4_line_93 |  | 92 | 93 | 0.0056359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1095-6_0_4_line_94 |  | 93 | 95 | 0.004944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1095-6_0_4_line_95 |  | 94 | 122 | 0.021033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1095-6_0_4_line_96 |  | 96 | 97 | 0.033761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1095-6_0_4_line_97 |  | 96 | 98 | 0.063524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1095-6_0_4_line_98 |  | 97 | 99 | 0.012554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1095-6_0_4_line_99 |  | 98 | 100 | 0.031043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1095-6_0_4_line_100 |  | 99 | 101 | 0.0015048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1095-6_0_4_line_101 |  | 100 | 133 | 0.016457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1095-6_0_4_line_102 |  | 101 | 102 | 0.018265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1095-6_0_4_line_103 |  | 102 | 103 | 0.029467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1095-6_0_4_line_104 |  | 102 | 104 | 0.045982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1095-6_0_4_line_105 |  | 103 | 105 | 0.0062181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1095-6_0_4_line_106 |  | 104 | 106 | 0.057428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1095-6_0_4_line_107 |  | 106 | 107 | 0.025276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1095-6_0_4_line_108 |  | 108 | 109 | 0.023646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1095-6_0_4_line_109 |  | 108 | 110 | 0.022637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1095-6_0_4_line_110 |  | 110 | 126 | 0.005481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1095-6_0_4_line_111 |  | 111 | 112 | 0.01645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1095-6_0_4_line_112 |  | 111 | 113 | 0.017126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1095-6_0_4_line_113 |  | 112 | 114 | 0.018399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1095-6_0_4_line_114 |  | 113 | 115 | 0.041638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1095-6_0_4_line_115 |  | 114 | 116 | 0.011769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1095-6_0_4_line_116 |  | 114 | 117 | 0.02287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1095-6_0_4_line_117 |  | 115 | 120 | 0.00847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1095-6_0_4_line_118 |  | 115 | 119 | 0.014867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1095-6_0_4_line_119 |  | 116 | 121 | 0.022303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1095-6_0_4_line_120 |  | 117 | 122 | 0.005839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_1095-6_0_4_line_121 |  | 118 | 119 | 0.021822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_1095-6_0_4_line_122 |  | 119 | 123 | 0.003827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_1095-6_0_4_line_123 |  | 121 | 131 | 0.01089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_1095-6_0_4_line_124 |  | 121 | 136 | 0.031311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_1095-6_0_4_line_125 |  | 124 | 125 | 0.0023048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_1095-6_0_4_line_126 |  | 124 | 126 | 0.02282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_1095-6_0_4_line_127 |  | 125 | 127 | 0.012977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_1095-6_0_4_line_128 |  | 125 | 128 | 0.013015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_1095-6_0_4_line_129 |  | 126 | 129 | 0.010261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_1095-6_0_4_line_130 |  | 127 | 130 | 0.024578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_1095-6_0_4_line_131 |  | 128 | 131 | 0.010083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_1095-6_0_4_line_132 |  | 130 | 132 | 0.024187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_1095-6_0_4_line_133 |  | 132 | 133 | 0.023977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_1095-6_0_4_line_134 |  | 134 | 135 | 0.023055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_1095-6_0_4_line_135 |  | 135 | 136 | 0.021927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1095-6_0_4_trafo_60 | 0.63 MVA 20/0.4 kV | 137 | 77 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2651394.2142 | 1224014.574 | 2651396.7861 | 1224012.6616 | 2651398.8388 | 1224009.3996 | 2651400.2067 | 1224005.5312 | 2651401.1757 | 1224000.4475 | 2651401.394 | 1223999.4026
1 | 2651394.2142 | 1224014.574 | 2651389.1966 | 1224041.6527
2 | 2651394.2142 | 1224014.574 | 2651391.2716 | 1224014.6486 | 2651359.6363 | 1224007.7779
3 | 2651394.3628 | 1224055.9791 | 2651386.8816 | 1224054.1463 | 2651389.1966 | 1224041.6527
4 | 2651343.7196 | 1224004.3211 | 2651359.6363 | 1224007.7779
5 | 2651394.3628 | 1224055.9791 | 2651407.4851 | 1224059.1939 | 2651409.7396 | 1224059.5816
6 | 2651336.976 | 1224002.8732 | 2651343.7196 | 1224004.3211
7 | 2651343.7196 | 1224004.3211 | 2651339.4997 | 1224028.9437
8 | 2651434.3906 | 1224064.9964 | 2651413.6783 | 1224060.2591 | 2651409.7396 | 1224059.5816
9 | 2651336.976 | 1224002.8732 | 2651341.4861 | 1223982.2421
10 | 2651336.976 | 1224002.8732 | 2651295.9629 | 1223994.5927
11 | 2651342.6135 | 1224034.0966 | 2651338.7613 | 1224033.2518 | 2651339.4997 | 1224028.9437
12 | 2651282.4267 | 1223940.3122 | 2651280.4731 | 1223951.0194
13 | 2651282.4267 | 1223940.3122 | 2651284.1289 | 1223930.9835
14 | 2651280.4731 | 1223951.0194 | 2651275.8791 | 1223976.1972
15 | 2651288.3751 | 1223907.712 | 2651284.1289 | 1223930.9835
16 | 2651273.3554 | 1223990.0284 | 2651275.8791 | 1223976.1972
17 | 2651297.0475 | 1223866.3448 | 2651294.288 | 1223881.2302 | 2651293.0285 | 1223882.2089 | 2651288.3751 | 1223907.712
18 | 2651273.3554 | 1223990.0284 | 2651294.5412 | 1223994.3057
19 | 2651273.3554 | 1223990.0284 | 2651271.1967 | 1223999.2801
20 | 2651297.0475 | 1223866.3448 | 2651276.5591 | 1223862.8107 | 2651250.9751 | 1223859.2772
21 | 2651295.9629 | 1223994.5927 | 2651294.5412 | 1223994.3057
22 | 2651265.9315 | 1224021.8457 | 2651271.1967 | 1223999.2801
23 | 2651250.9751 | 1223859.2772 | 2651242.303 | 1223905.7884
24 | 2651282.0329 | 1224091.9253 | 2651282.5641 | 1224089.6036
25 | 2651282.5641 | 1224089.6036 | 2651286.4281 | 1224072.7142 | 2651286.4281 | 1224072.7142
26 | 2651273.016 | 1224070.0132 | 2651286.4281 | 1224072.7142
27 | 2651255.515 | 1224066.4887 | 2651273.016 | 1224070.0132
28 | 2651255.515 | 1224066.4887 | 2651259.8532 | 1224047.896
29 | 2651255.515 | 1224066.4887 | 2651251.9332 | 1224084.5751
30 | 2651255.515 | 1224066.4887 | 2651215.3109 | 1224059.6498
31 | 2651434.3906 | 1224064.9964 | 2651431.5892 | 1224025.7344
32 | 2651263.9142 | 1224030.4913 | 2651259.8532 | 1224047.896
33 | 2651203.4501 | 1224120.6856 | 2651210.3142 | 1224085.1893 | 2651213.8615 | 1224066.8307 | 2651215.3109 | 1224059.6498
34 | 2651215.3109 | 1224059.6498 | 2651205.1645 | 1224058.006 | 2651198.8798 | 1224056.9958 | 2651188.2083 | 1224052.9238 | 2651178.8985 | 1224047.4626
35 | 2651263.9142 | 1224030.4913 | 2651265.9315 | 1224021.8457
36 | 2651203.4501 | 1224120.6856 | 2651185.9804 | 1224116.266 | 2651184.7321 | 1224116.0303
37 | 2651203.4501 | 1224120.6856 | 2651201.0643 | 1224138.4919
38 | 2651178.8985 | 1224047.4626 | 2651178.8985 | 1224047.4626 | 2651170.2679 | 1224038.8387 | 2651157.3639 | 1224017.1473
39 | 2651341.4861 | 1223982.2421 | 2651346.6699 | 1223958.5293 | 2651346.9813 | 1223957.018
40 | 2651348.2217 | 1223950.9988 | 2651346.9813 | 1223957.018
41 | 2651184.7321 | 1224116.0303 | 2651161.2488 | 1224111.5951 | 2651151.0647 | 1224112.9224
42 | 2651157.3639 | 1224017.1473 | 2651153.2129 | 1224010.1695
43 | 2651242.303 | 1223905.7884 | 2651237.3491 | 1223932.3582
44 | 2651232.6636 | 1223958.099 | 2651233.9151 | 1223950.7759 | 2651237.3491 | 1223932.3582
45 | 2651200.6578 | 1223906.8943 | 2651198.7923 | 1223906.5929
46 | 2651163.1786 | 1223902.0489 | 2651168.6864 | 1223901.7293 | 2651198.7923 | 1223906.5929
47 | 2651163.1786 | 1223902.0489 | 2651163.8892 | 1223913.7733 | 2651163.5113 | 1223917.0528
48 | 2651163.1786 | 1223902.0489 | 2651162.0068 | 1223897.2358 | 2651155.8771 | 1223880.8064 | 2651155.1511 | 1223877.287
49 | 2651163.5113 | 1223917.0528 | 2651162.1358 | 1223928.9899 | 2651157.8354 | 1223944.9851 | 2651157.8354 | 1223944.9851
50 | 2651154.9035 | 1223876.0862 | 2651155.1511 | 1223877.287
51 | 2651157.8354 | 1223944.9851 | 2651156.8337 | 1223947.7337 | 2651153.4008 | 1223957.199 | 2651153.4008 | 1223957.199
52 | 2651151.5604 | 1223859.8786 | 2651154.9035 | 1223876.0862
53 | 2651059.2333 | 1224025.3442 | 2651058.8794 | 1224019.6691
54 | 2651059.2333 | 1224025.3442 | 2651059.592 | 1224031.0953
55 | 2651058.8794 | 1224019.6691 | 2651058.5069 | 1224013.6972
56 | 2651066.6638 | 1224030.203 | 2651059.592 | 1224031.0953 | 2651059.592 | 1224031.0953
57 | 2651058.5069 | 1224013.6972 | 2651057.9533 | 1224004.8216
58 | 2651066.6638 | 1224030.203 | 2651068.7718 | 1224029.9369
59 | 2651057.5856 | 1223998.9249 | 2651057.9533 | 1224004.8216
60 | 2651076.5041 | 1224028.9612 | 2651068.7718 | 1224029.9369
61 | 2651057.5724 | 1223998.7127 | 2651057.5856 | 1223998.9249
62 | 2651076.5041 | 1224028.9612 | 2651070.8927 | 1224019.3208
63 | 2651076.5041 | 1224028.9612 | 2651086.009 | 1224045.2861
64 | 2651115.9892 | 1224070.0713 | 2651111.3559 | 1224058.1431
65 | 2651115.9892 | 1224070.0713 | 2651123.6279 | 1224089.7366
66 | 2651111.3559 | 1224058.1431 | 2651111.0489 | 1224057.3528
67 | 2651124.3428 | 1224091.577 | 2651123.6279 | 1224089.7366
68 | 2651086.009 | 1224045.2861 | 2651095.5568 | 1224034.5169 | 2651106.5625 | 1224027.0401 | 2651104.7969 | 1224035.7414 | 2651105.5815 | 1224043.275 | 2651111.0489 | 1224057.3528
69 | 2651111.0489 | 1224057.3528 | 2651131.3247 | 1224041.1543
70 | 2651130.8738 | 1224115.9926 | 2651129.7062 | 1224105.3982 | 2651124.3428 | 1224091.577
71 | 2651124.3428 | 1224091.577 | 2651108.2845 | 1224094.6962
72 | 2651086.009 | 1224045.2861 | 2651074.6578 | 1224058.1045
73 | 2651142.2068 | 1224032.4605 | 2651131.3247 | 1224041.1543
74 | 2651130.8738 | 1224115.9926 | 2651114.8679 | 1224118.7907
75 | 2651130.8738 | 1224115.9926 | 2651146.363 | 1224113.5351 | 2651148.3131 | 1224113.281
76 | 2651130.8738 | 1224115.9926 | 2651130.7328 | 1224124.4633 | 2651129.4532 | 1224152.1177
77 | 2651085.699 | 1224099.0834 | 2651108.2845 | 1224094.6962
78 | 2651114.8679 | 1224118.7907 | 2651102.8679 | 1224120.8886 | 2651092.588 | 1224123.613
79 | 2651151.0647 | 1224112.9224 | 2651148.3131 | 1224113.281
80 | 2651142.0141 | 1223991.3445 | 2651153.2129 | 1224010.1695
81 | 2651133.0417 | 1223978.3595 | 2651146.9609 | 1223968.0504 | 2651153.4008 | 1223957.199
82 | 2651133.0417 | 1223978.3595 | 2651128.8705 | 1223972.0708
83 | 2651133.0417 | 1223978.3595 | 2651142.0141 | 1223991.3445
84 | 2651128.8705 | 1223972.0708 | 2651117.4141 | 1223954.7991
85 | 2651092.588 | 1224123.613 | 2651081.0873 | 1224126.6609 | 2651064.5593 | 1224129.1207 | 2651058.5495 | 1224129.1869
86 | 2651102.7963 | 1223938.2616 | 2651114.4997 | 1223950.4053 | 2651117.4141 | 1223954.7991
87 | 2651102.7963 | 1223938.2616 | 2651095.4625 | 1223930.652 | 2651091.2463 | 1223926.2687 | 2651085.6298 | 1223922.8878
88 | 2651059.2232 | 1223906.8163 | 2651070.9538 | 1223914.0538 | 2651085.6298 | 1223922.8878
89 | 2651032.0482 | 1223890.05 | 2651059.2232 | 1223906.8163
90 | 2651032.0482 | 1223890.05 | 2651039.8301 | 1223876.0648
91 | 2651039.8301 | 1223876.0648 | 2651049.7422 | 1223858.2513
92 | 2651057.5724 | 1223998.7127 | 2651057.2094 | 1223992.8764
93 | 2651057.2094 | 1223992.8764 | 2651056.8596 | 1223987.2514
94 | 2651056.5527 | 1223982.3169 | 2651056.8596 | 1223987.2514
95 | 2651049.7422 | 1223858.2513 | 2651059.9693 | 1223839.8716
96 | 2650879.1535 | 1223814.3509 | 2650877.5643 | 1223829.947 | 2650880.3314 | 1223845.1022 | 2650880.5609 | 1223847.7708
97 | 2650944.0742 | 1223846.6035 | 2650880.5609 | 1223847.7708
98 | 2650879.1535 | 1223814.3509 | 2650871.2381 | 1223804.6067
99 | 2650972.7935 | 1223858.5899 | 2650944.0742 | 1223846.6035
100 | 2650871.2381 | 1223804.6067 | 2650870.2894 | 1223803.4387
101 | 2650972.7935 | 1223858.5899 | 2650980.8354 | 1223844.2313
102 | 2650858.773 | 1223789.2614 | 2650870.2894 | 1223803.4387
103 | 2650858.773 | 1223789.2614 | 2650881.4598 | 1223770.4571
104 | 2650827.6974 | 1223755.6532 | 2650839.3082 | 1223765.2471 | 2650845.1037 | 1223772.1008 | 2650853.7345 | 1223782.5698 | 2650858.773 | 1223789.2614
105 | 2650881.4598 | 1223770.4571 | 2650886.2472 | 1223766.489
106 | 2650827.6974 | 1223755.6532 | 2650872.8667 | 1223720.1898
107 | 2650872.8667 | 1223720.1898 | 2650887.1211 | 1223708.9984 | 2650890.419 | 1223703.7567 | 2650890.4606 | 1223702.7977
108 | 2650974.8831 | 1223789.5839 | 2650986.1237 | 1223768.7804
109 | 2651001.455 | 1223755.1714 | 2650996.3461 | 1223754.9497 | 2650991.5285 | 1223758.7775 | 2650986.1237 | 1223768.7804
110 | 2651006.367 | 1223752.7119 | 2651001.455 | 1223755.1714
111 | 2651096.7785 | 1223812.6445 | 2651091.5102 | 1223823.0739 | 2651087.7918 | 1223826.0549 | 2651087.7918 | 1223826.0549
112 | 2651104.5003 | 1223797.3583 | 2651096.7785 | 1223812.6445
113 | 2651073.9286 | 1223814.7847 | 2651083.3131 | 1223824.8491 | 2651087.7918 | 1223826.0549
114 | 2651073.1694 | 1223782.1914 | 2651074.9715 | 1223778.9604 | 2651105.9666 | 1223794.3802 | 2651104.5003 | 1223797.3583
115 | 2651073.9286 | 1223814.7847 | 2651064.8753 | 1223807.2643
116 | 2651073.9286 | 1223814.7847 | 2651062.8084 | 1223834.7693
117 | 2651073.1694 | 1223782.1914 | 2651069.7825 | 1223779.2272 | 2651066.4651 | 1223781.4334
118 | 2651073.1694 | 1223782.1914 | 2651065.9225 | 1223795.1817
119 | 2651047.7196 | 1223793.0132 | 2651064.8753 | 1223807.2643
120 | 2651062.8084 | 1223834.7693 | 2651059.9693 | 1223839.8716
121 | 2651065.9225 | 1223795.1817 | 2651062.9882 | 1223800.4598 | 2651070.2351 | 1223806.0254 | 2651076.0916 | 1223809.1663
122 | 2651065.9225 | 1223795.1817 | 2651063.0017 | 1223792.6996
123 | 2651047.7196 | 1223793.0132 | 2651039.4698 | 1223785.9048
124 | 2651047.7196 | 1223793.0132 | 2651032.4396 | 1223820.3429
125 | 2651023.9281 | 1223770.5066 | 2651022.1966 | 1223768.9855
126 | 2651006.367 | 1223752.7119 | 2651008.9908 | 1223756.2366 | 2651011.4798 | 1223759.571 | 2651022.1966 | 1223768.9855
127 | 2651023.9281 | 1223770.5066 | 2651022.9314 | 1223771.7766 | 2651022.2807 | 1223772.4937 | 2651020.3753 | 1223773.6337 | 2651016.381 | 1223780.7654
128 | 2651034.348 | 1223778.3452 | 2651023.9281 | 1223770.5066
129 | 2651006.367 | 1223752.7119 | 2651012.3638 | 1223744.3855
130 | 2651004.3707 | 1223802.2094 | 2651016.381 | 1223780.7654
131 | 2651034.348 | 1223778.3452 | 2651039.9312 | 1223783.385 | 2651039.4698 | 1223785.9048
132 | 2650992.5519 | 1223823.3118 | 2651004.3707 | 1223802.2094
133 | 2650980.8354 | 1223844.2313 | 2650992.5519 | 1223823.3118
134 | 2651010.4877 | 1223859.6056 | 2651021.7389 | 1223839.482
135 | 2651021.7389 | 1223839.482 | 2651032.4396 | 1223820.3429

## bus_geodata
| x | y | coords
0 | 2651401.394 | 1223999.4026
1 | 2651394.2142 | 1224014.574
2 | 2651389.1966 | 1224041.6527
3 | 2651359.6363 | 1224007.7779
4 | 2651394.3628 | 1224055.9791
5 | 2651343.7196 | 1224004.3211
6 | 2651409.7396 | 1224059.5816
7 | 2651336.976 | 1224002.8732
8 | 2651339.4997 | 1224028.9437
9 | 2651282.4267 | 1223940.3122
10 | 2651280.4731 | 1223951.0194
11 | 2651284.1289 | 1223930.9835
12 | 2651275.8791 | 1223976.1972
13 | 2651288.3751 | 1223907.712
14 | 2651273.3554 | 1223990.0284
15 | 2651297.0475 | 1223866.3448
16 | 2651294.5412 | 1223994.3057
17 | 2651271.1967 | 1223999.2801
18 | 2651250.9751 | 1223859.2772
19 | 2651282.0329 | 1224091.9253
20 | 2651282.5641 | 1224089.6036
21 | 2651286.4281 | 1224072.7142
22 | 2651273.016 | 1224070.0132
23 | 2651255.5149 | 1224066.4887
24 | 2651434.3906 | 1224064.9964
25 | 2651431.5892 | 1224025.7344
26 | 2651259.8532 | 1224047.896
27 | 2651251.9332 | 1224084.5751
28 | 2651215.3109 | 1224059.6498
29 | 2651263.9142 | 1224030.4913
30 | 2651203.4501 | 1224120.6856
31 | 2651178.8985 | 1224047.4626
32 | 2651341.4861 | 1223982.2421
33 | 2651295.9629 | 1223994.5927
34 | 2651342.6135 | 1224034.0966
35 | 2651346.9813 | 1223957.018
36 | 2651265.9315 | 1224021.8457
37 | 2651184.7321 | 1224116.0303
38 | 2651201.0643 | 1224138.4919
39 | 2651157.3639 | 1224017.1473
40 | 2651242.303 | 1223905.7884
41 | 2651237.3491 | 1223932.3582
42 | 2651348.2217 | 1223950.9988
43 | 2651200.6578 | 1223906.8943
44 | 2651198.7923 | 1223906.5929
45 | 2651163.1786 | 1223902.0489
46 | 2651163.5113 | 1223917.0528
47 | 2651155.1511 | 1223877.287
48 | 2651157.8354 | 1223944.9851
49 | 2651154.9035 | 1223876.0862
50 | 2651059.2333 | 1224025.3442
51 | 2651058.8794 | 1224019.6691
52 | 2651059.592 | 1224031.0953
53 | 2651058.5069 | 1224013.6972
54 | 2651066.6638 | 1224030.203
55 | 2651057.9533 | 1224004.8216
56 | 2651068.7718 | 1224029.9369
57 | 2651057.5856 | 1223998.9249
58 | 2651076.5041 | 1224028.9612
59 | 2651115.9892 | 1224070.0713
60 | 2651111.3559 | 1224058.1431
61 | 2651123.6279 | 1224089.7366
62 | 2651111.0489 | 1224057.3528
63 | 2651124.3428 | 1224091.577
64 | 2651086.009 | 1224045.2861
65 | 2651131.3247 | 1224041.1543
66 | 2651130.8738 | 1224115.9926
67 | 2651108.2845 | 1224094.6962
68 | 2651074.6578 | 1224058.1045
69 | 2651142.2068 | 1224032.4605
70 | 2651114.8679 | 1224118.7907
71 | 2651148.3131 | 1224113.281
72 | 2651129.4532 | 1224152.1177
73 | 2651085.699 | 1224099.0834
74 | 2651232.6636 | 1223958.099
75 | 2651151.0646 | 1224112.9224
76 | 2651153.2129 | 1224010.1695
77 | 2651153.4008 | 1223957.199
78 | 2651151.5604 | 1223859.8786
79 | 2651133.0417 | 1223978.3595
80 | 2651128.8705 | 1223972.0708
81 | 2651142.0141 | 1223991.3445
82 | 2651092.588 | 1224123.613
83 | 2651058.5495 | 1224129.1869
84 | 2651117.4141 | 1223954.7991
85 | 2651102.7963 | 1223938.2616
86 | 2651070.8927 | 1224019.3208
87 | 2651085.6298 | 1223922.8878
88 | 2651059.2232 | 1223906.8163
89 | 2651032.0482 | 1223890.05
90 | 2651039.8301 | 1223876.0648
91 | 2651057.5724 | 1223998.7127
92 | 2651057.2094 | 1223992.8764
93 | 2651056.8596 | 1223987.2514
94 | 2651049.7422 | 1223858.2513
95 | 2651056.5527 | 1223982.3169
96 | 2650880.5609 | 1223847.7708
97 | 2650879.1534 | 1223814.3509
98 | 2650944.0742 | 1223846.6035
99 | 2650871.2381 | 1223804.6067
100 | 2650972.7935 | 1223858.5899
101 | 2650870.2894 | 1223803.4387
102 | 2650858.773 | 1223789.2614
103 | 2650881.4598 | 1223770.4571
104 | 2650827.6974 | 1223755.6532
105 | 2650886.2472 | 1223766.489
106 | 2650872.8667 | 1223720.1898
107 | 2650890.4606 | 1223702.7977
108 | 2650986.1237 | 1223768.7804
109 | 2650974.8831 | 1223789.5839
110 | 2651001.455 | 1223755.1714
111 | 2651096.7785 | 1223812.6445
112 | 2651087.7918 | 1223826.0549
113 | 2651104.5003 | 1223797.3583
114 | 2651073.9286 | 1223814.7847
115 | 2651073.1694 | 1223782.1914
116 | 2651064.8753 | 1223807.2643
117 | 2651062.8084 | 1223834.7694
118 | 2651076.0916 | 1223809.1663
119 | 2651065.9225 | 1223795.1817
120 | 2651066.4651 | 1223781.4334
121 | 2651047.7196 | 1223793.0132
122 | 2651059.9693 | 1223839.8716
123 | 2651063.0017 | 1223792.6996
124 | 2651022.1966 | 1223768.9855
125 | 2651023.9281 | 1223770.5066
126 | 2651006.367 | 1223752.7119
127 | 2651016.381 | 1223780.7654
128 | 2651034.348 | 1223778.3452
129 | 2651012.3638 | 1223744.3855
130 | 2651004.3707 | 1223802.2094
131 | 2651039.4698 | 1223785.9048
132 | 2650992.5519 | 1223823.3118
133 | 2650980.8354 | 1223844.2313
134 | 2651010.4877 | 1223859.6056
135 | 2651021.7389 | 1223839.482
136 | 2651032.4396 | 1223820.3429
137 | 2651133.0417 | 1223978.3595

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97453 | -0.49046 | 0.0044677 | 0.0011197
1 | 0.9746 | -0.48903 | 0 | 0
2 | 0.97431 | -0.49479 | 0.0036628 | 0.00091798
3 | 0.97512 | -0.47876 | 0.0039529 | 0.00099069
4 | 0.97416 | -0.49769 | 0.0011961 | 0.00029977
5 | 0.97542 | -0.47285 | 0 | 0
6 | 0.97407 | -0.49958 | 0.0032644 | 0.00081813
7 | 0.97559 | -0.46945 | 0 | 0
8 | 0.97525 | -0.47614 | 0.0032036 | 0.0008029
9 | 0.97686 | -0.44448 | 0.001959 | 0.00049097
10 | 0.97704 | -0.4411 | 0.0056587 | 0.0014182
11 | 0.97673 | -0.44708 | 0.0039584 | 0.00099206
12 | 0.97757 | -0.43052 | 0.0037742 | 0.00094591
13 | 0.97649 | -0.45187 | 0.0031731 | 0.00079526
14 | 0.97792 | -0.42375 | 0 | 0
15 | 0.97618 | -0.45803 | 0 | 0
16 | 0.97704 | -0.44107 | 0.0059381 | 0.0014882
17 | 0.97854 | -0.41157 | 0.0043436 | 0.0010886
18 | 0.97584 | -0.46475 | 0 | 0
19 | 0.98313 | -0.32204 | 0.002975 | 0.0007456
20 | 0.98314 | -0.32191 | 0.0033944 | 0.00085072
21 | 0.98324 | -0.31992 | 0.0027689 | 0.00069396
22 | 0.98336 | -0.31767 | 0.0021555 | 0.00054021
23 | 0.98354 | -0.31403 | 0 | 0
24 | 0.97399 | -0.50109 | 0 | 0
25 | 0.97387 | -0.50345 | 0.0032618 | 0.0008175
26 | 0.9821 | -0.34217 | 0.0027204 | 0.00068179
27 | 0.98352 | -0.31452 | 0.0014679 | 0.00036789
28 | 0.98711 | -0.24509 | 0 | 0
29 | 0.98079 | -0.3677 | 0.0018022 | 0.00045168
30 | 0.98344 | -0.31588 | 0 | 0
31 | 0.9911 | -0.16851 | 0.0013394 | 0.0003357
32 | 0.97542 | -0.47285 | 0.0029977 | 0.00075129
33 | 0.97699 | -0.44207 | 0.00221 | 0.00055387
34 | 0.97522 | -0.47674 | 0.0039756 | 0.00099637
35 | 0.97528 | -0.47559 | 0.002569 | 0.00064384
36 | 0.98015 | -0.38012 | 0.002441 | 0.00061176
37 | 0.98242 | -0.33574 | 0.0015677 | 0.00039291
38 | 0.98323 | -0.31998 | 0.012664 | 0.0031738
39 | 0.99369 | -0.11935 | 0.0073365 | 0.0018387
40 | 0.97549 | -0.47159 | 0.0029243 | 0.00073291
41 | 0.97536 | -0.47406 | 0.0023032 | 0.00057724
42 | 0.97526 | -0.47595 | 0.003219 | 0.00080676
43 | 0.99645 | -0.068351 | 0.011966 | 0.002999
44 | 0.99647 | -0.067954 | 0.0071281 | 0.0017865
45 | 0.99709 | -0.055891 | 0 | 0
46 | 0.99773 | -0.043626 | 0.0095471 | 0.0023927
47 | 0.99644 | -0.06844 | 0.0088017 | 0.0022059
48 | 0.99919 | -0.015611 | 0.012801 | 0.0032081
49 | 0.99642 | -0.068841 | 0.008953 | 0.0022438
50 | 0.97114 | -0.55671 | 0.0033124 | 0.00083017
51 | 0.97106 | -0.55843 | 0.0033622 | 0.00084265
52 | 0.97125 | -0.55461 | 0.003475 | 0.00087093
53 | 0.97098 | -0.55988 | 0.0037291 | 0.00093461
54 | 0.9714 | -0.55155 | 0.0030101 | 0.00075441
55 | 0.9709 | -0.56142 | 0.0038114 | 0.00095523
56 | 0.97146 | -0.55052 | 0.003968 | 0.00099448
57 | 0.97087 | -0.56202 | 0 | 0
58 | 0.97167 | -0.54617 | 0 | 0
59 | 0.97602 | -0.46066 | 0.00052935 | 0.00013267
60 | 0.97534 | -0.47399 | 0.0051049 | 0.0012794
61 | 0.97715 | -0.43851 | 0.00045468 | 0.00011395
62 | 0.9753 | -0.4748 | 0 | 0
63 | 0.97726 | -0.43642 | 0 | 0
64 | 0.97248 | -0.53022 | 0 | 0
65 | 0.97528 | -0.47524 | 0.00046339 | 0.00011614
66 | 0.97876 | -0.40712 | 0 | 0
67 | 0.97718 | -0.43797 | 0.00050344 | 0.00012617
68 | 0.9724 | -0.53183 | 0.0050838 | 0.0012741
69 | 0.97527 | -0.47535 | 0.00045212 | 0.00011331
70 | 0.97849 | -0.41233 | 0.0065445 | 0.0016402
71 | 0.98035 | -0.37593 | 0.009805 | 0.0024574
72 | 0.9782 | -0.41801 | 0.016555 | 0.004149
73 | 0.97708 | -0.43995 | 0.004696 | 0.0011769
74 | 0.9753 | -0.47534 | 0.0026683 | 0.00066874
75 | 0.98063 | -0.37054 | 0.0054734 | 0.0013718
76 | 0.99426 | -0.10837 | 0.00052465 | 0.00013149
77 | 1 | 0 | -0.40614 | -0.10377
78 | 0.99627 | -0.07165 | 0.0096698 | 0.0024235
79 | 0.99695 | -0.057482 | 0 | 0
80 | 0.99627 | -0.070592 | 0.018184 | 0.0045575
81 | 0.99583 | -0.07875 | 0 | 0
82 | 0.97826 | -0.41693 | 0.0041647 | 0.0010438
83 | 0.97803 | -0.4213 | 0.006917 | 0.0017336
84 | 0.99473 | -0.10005 | 0.010504 | 0.0026327
85 | 0.99329 | -0.12751 | 0.0053948 | 0.0013521
86 | 0.97151 | -0.54939 | 0.015618 | 0.0039143
87 | 0.9919 | -0.15416 | 0.0022687 | 0.0005686
88 | 0.99011 | -0.18852 | 0.001634 | 0.00040951
89 | 0.98832 | -0.22322 | 0 | 0
90 | 0.98742 | -0.24066 | 0.00063305 | 0.00015866
91 | 0.97087 | -0.56204 | 0.0017302 | 0.00043363
92 | 0.97085 | -0.56245 | 0.0012132 | 0.00030405
93 | 0.97084 | -0.56272 | 0.0011936 | 0.00029913
94 | 0.98628 | -0.26269 | 0.00057831 | 0.00014494
95 | 0.97083 | -0.56285 | 0.0013877 | 0.0003478
96 | 0.98128 | -0.36036 | 0.0001883 | 4.7191e-05
97 | 0.98117 | -0.36245 | 0 | 0
98 | 0.98149 | -0.35621 | 0 | 0
99 | 0.98113 | -0.36323 | 0.00022693 | 5.6874e-05
100 | 0.98159 | -0.35418 | 0 | 0
101 | 0.98113 | -0.36331 | 0.0010125 | 0.00025375
102 | 0.98109 | -0.36403 | 0 | 0
103 | 0.98108 | -0.36426 | 0.00015377 | 3.8538e-05
104 | 0.98102 | -0.3655 | 0 | 0
105 | 0.98108 | -0.36429 | 0.00026377 | 6.6108e-05
106 | 0.98092 | -0.36732 | 0.0014686 | 0.00036807
107 | 0.98092 | -0.36745 | 0.00028603 | 7.1685e-05
108 | 0.98184 | -0.34927 | 0.0026086 | 0.00065379
109 | 0.98179 | -0.35024 | 0.002275 | 0.00057017
110 | 0.98194 | -0.34727 | 0 | 0
111 | 0.98274 | -0.33177 | 0.015174 | 0.0038029
112 | 0.98304 | -0.32586 | 0.012415 | 0.0031115
113 | 0.98266 | -0.33324 | 0 | 0
114 | 0.98359 | -0.31513 | 0 | 0
115 | 0.98248 | -0.33682 | 0 | 0
116 | 0.98331 | -0.32047 | 0.00067775 | 0.00016986
117 | 0.9848 | -0.29146 | 0.0016316 | 0.00040891
118 | 0.98242 | -0.33802 | 0.001145 | 0.00028695
119 | 0.98244 | -0.33757 | 0 | 0
120 | 0.98246 | -0.33712 | 0.0019528 | 0.00048941
121 | 0.98281 | -0.33033 | 0 | 0
122 | 0.98512 | -0.28525 | 0.00063668 | 0.00015957
123 | 0.98243 | -0.33768 | 0.0016542 | 0.00041459
124 | 0.98213 | -0.34362 | 0.0028189 | 0.00070649
125 | 0.98215 | -0.34318 | 0 | 0
126 | 0.98197 | -0.34679 | 0 | 0
127 | 0.98204 | -0.34546 | 0.0022586 | 0.00056606
128 | 0.9824 | -0.33844 | 0 | 0
129 | 0.98194 | -0.34731 | 0.0027936 | 0.00070013
130 | 0.98187 | -0.34876 | 0.0021079 | 0.0005283
131 | 0.98258 | -0.33476 | 0.0023371 | 0.00058574
132 | 0.98175 | -0.35109 | 0.00068435 | 0.00017151
133 | 0.98165 | -0.35311 | 0.001034 | 0.00025915
134 | 0.98271 | -0.33224 | 0.00065507 | 0.00016418
135 | 0.98273 | -0.33197 | 0.00068223 | 0.00017098
136 | 0.98275 | -0.33144 | 0.00062712 | 0.00015717
137 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0044677 | -0.0011197 | 0.004468 | 0.0011197 | 3.0373e-07 | -2.2484e-08 | 0.0068217 | 0.0068217 | 0.0068217 | 0.97453 | -0.49046 | 0.9746 | -0.48903 | 1.8741
1 | 0.01139 | 0.0028552 | -0.011387 | -0.0028536 | 3.1236e-06 | 1.656e-06 | 0.017391 | 0.017391 | 0.017391 | 0.9746 | -0.48903 | 0.97431 | -0.49479 | 4.7778
2 | -0.015858 | -0.0039749 | 0.015866 | 0.0039794 | 7.7642e-06 | 4.5287e-06 | 0.024213 | 0.024213 | 0.024213 | 0.9746 | -0.48903 | 0.97512 | -0.47876 | 6.6519
3 | 0.0077246 | 0.0019356 | -0.0077235 | -0.0019352 | 1.0652e-06 | 4.2757e-07 | 0.011797 | 0.011797 | 0.011797 | 0.97431 | -0.49479 | 0.97416 | -0.49769 | 3.241
4 | -0.019819 | -0.0049701 | 0.019825 | 0.0049735 | 5.5872e-06 | 3.3725e-06 | 0.030245 | 0.030245 | 0.030245 | 0.97512 | -0.47876 | 0.97542 | -0.47285 | 8.309
5 | 0.0065274 | 0.0016354 | -0.0065268 | -0.0016352 | 5.8892e-07 | 1.8024e-07 | 0.0099703 | 0.0099704 | 0.0099704 | 0.97416 | -0.49769 | 0.97407 | -0.49958 | 2.7391
6 | -0.027005 | -0.0067731 | 0.027009 | 0.0067759 | 4.3778e-06 | 2.7159e-06 | 0.041198 | 0.041198 | 0.041198 | 0.97542 | -0.47285 | 0.97559 | -0.46945 | 11.3182
7 | 0.0071804 | 0.0017996 | -0.0071793 | -0.0017992 | 1.1241e-06 | 4.0762e-07 | 0.010954 | 0.010954 | 0.010954 | 0.97542 | -0.47285 | 0.97525 | -0.47614 | 3.0093
8 | 0.0032624 | 0.00081708 | -0.0032622 | -0.00081724 | 2.3512e-07 | -1.6372e-07 | 0.0049836 | 0.0049837 | 0.0049837 | 0.97407 | -0.49958 | 0.97399 | -0.50109 | 1.3692
9 | 0.0087879 | 0.0022027 | -0.0087865 | -0.002202 | 1.4228e-06 | 6.4694e-07 | 0.013404 | 0.013404 | 0.013404 | 0.97559 | -0.46945 | 0.97542 | -0.47285 | 3.6824
10 | -0.035797 | -0.0089785 | 0.035844 | 0.0090079 | 4.6779e-05 | 2.9415e-05 | 0.054602 | 0.054602 | 0.054602 | 0.97559 | -0.46945 | 0.97699 | -0.44207 | 15.0006
11 | 0.0039757 | 0.00099634 | -0.0039756 | -0.00099637 | 1.1473e-07 | -3.032e-08 | 0.006066 | 0.006066 | 0.006066 | 0.97525 | -0.47614 | 0.97522 | -0.47674 | 1.6665
12 | -0.016999 | -0.0042624 | 0.017002 | 0.0042641 | 2.7367e-06 | 1.6152e-06 | 0.025895 | 0.025894 | 0.025895 | 0.97686 | -0.44448 | 0.97704 | -0.4411 | 7.1139
13 | 0.01504 | 0.0037715 | -0.015038 | -0.0037704 | 1.8665e-06 | 1.0759e-06 | 0.02291 | 0.022911 | 0.022911 | 0.97686 | -0.44448 | 0.97673 | -0.44708 | 6.2941
14 | -0.02266 | -0.0056823 | 0.022672 | 0.0056893 | 1.1432e-05 | 6.9957e-06 | 0.034513 | 0.034513 | 0.034513 | 0.97704 | -0.4411 | 0.97757 | -0.43052 | 9.4815
15 | 0.01108 | 0.0027783 | -0.011077 | -0.002777 | 2.5277e-06 | 1.3217e-06 | 0.01688 | 0.01688 | 0.01688 | 0.97673 | -0.44708 | 0.97649 | -0.45187 | 4.6374
16 | -0.026446 | -0.0066352 | 0.026455 | 0.0066405 | 8.5446e-06 | 5.2922e-06 | 0.040257 | 0.040257 | 0.040257 | 0.97757 | -0.43052 | 0.97792 | -0.42375 | 11.0597
17 | 0.007904 | 0.0019818 | -0.0079017 | -0.0019808 | 2.3208e-06 | 9.5185e-07 | 0.012045 | 0.012045 | 0.012045 | 0.97649 | -0.45187 | 0.97618 | -0.45803 | 3.3091
18 | 0.04403 | 0.011074 | -0.043994 | -0.011051 | 3.6396e-05 | 2.3022e-05 | 0.067011 | 0.067012 | 0.067012 | 0.97792 | -0.42375 | 0.97704 | -0.44107 | 18.4098
19 | -0.070485 | -0.017715 | 0.070526 | 0.017741 | 4.0993e-05 | 2.6117e-05 | 0.10727 | 0.10727 | 0.10727 | 0.97792 | -0.42375 | 0.97854 | -0.41157 | 29.4695
20 | 0.0079017 | 0.0019808 | -0.0078992 | -0.0019798 | 2.529e-06 | 1.0377e-06 | 0.012045 | 0.012045 | 0.012045 | 0.97618 | -0.45803 | 0.97584 | -0.46475 | 3.3091
21 | 0.038056 | 0.009563 | -0.038054 | -0.0095618 | 1.8275e-06 | 1.1515e-06 | 0.057968 | 0.057968 | 0.057968 | 0.97704 | -0.44107 | 0.97699 | -0.44207 | 15.9252
22 | -0.07487 | -0.018829 | 0.074982 | 0.018901 | 0.00011268 | 7.1822e-05 | 0.11387 | 0.11387 | 0.11387 | 0.97854 | -0.41157 | 0.98015 | -0.38012 | 31.284
23 | 0.0078992 | 0.0019798 | -0.0078966 | -0.0019787 | 2.5742e-06 | 1.0566e-06 | 0.012045 | 0.012045 | 0.012045 | 0.97584 | -0.46475 | 0.97549 | -0.47159 | 3.3092
24 | -0.002975 | -0.0007456 | 0.002975 | 0.00074558 | 1.8108e-08 | -1.8612e-08 | 0.0045027 | 0.0045027 | 0.0045027 | 0.98313 | -0.32204 | 0.98314 | -0.32191 | 1.237
25 | -0.0063694 | -0.0015963 | 0.00637 | 0.0015965 | 6.0381e-07 | 1.6671e-07 | 0.0096403 | 0.0096402 | 0.0096403 | 0.98314 | -0.32191 | 0.98324 | -0.31992 | 2.6484
26 | -0.0091389 | -0.0022904 | 0.0091399 | 0.0022909 | 9.814e-07 | 4.5455e-07 | 0.013831 | 0.013831 | 0.013831 | 0.98324 | -0.31992 | 0.98336 | -0.31767 | 3.7996
27 | -0.011295 | -0.0028311 | 0.011297 | 0.0028321 | 1.9558e-06 | 1.0252e-06 | 0.017092 | 0.017092 | 0.017092 | 0.98336 | -0.31767 | 0.98354 | -0.31403 | 4.6957
28 | 0.0822 | 0.020808 | -0.082089 | -0.020738 | 0.00011086 | 7.0708e-05 | 0.12444 | 0.12444 | 0.12444 | 0.98354 | -0.31403 | 0.9821 | -0.34217 | 34.1855
29 | 0.0014679 | 0.00036768 | -0.0014679 | -0.00036789 | 3.41e-08 | -2.1216e-07 | 0.0022208 | 0.0022208 | 0.0022208 | 0.98354 | -0.31403 | 0.98352 | -0.31452 | 0.61012
30 | -0.094965 | -0.024008 | 0.09528 | 0.024209 | 0.00031511 | 0.00020115 | 0.14375 | 0.14375 | 0.14375 | 0.98354 | -0.31403 | 0.98711 | -0.24509 | 39.4912
31 | 0.0032622 | 0.00081724 | -0.0032618 | -0.0008175 | 3.6663e-07 | -2.5518e-07 | 0.0049837 | 0.0049839 | 0.0049839 | 0.97399 | -0.50109 | 0.97387 | -0.50345 | 1.3692
32 | 0.079369 | 0.020056 | -0.079272 | -0.019994 | 9.7015e-05 | 6.1864e-05 | 0.12031 | 0.12031 | 0.12031 | 0.9821 | -0.34217 | 0.98079 | -0.3677 | 33.0532
33 | 0.1281 | 0.032607 | -0.12767 | -0.03233 | 0.00043558 | 0.00027719 | 0.19329 | 0.19329 | 0.19329 | 0.98711 | -0.24509 | 0.98344 | -0.31588 | 26.5503
34 | -0.22338 | -0.056816 | 0.22421 | 0.057345 | 0.00082764 | 0.00052869 | 0.33703 | 0.33703 | 0.33703 | 0.98711 | -0.24509 | 0.9911 | -0.16851 | 46.2958
35 | 0.077469 | 0.019542 | -0.077423 | -0.019513 | 4.6026e-05 | 2.9345e-05 | 0.11758 | 0.11758 | 0.11758 | 0.98079 | -0.3677 | 0.98015 | -0.38012 | 32.3021
36 | 0.115 | 0.029155 | -0.11489 | -0.029085 | 0.00010966 | 6.9694e-05 | 0.17412 | 0.17412 | 0.17412 | 0.98344 | -0.31588 | 0.98242 | -0.33574 | 23.9178
37 | 0.012666 | 0.0031751 | -0.012664 | -0.0031738 | 2.4744e-06 | 1.3557e-06 | 0.019165 | 0.019165 | 0.019165 | 0.98344 | -0.31588 | 0.98323 | -0.31998 | 5.2651
38 | -0.22555 | -0.057681 | 0.22609 | 0.058024 | 0.00053797 | 0.00034285 | 0.33904 | 0.33904 | 0.33904 | 0.9911 | -0.16851 | 0.99369 | -0.11935 | 31.048
39 | 0.0057888 | 0.0014507 | -0.005788 | -0.0014506 | 7.5496e-07 | 1.6098e-07 | 0.0088308 | 0.0088309 | 0.0088309 | 0.97542 | -0.47285 | 0.97528 | -0.47559 | 2.4261
40 | 0.0032191 | 0.00080672 | -0.003219 | -0.00080676 | 5.5593e-08 | -4.111e-08 | 0.0049114 | 0.0049114 | 0.0049114 | 0.97528 | -0.47559 | 0.97526 | -0.47595 | 1.3493
41 | 0.11332 | 0.028692 | -0.11313 | -0.028572 | 0.00018898 | 0.00012008 | 0.17175 | 0.17175 | 0.17175 | 0.98242 | -0.33574 | 0.98063 | -0.37054 | 23.5917
42 | -0.23342 | -0.059862 | 0.23355 | 0.059942 | 0.00012435 | 7.9265e-05 | 0.35003 | 0.35003 | 0.35003 | 0.99369 | -0.11935 | 0.99426 | -0.10837 | 32.054
43 | 0.0049723 | 0.0012458 | -0.0049717 | -0.0012458 | 5.8306e-07 | 3.5787e-08 | 0.0075846 | 0.0075847 | 0.0075847 | 0.97549 | -0.47159 | 0.97536 | -0.47406 | 2.0837
44 | 0.0026685 | 0.00066852 | -0.0026683 | -0.00066874 | 1.6261e-07 | -2.2246e-07 | 0.004071 | 0.0040711 | 0.0040711 | 0.97536 | -0.47406 | 0.9753 | -0.47534 | 1.1184
45 | -0.011966 | -0.002999 | 0.011967 | 0.0029992 | 2.2628e-07 | 1.202e-07 | 0.01787 | 0.01787 | 0.01787 | 0.99645 | -0.068351 | 0.99647 | -0.067954 | 4.9092
46 | -0.019095 | -0.0047856 | 0.019106 | 0.0047922 | 1.098e-05 | 6.5579e-06 | 0.028514 | 0.028514 | 0.028514 | 0.99647 | -0.067954 | 0.99709 | -0.055891 | 7.8335
47 | -0.046548 | -0.011676 | 0.046576 | 0.011694 | 2.7232e-05 | 1.7232e-05 | 0.06947 | 0.06947 | 0.06947 | 0.99709 | -0.055891 | 0.99773 | -0.043626 | 19.0852
48 | 0.027443 | 0.0068842 | -0.027426 | -0.0068741 | 1.6407e-05 | 1.0161e-05 | 0.040956 | 0.040957 | 0.040957 | 0.99709 | -0.055891 | 0.99644 | -0.06844 | 11.2518
49 | -0.056123 | -0.014086 | 0.056198 | 0.014134 | 7.5097e-05 | 4.7688e-05 | 0.083709 | 0.083709 | 0.083709 | 0.99773 | -0.043626 | 0.99919 | -0.015611 | 22.9969
50 | 0.018624 | 0.0046681 | -0.018624 | -0.0046679 | 3.5564e-07 | 2.1164e-07 | 0.027813 | 0.027813 | 0.027813 | 0.99644 | -0.06844 | 0.99642 | -0.068841 | 7.6408
51 | -0.068998 | -0.017342 | 0.06905 | 0.017375 | 5.1466e-05 | 3.2768e-05 | 0.10277 | 0.10277 | 0.10277 | 0.99919 | -0.015611 | 1 | 0 | 28.2339
52 | 0.0096711 | 0.0024241 | -0.0096698 | -0.0024235 | 1.2945e-06 | 6.1293e-07 | 0.014443 | 0.014443 | 0.014443 | 0.99642 | -0.068841 | 0.99627 | -0.07165 | 3.9678
53 | 0.016431 | 0.0041186 | -0.016429 | -0.0041178 | 1.3515e-06 | 7.9461e-07 | 0.025176 | 0.025176 | 0.025176 | 0.97114 | -0.55671 | 0.97106 | -0.55843 | 6.9164
54 | -0.019743 | -0.0049488 | 0.019745 | 0.00495 | 1.9775e-06 | 1.1943e-06 | 0.030251 | 0.030251 | 0.030251 | 0.97114 | -0.55671 | 0.97125 | -0.55461 | 8.3108
55 | 0.013067 | 0.0032752 | -0.013066 | -0.0032747 | 8.9966e-07 | 5.0177e-07 | 0.020024 | 0.020024 | 0.020024 | 0.97106 | -0.55843 | 0.97098 | -0.55988 | 5.501
56 | -0.02322 | -0.0058209 | 0.023223 | 0.005823 | 3.3829e-06 | 2.0768e-06 | 0.035575 | 0.035575 | 0.035575 | 0.97125 | -0.55461 | 0.9714 | -0.55155 | 9.7734
57 | 0.0093371 | 0.0023401 | -0.0093364 | -0.0023397 | 6.8279e-07 | 3.27e-07 | 0.014309 | 0.014309 | 0.014309 | 0.97098 | -0.55988 | 0.9709 | -0.56142 | 3.931
58 | -0.026234 | -0.0065774 | 0.026235 | 0.0065782 | 1.2867e-06 | 7.972e-07 | 0.040186 | 0.040186 | 0.040186 | 0.9714 | -0.55155 | 0.97146 | -0.55052 | 11.0402
59 | 0.005525 | 0.0013845 | -0.0055248 | -0.0013845 | 1.5885e-07 | 2.8603e-08 | 0.0084675 | 0.0084676 | 0.0084676 | 0.9709 | -0.56142 | 0.97087 | -0.56202 | 2.3263
60 | -0.030203 | -0.0075727 | 0.030209 | 0.0075766 | 6.2555e-06 | 3.907e-06 | 0.046264 | 0.046264 | 0.046264 | 0.97146 | -0.55052 | 0.97167 | -0.54617 | 12.7099
61 | 0.0055248 | 0.0013845 | -0.0055248 | -0.0013845 | 5.717e-09 | 1.0287e-09 | 0.0084676 | 0.0084676 | 0.0084676 | 0.97087 | -0.56202 | 0.97087 | -0.56204 | 2.3263
62 | 0.015621 | 0.0039157 | -0.015618 | -0.0039143 | 2.3937e-06 | 1.3938e-06 | 0.023921 | 0.023921 | 0.023921 | 0.97167 | -0.54617 | 0.97151 | -0.54939 | 6.5718
63 | -0.04583 | -0.011492 | 0.045865 | 0.011514 | 3.4872e-05 | 2.2084e-05 | 0.070186 | 0.070185 | 0.070186 | 0.97167 | -0.54617 | 0.97248 | -0.53022 | 19.2817
64 | 0.057143 | 0.014407 | -0.057106 | -0.014384 | 3.6446e-05 | 2.3166e-05 | 0.087149 | 0.087149 | 0.087149 | 0.97602 | -0.46066 | 0.97534 | -0.47399 | 23.9422
65 | -0.057672 | -0.01454 | 0.057733 | 0.014579 | 6.1205e-05 | 3.8907e-05 | 0.087956 | 0.087956 | 0.087956 | 0.97602 | -0.46066 | 0.97715 | -0.43851 | 24.1639
66 | 0.052001 | 0.013104 | -0.051999 | -0.013103 | 2.0024e-06 | 1.271e-06 | 0.079361 | 0.079361 | 0.079361 | 0.97534 | -0.47399 | 0.9753 | -0.4748 | 21.8025
67 | -0.058188 | -0.014693 | 0.058194 | 0.014696 | 5.8182e-06 | 3.6989e-06 | 0.088649 | 0.088649 | 0.088649 | 0.97715 | -0.43851 | 0.97726 | -0.43642 | 24.354
68 | 0.051084 | 0.012874 | -0.050949 | -0.012788 | 0.00013506 | 8.5703e-05 | 0.077965 | 0.077965 | 0.077965 | 0.9753 | -0.4748 | 0.97248 | -0.53022 | 21.4189
69 | 0.00091553 | 0.00022896 | -0.00091551 | -0.00022928 | 1.8985e-08 | -3.117e-07 | 0.0013967 | 0.0013968 | 0.0013968 | 0.9753 | -0.4748 | 0.97528 | -0.47524 | 0.38373
70 | -0.063394 | -0.015999 | 0.063483 | 0.016056 | 8.9109e-05 | 5.671e-05 | 0.096567 | 0.096567 | 0.096567 | 0.97726 | -0.43642 | 0.97876 | -0.40712 | 26.5294
71 | 0.0052003 | 0.0013031 | -0.0051999 | -0.0013031 | 3.8461e-07 | 4.1211e-08 | 0.0079182 | 0.0079183 | 0.0079183 | 0.97726 | -0.43642 | 0.97718 | -0.43797 | 2.1753
72 | 0.0050842 | 0.0012742 | -0.0050838 | -0.0012741 | 3.8858e-07 | 3.6274e-08 | 0.0077794 | 0.0077795 | 0.0077795 | 0.97248 | -0.53022 | 0.9724 | -0.53183 | 2.1372
73 | 0.00045212 | 0.00011314 | -0.00045212 | -0.00011331 | 2.4852e-09 | -1.7222e-07 | 0.00068975 | 0.00068982 | 0.00068982 | 0.97528 | -0.47524 | 0.97527 | -0.47535 | 0.18951
74 | 0.017634 | 0.0044219 | -0.01763 | -0.0044193 | 4.3799e-06 | 2.599e-06 | 0.026811 | 0.026811 | 0.026811 | 0.97876 | -0.40712 | 0.97849 | -0.41233 | 7.3656
75 | -0.097681 | -0.024632 | 0.097827 | 0.024725 | 0.00014607 | 9.3264e-05 | 0.14856 | 0.14856 | 0.14856 | 0.97876 | -0.40712 | 0.98035 | -0.37593 | 40.8132
76 | 0.016563 | 0.0041541 | -0.016555 | -0.004149 | 8.5984e-06 | 5.0488e-06 | 0.025183 | 0.025183 | 0.025183 | 0.97876 | -0.40712 | 0.9782 | -0.41801 | 6.9184
77 | 0.0046965 | 0.0011769 | -0.004696 | -0.0011769 | 4.4129e-07 | -5.7705e-09 | 0.0071516 | 0.0071517 | 0.0071517 | 0.97718 | -0.43797 | 0.97708 | -0.43995 | 1.9648
78 | 0.011086 | 0.0027791 | -0.011083 | -0.0027778 | 2.4317e-06 | 1.2698e-06 | 0.016858 | 0.016858 | 0.016858 | 0.97849 | -0.41233 | 0.97826 | -0.41693 | 4.6314
79 | -0.10763 | -0.027183 | 0.10766 | 0.0272 | 2.7797e-05 | 1.7755e-05 | 0.16344 | 0.16344 | 0.16344 | 0.98035 | -0.37593 | 0.98063 | -0.37054 | 44.9017
80 | -0.23407 | -0.060073 | 0.23441 | 0.060288 | 0.00033697 | 0.00021481 | 0.35081 | 0.35081 | 0.35081 | 0.99426 | -0.10837 | 0.99583 | -0.07875 | 32.1259
81 | 0.33544 | 0.086398 | -0.33451 | -0.085801 | 0.0009355 | 0.00059754 | 0.49997 | 0.49997 | 0.49997 | 1 | 0 | 0.99695 | -0.057482 | 45.7847
82 | 0.099854 | 0.025358 | -0.099791 | -0.025318 | 6.2957e-05 | 4.0194e-05 | 0.14916 | 0.14916 | 0.14916 | 0.99695 | -0.057482 | 0.99627 | -0.070592 | 40.9768
83 | 0.23465 | 0.060443 | -0.23441 | -0.060288 | 0.0002426 | 0.00015465 | 0.35081 | 0.35081 | 0.35081 | 0.99695 | -0.057482 | 0.99583 | -0.07875 | 32.1259
84 | 0.081606 | 0.02076 | -0.081491 | -0.020687 | 0.00011567 | 7.3761e-05 | 0.122 | 0.122 | 0.122 | 0.99627 | -0.070592 | 0.99473 | -0.10005 | 33.5153
85 | 0.0069184 | 0.001734 | -0.006917 | -0.0017336 | 1.4377e-06 | 4.856e-07 | 0.010524 | 0.010524 | 0.010524 | 0.97826 | -0.41693 | 0.97803 | -0.4213 | 2.8911
86 | 0.070986 | 0.018054 | -0.070892 | -0.017994 | 9.3775e-05 | 5.9729e-05 | 0.10628 | 0.10628 | 0.10628 | 0.99473 | -0.10005 | 0.99329 | -0.12751 | 29.1984
87 | 0.065498 | 0.016642 | -0.065414 | -0.016589 | 8.3919e-05 | 5.3408e-05 | 0.0982 | 0.098201 | 0.098201 | 0.99329 | -0.12751 | 0.9919 | -0.15416 | 26.9782
88 | 0.063145 | 0.01602 | -0.063041 | -0.015954 | 0.00010418 | 6.6274e-05 | 0.094797 | 0.094797 | 0.094797 | 0.9919 | -0.15416 | 0.99011 | -0.18852 | 26.0432
89 | 0.061407 | 0.015544 | -0.061305 | -0.015479 | 0.0001021 | 6.4936e-05 | 0.092342 | 0.092342 | 0.092342 | 0.99011 | -0.18852 | 0.98832 | -0.22322 | 25.3686
90 | 0.061305 | 0.015479 | -0.061254 | -0.015447 | 5.1176e-05 | 3.2548e-05 | 0.092342 | 0.092342 | 0.092342 | 0.98832 | -0.22322 | 0.98742 | -0.24066 | 25.3686
91 | 0.060621 | 0.015288 | -0.060557 | -0.015248 | 6.3846e-05 | 4.0601e-05 | 0.091388 | 0.091388 | 0.091388 | 0.98742 | -0.24066 | 0.98628 | -0.26269 | 25.1066
92 | 0.0037946 | 0.00095085 | -0.0037945 | -0.00095088 | 7.4169e-08 | -2.4843e-08 | 0.0058157 | 0.0058158 | 0.0058158 | 0.97087 | -0.56204 | 0.97085 | -0.56245 | 1.5977
93 | 0.0025813 | 0.00064683 | -0.0025813 | -0.00064687 | 3.3081e-08 | -4.8518e-08 | 0.0039563 | 0.0039564 | 0.0039564 | 0.97085 | -0.56245 | 0.97084 | -0.56272 | 1.0869
94 | 0.0013877 | 0.00034774 | -0.0013877 | -0.0003478 | 8.3877e-09 | -5.5766e-08 | 0.002127 | 0.002127 | 0.002127 | 0.97084 | -0.56272 | 0.97083 | -0.56285 | 0.58434
95 | 0.059978 | 0.015103 | -0.059914 | -0.015062 | 6.4623e-05 | 4.1091e-05 | 0.090515 | 0.090516 | 0.090516 | 0.98628 | -0.26269 | 0.98512 | -0.28525 | 24.8669
96 | 0.0034124 | 0.00085265 | -0.0034121 | -0.00085286 | 3.3889e-07 | -2.0955e-07 | 0.0051737 | 0.0051738 | 0.0051738 | 0.98128 | -0.36036 | 0.98117 | -0.36245 | 1.4214
97 | -0.0036007 | -0.00089984 | 0.0036014 | 0.00089949 | 7.0992e-07 | -3.483e-07 | 0.0054592 | 0.0054589 | 0.0054592 | 0.98128 | -0.36036 | 0.98149 | -0.35621 | 1.4998
98 | 0.0034121 | 0.00085286 | -0.003412 | -0.00085293 | 1.2602e-07 | -7.7896e-08 | 0.0051738 | 0.0051739 | 0.0051739 | 0.98117 | -0.36245 | 0.98113 | -0.36323 | 1.4214
99 | -0.0036014 | -0.00089949 | 0.0036018 | 0.00089932 | 3.469e-07 | -1.7035e-07 | 0.0054589 | 0.0054588 | 0.0054589 | 0.98149 | -0.35621 | 0.98159 | -0.35418 | 1.4997
100 | 0.003185 | 0.00079606 | -0.003185 | -0.00079607 | 1.3163e-08 | -1.0579e-08 | 0.0048297 | 0.0048297 | 0.0048297 | 0.98113 | -0.36323 | 0.98113 | -0.36331 | 1.3268
101 | -0.0036018 | -0.00089932 | 0.003602 | 0.00089923 | 1.839e-07 | -9.0349e-08 | 0.0054588 | 0.0054587 | 0.0054588 | 0.98159 | -0.35418 | 0.98165 | -0.35311 | 1.4997
102 | 0.0021725 | 0.00054232 | -0.0021725 | -0.0005425 | 7.4329e-08 | -1.8309e-07 | 0.0032942 | 0.0032942 | 0.0032942 | 0.98113 | -0.36331 | 0.98109 | -0.36403 | 0.90501
103 | 0.00041755 | 0.0001042 | -0.00041754 | -0.00010457 | 4.4304e-09 | -3.6926e-07 | 0.00063313 | 0.00063327 | 0.00063327 | 0.98109 | -0.36403 | 0.98108 | -0.36426 | 0.17397
104 | 0.0017549 | 0.0004383 | -0.0017548 | -0.00043881 | 1.2212e-07 | -5.0245e-07 | 0.0026611 | 0.0026613 | 0.0026613 | 0.98109 | -0.36403 | 0.98102 | -0.3655 | 0.73113
105 | 0.00026377 | 6.6029e-05 | -0.00026377 | -6.6108e-05 | 3.7316e-10 | -7.8281e-08 | 0.00040004 | 0.00040007 | 0.00040007 | 0.98108 | -0.36426 | 0.98108 | -0.36429 | 0.10991
106 | 0.0017548 | 0.00043881 | -0.0017546 | -0.00043943 | 1.5254e-07 | -6.2738e-07 | 0.0026613 | 0.0026616 | 0.0026616 | 0.98102 | -0.3655 | 0.98092 | -0.36732 | 0.7312
107 | 0.00028603 | 7.1367e-05 | -0.00028603 | -7.1685e-05 | 1.7839e-09 | -3.1792e-07 | 0.00043378 | 0.00043389 | 0.00043389 | 0.98092 | -0.36732 | 0.98092 | -0.36745 | 0.1192
108 | 0.0022751 | 0.00056994 | -0.002275 | -0.00057017 | 1.0542e-07 | -2.3157e-07 | 0.0034479 | 0.003448 | 0.003448 | 0.98184 | -0.34927 | 0.98179 | -0.35024 | 0.94725
109 | -0.0048837 | -0.0012237 | 0.0048842 | 0.0012237 | 4.6501e-07 | 1.1287e-08 | 0.0074014 | 0.0074013 | 0.0074014 | 0.98184 | -0.34927 | 0.98194 | -0.34727 | 2.0333
110 | -0.0048842 | -0.0012237 | 0.0048843 | 0.0012237 | 1.1259e-07 | 2.7228e-09 | 0.0074013 | 0.0074013 | 0.0074013 | 0.98194 | -0.34727 | 0.98197 | -0.34679 | 2.0333
111 | -0.019927 | -0.0049934 | 0.019933 | 0.0049968 | 5.616e-06 | 3.3858e-06 | 0.030173 | 0.030173 | 0.030173 | 0.98274 | -0.33177 | 0.98304 | -0.32586 | 8.2892
112 | 0.0047533 | 0.0011904 | -0.0047529 | -0.0011904 | 3.3264e-07 | -4.0803e-09 | 0.0071969 | 0.007197 | 0.007197 | 0.98274 | -0.33177 | 0.98266 | -0.33324 | 1.9772
113 | -0.032348 | -0.0081082 | 0.032364 | 0.0081186 | 1.6542e-05 | 1.0354e-05 | 0.048965 | 0.048965 | 0.048965 | 0.98304 | -0.32586 | 0.98359 | -0.31513 | 13.4519
114 | 0.0047529 | 0.0011904 | -0.0047521 | -0.0011904 | 8.0878e-07 | -9.7632e-09 | 0.007197 | 0.0071972 | 0.0071972 | 0.98266 | -0.33324 | 0.98248 | -0.33682 | 1.9772
115 | 0.025199 | 0.006322 | -0.025192 | -0.006318 | 6.4148e-06 | 3.9561e-06 | 0.038124 | 0.038124 | 0.038124 | 0.98359 | -0.31513 | 0.98331 | -0.32047 | 10.4736
116 | -0.057563 | -0.014441 | 0.057628 | 0.014482 | 6.5047e-05 | 4.1339e-05 | 0.087089 | 0.087089 | 0.087089 | 0.98359 | -0.31513 | 0.9848 | -0.29146 | 23.9255
117 | 0.0019528 | 0.00048932 | -0.0019528 | -0.00048941 | 2.7784e-08 | -8.9477e-08 | 0.0029576 | 0.0029576 | 0.0029576 | 0.98248 | -0.33682 | 0.98246 | -0.33712 | 0.81253
118 | 0.0027993 | 0.00070112 | -0.0027992 | -0.00070124 | 1.0021e-07 | -1.2413e-07 | 0.0042396 | 0.0042396 | 0.0042396 | 0.98248 | -0.33682 | 0.98244 | -0.33757 | 1.1647
119 | 0.024514 | 0.0061482 | -0.024503 | -0.0061411 | 1.1511e-05 | 7.0841e-06 | 0.037098 | 0.037099 | 0.037099 | 0.98331 | -0.32047 | 0.98281 | -0.33033 | 10.1919
120 | -0.059259 | -0.014891 | 0.059277 | 0.014902 | 1.756e-05 | 1.1164e-05 | 0.089554 | 0.089554 | 0.089554 | 0.9848 | -0.29146 | 0.98512 | -0.28525 | 24.6027
121 | -0.001145 | -0.00028695 | 0.001145 | 0.00028669 | 2.461e-08 | -2.6057e-07 | 0.0017342 | 0.0017341 | 0.0017342 | 0.98242 | -0.33802 | 0.98244 | -0.33757 | 0.47643
122 | 0.0016543 | 0.00041455 | -0.0016542 | -0.00041459 | 9.0094e-09 | -4.2693e-08 | 0.0025055 | 0.0025056 | 0.0025056 | 0.98244 | -0.33757 | 0.98243 | -0.33768 | 0.68834
123 | 0.022538 | 0.0056496 | -0.022534 | -0.0056467 | 4.7554e-06 | 2.9055e-06 | 0.034124 | 0.034124 | 0.034124 | 0.98281 | -0.33033 | 0.98258 | -0.33476 | 9.3749
124 | 0.0019646 | 0.00049146 | -0.0019645 | -0.00049179 | 1.0386e-07 | -3.3028e-07 | 0.0029741 | 0.0029743 | 0.0029743 | 0.98281 | -0.33033 | 0.98275 | -0.33144 | 0.8171
125 | -0.010498 | -0.0026307 | 0.010498 | 0.0026308 | 2.1865e-07 | 1.1077e-07 | 0.015905 | 0.015905 | 0.015905 | 0.98213 | -0.34362 | 0.98215 | -0.34318 | 4.3696
126 | 0.0076791 | 0.0019242 | -0.0076779 | -0.0019238 | 1.1583e-06 | 4.5261e-07 | 0.011634 | 0.011635 | 0.011635 | 0.98213 | -0.34362 | 0.98197 | -0.34679 | 3.1963
127 | 0.0096901 | 0.0024252 | -0.0096891 | -0.0024247 | 1.0487e-06 | 5.0697e-07 | 0.01468 | 0.01468 | 0.01468 | 0.98215 | -0.34318 | 0.98204 | -0.34546 | 4.0329
128 | -0.020188 | -0.0050561 | 0.020193 | 0.0050588 | 4.5656e-06 | 2.7572e-06 | 0.030585 | 0.030585 | 0.030585 | 0.98215 | -0.34318 | 0.9824 | -0.33844 | 8.4025
129 | 0.0027936 | 0.00070005 | -0.0027936 | -0.00070013 | 6.8957e-08 | -8.5672e-08 | 0.0042333 | 0.0042333 | 0.0042333 | 0.98197 | -0.34679 | 0.98194 | -0.34731 | 1.163
130 | 0.0074305 | 0.0018587 | -0.0074293 | -0.0018582 | 1.1681e-06 | 4.3667e-07 | 0.011258 | 0.011258 | 0.011258 | 0.98204 | -0.34546 | 0.98187 | -0.34876 | 3.0928
131 | -0.020193 | -0.0050588 | 0.020196 | 0.005061 | 3.5371e-06 | 2.1361e-06 | 0.030585 | 0.030585 | 0.030585 | 0.9824 | -0.33844 | 0.98258 | -0.33476 | 8.4025
132 | 0.0053214 | 0.0013299 | -0.0053208 | -0.0013299 | 5.8969e-07 | 7.1532e-08 | 0.0080632 | 0.0080633 | 0.0080633 | 0.98187 | -0.34876 | 0.98175 | -0.35109 | 2.2152
133 | 0.0046364 | 0.0011584 | -0.004636 | -0.0011584 | 4.4387e-07 | -1.9077e-08 | 0.007026 | 0.0070262 | 0.0070262 | 0.98175 | -0.35109 | 0.98165 | -0.35311 | 1.9303
134 | -0.00065507 | -0.00016418 | 0.00065508 | 0.00016389 | 8.5055e-09 | -2.8666e-07 | 0.00099191 | 0.00099181 | 0.00099191 | 0.98271 | -0.33224 | 0.98273 | -0.33197 | 0.2725
135 | -0.0013373 | -0.00033487 | 0.0013373 | 0.00033462 | 3.3711e-08 | -2.5625e-07 | 0.0020248 | 0.0020247 | 0.0020248 | 0.98273 | -0.33197 | 0.98275 | -0.33144 | 0.55627

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.41246 | 0.10536

## res_load
| p_mw | q_mvar
0 | 0.0044677 | 0.0011197
1 | 0.0036628 | 0.00091798
2 | 0.0039529 | 0.00099069
3 | 0.0011961 | 0.00029977
4 | 0.0032644 | 0.00081813
5 | 0.0032036 | 0.0008029
6 | 0.001959 | 0.00049097
7 | 0.0056587 | 0.0014182
8 | 0.0039584 | 0.00099206
9 | 0.0037742 | 0.00094591
10 | 0.0031731 | 0.00079526
11 | 0.0059381 | 0.0014882
12 | 0.0043436 | 0.0010886
13 | 0.002975 | 0.0007456
14 | 0.0033944 | 0.00085072
15 | 0.0027689 | 0.00069396
16 | 0.0021555 | 0.00054021
17 | 0.0032618 | 0.0008175
18 | 0.0027204 | 0.00068179
19 | 0.0014679 | 0.00036789
20 | 0.0018022 | 0.00045168
21 | 0.0013394 | 0.0003357
22 | 0.0029977 | 0.00075129
23 | 0.00221 | 0.00055387
24 | 0.0039756 | 0.00099637
25 | 0.002569 | 0.00064384
26 | 0.002441 | 0.00061176
27 | 0.0015677 | 0.00039291
28 | 0.012664 | 0.0031738
29 | 0.0073365 | 0.0018387
30 | 0.0029243 | 0.00073291
31 | 0.0023032 | 0.00057724
32 | 0.003219 | 0.00080676
33 | 0.011966 | 0.002999
34 | 0.0071281 | 0.0017865
35 | 0.0095471 | 0.0023927
36 | 0.0088017 | 0.0022059
37 | 0.012801 | 0.0032081
38 | 0.008953 | 0.0022438
39 | 0.0033124 | 0.00083017
40 | 0.0033622 | 0.00084265
41 | 0.003475 | 0.00087093
42 | 0.0037291 | 0.00093461
43 | 0.0030101 | 0.00075441
44 | 0.0038114 | 0.00095523
45 | 0.003968 | 0.00099448
46 | 0.00052935 | 0.00013267
47 | 0.0051049 | 0.0012794
48 | 0.00045468 | 0.00011395
49 | 0.00046339 | 0.00011614
50 | 0.00050344 | 0.00012617
51 | 0.0050838 | 0.0012741
52 | 0.00045212 | 0.00011331
53 | 0.0065445 | 0.0016402
54 | 0.009805 | 0.0024574
55 | 0.016555 | 0.004149
56 | 0.004696 | 0.0011769
57 | 0.0026683 | 0.00066874
58 | 0.0054734 | 0.0013718
59 | 0.00052465 | 0.00013149
60 | 0.0063226 | 0.0015846
61 | 0.0096698 | 0.0024235
62 | 0.018184 | 0.0045575
63 | 0.0041647 | 0.0010438
64 | 0.006917 | 0.0017336
65 | 0.010504 | 0.0026327
66 | 0.0053948 | 0.0013521
67 | 0.015618 | 0.0039143
68 | 0.0022687 | 0.0005686
69 | 0.001634 | 0.00040951
70 | 0.00063305 | 0.00015866
71 | 0.0017302 | 0.00043363
72 | 0.0012132 | 0.00030405
73 | 0.0011936 | 0.00029913
74 | 0.00057831 | 0.00014494
75 | 0.0013877 | 0.0003478
76 | 0.0001883 | 4.7191e-05
77 | 0.00022693 | 5.6874e-05
78 | 0.0010125 | 0.00025375
79 | 0.00015377 | 3.8538e-05
80 | 0.00026377 | 6.6108e-05
81 | 0.0014686 | 0.00036807
82 | 0.00028603 | 7.1685e-05
83 | 0.0026086 | 0.00065379
84 | 0.002275 | 0.00057017
85 | 0.015174 | 0.0038029
86 | 0.012415 | 0.0031115
87 | 0.00067775 | 0.00016986
88 | 0.0016316 | 0.00040891
89 | 0.001145 | 0.00028695
90 | 0.0019528 | 0.00048941
91 | 0.00063668 | 0.00015957
92 | 0.0016542 | 0.00041459
93 | 0.0028189 | 0.00070649
94 | 0.0022586 | 0.00056606
95 | 0.0027936 | 0.00070013
96 | 0.0021079 | 0.0005283
97 | 0.0023371 | 0.00058574
98 | 0.00068435 | 0.00017151
99 | 0.001034 | 0.00025915
100 | 0.00065507 | 0.00016418
101 | 0.00068223 | 0.00017098
102 | 0.00062712 | 0.00015717

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1