## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1103-3_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1103-3_0_6_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_1103-3_0_6_node_5 | 0.4 | n |  | TRUE
3 | bus_LV_1103-3_0_6_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1103-3_0_6_node_6 | 0.4 | n |  | TRUE
5 | bus_LV_1103-3_0_6_node_7 | 0.4 | n |  | TRUE
6 | bus_LV_1103-3_0_6_node_8 | 0.4 | n |  | TRUE
7 | bus_LV_1103-3_0_6_node_9 | 0.4 | n |  | TRUE
8 | bus_LV_1103-3_0_6_node_18 | 0.4 | n |  | TRUE
9 | bus_LV_1103-3_0_6_node_19 | 0.4 | n |  | TRUE
10 | bus_LV_1103-3_0_6_node_10 | 0.4 | n |  | TRUE
11 | bus_LV_1103-3_0_6_node_11 | 0.4 | n |  | TRUE
12 | bus_LV_1103-3_0_6_node_12 | 0.4 | n |  | TRUE
13 | bus_LV_1103-3_0_6_node_17 | 0.4 | n |  | TRUE
14 | bus_LV_1103-3_0_6_node_15 | 0.4 | n |  | TRUE
15 | bus_LV_1103-3_0_6_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_1103-3_0_6_node_14 | 0.4 | n |  | TRUE
17 | bus_LV_1103-3_0_6_node_16 | 0.4 | n |  | TRUE
18 | bus_LV_1103-3_0_6_node_25 | 0.4 | n |  | TRUE
19 | bus_LV_1103-3_0_6_node_21 | 0.4 | n |  | TRUE
20 | bus_LV_1103-3_0_6_node_23 | 0.4 | n |  | TRUE
21 | bus_LV_1103-3_0_6_node_27 | 0.4 | n |  | TRUE
22 | bus_LV_1103-3_0_6_node_28 | 0.4 | n |  | TRUE
23 | bus_LV_1103-3_0_6_node_24 | 0.4 | n |  | TRUE
24 | bus_LV_1103-3_0_6_node_26 | 0.4 | n |  | TRUE
25 | bus_LV_1103-3_0_6_node_22 | 0.4 | n |  | TRUE
26 | bus_LV_1103-3_0_6_node_29 | 0.4 | n |  | TRUE
27 | bus_MV_473_0_node_78 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1103-3_0_6_load_0 | 0 | 0.072499 | 0.01817 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1103-3_0_6_load_5 | 2 | 0.0034118 | 0.00085508 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1103-3_0_6_load_6 | 4 | 0.03002 | 0.0075238 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1103-3_0_6_load_8 | 6 | 0.0013641 | 0.00034187 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1103-3_0_6_load_9 | 7 | 0.0063188 | 0.0015836 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1103-3_0_6_load_18 | 8 | 0.0022021 | 0.00055191 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1103-3_0_6_load_19 | 9 | 0.01339 | 0.0033559 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1103-3_0_6_load_10 | 10 | 0.043285 | 0.010848 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1103-3_0_6_load_11 | 11 | 0.025505 | 0.0063921 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1103-3_0_6_load_12 | 12 | 0.042913 | 0.010755 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1103-3_0_6_load_17 | 13 | 0.030739 | 0.0077039 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1103-3_0_6_load_13 | 15 | 0.0089268 | 0.0022373 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1103-3_0_6_load_14 | 16 | 0.00036247 | 9.0844e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1103-3_0_6_load_16 | 17 | 0.053159 | 0.013323 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1103-3_0_6_load_27 | 21 | 0.03558 | 0.0089173 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1103-3_0_6_load_28 | 22 | 0.02192 | 0.0054937 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1103-3_0_6_load_22 | 25 | 0.061566 | 0.01543 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1103-3_0_6_load_29 | 26 | 0.091039 | 0.022817 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 12 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1103-3_0_6_line_0 |  | 0 | 1 | 0.032759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
1 | LV_1103-3_0_6_line_1 |  | 1 | 2 | 0.021365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1103-3_0_6_line_2 |  | 1 | 3 | 0.16792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
3 | LV_1103-3_0_6_line_3 |  | 3 | 4 | 0.06512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
4 | LV_1103-3_0_6_line_4 |  | 4 | 5 | 0.039545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
5 | LV_1103-3_0_6_line_5 |  | 5 | 6 | 0.01419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
6 | LV_1103-3_0_6_line_6 |  | 5 | 7 | 0.030516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1103-3_0_6_line_7 |  | 6 | 8 | 0.08417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
8 | LV_1103-3_0_6_line_8 |  | 8 | 9 | 0.035236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
9 | LV_1103-3_0_6_line_9 |  | 9 | 21 | 0.016625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
10 | LV_1103-3_0_6_line_10 |  | 10 | 11 | 0.12897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1103-3_0_6_line_11 |  | 11 | 12 | 0.086925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1103-3_0_6_line_12 |  | 12 | 13 | 0.011945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
13 | LV_1103-3_0_6_line_13 |  | 13 | 14 | 0.08365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
14 | LV_1103-3_0_6_line_14 |  | 14 | 17 | 0.086466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
15 | LV_1103-3_0_6_line_15 |  | 14 | 15 | 0.083331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1103-3_0_6_line_16 |  | 15 | 16 | 0.12704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1103-3_0_6_line_17 |  | 17 | 18 | 0.027387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
18 | LV_1103-3_0_6_line_18 |  | 18 | 19 | 0.088831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
19 | LV_1103-3_0_6_line_19 |  | 18 | 20 | 0.024302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
20 | LV_1103-3_0_6_line_20 |  | 19 | 22 | 0.094731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
21 | LV_1103-3_0_6_line_21 |  | 20 | 25 | 0.022154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
22 | LV_1103-3_0_6_line_22 |  | 21 | 22 | 0.0078071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
23 | LV_1103-3_0_6_line_23 |  | 23 | 24 | 0.098193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_1103-3_0_6_line_24 |  | 23 | 25 | 0.031057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
25 | LV_1103-3_0_6_line_25 |  | 24 | 26 | 0.063546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1103-3_0_6_trafo_12 | 0.63 MVA 20/0.4 kV | 27 | 12 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2650558.0536 | 1226549.7228 | 2650549.3096 | 1226581.2934
1 | 2650558.0536 | 1226549.7228 | 2650561.7283 | 1226550.7657 | 2650578.5717 | 1226555.6787
2 | 2650544.9998 | 1226436.6749 | 2650543.1405 | 1226440.5171 | 2650499.458 | 1226533.6711 | 2650512.9966 | 1226537.0102 | 2650517.3594 | 1226538.248 | 2650558.0536 | 1226549.7228
3 | 2650544.9998 | 1226436.6749 | 2650569.4488 | 1226386.0955 | 2650573.3204 | 1226378.0362
4 | 2650590.4442 | 1226342.3911 | 2650573.3204 | 1226378.0362
5 | 2650590.4442 | 1226342.3911 | 2650596.542 | 1226329.5783
6 | 2650590.4442 | 1226342.3911 | 2650593.799 | 1226343.6203 | 2650619.1085 | 1226352.8598
7 | 2650632.7127 | 1226253.5768 | 2650596.542 | 1226329.5783
8 | 2650632.7127 | 1226253.5768 | 2650647.8546 | 1226221.7607
9 | 2650647.8546 | 1226221.7607 | 2650654.9989 | 1226206.7492
10 | 2650473.9511 | 1226209.3474 | 2650473.1281 | 1226211.0138 | 2650461.7061 | 1226232.3858 | 2650447.0031 | 1226255.4422 | 2650394.6488 | 1226309.8913
11 | 2650473.9511 | 1226209.3474 | 2650498.0462 | 1226160.5603 | 2650508.5509 | 1226132.0873 | 2650508.8263 | 1226129.9415
12 | 2650510.3466 | 1226118.0938 | 2650508.8263 | 1226129.9415
13 | 2650514.0015 | 1226034.673 | 2650515.1428 | 1226052.9162 | 2650511.6434 | 1226107.9874 | 2650510.3466 | 1226118.0938
14 | 2650514.0015 | 1226034.673 | 2650526.6724 | 1226047.4996 | 2650590.9087 | 1226071.1044
15 | 2650514.0015 | 1226034.673 | 2650504.5827 | 1226020.0173 | 2650489.7485 | 1226009.3293 | 2650450.5634 | 1225986.5831 | 2650448.7107 | 1225985.19
16 | 2650364.2098 | 1225893.8887 | 2650367.7501 | 1225894.5471 | 2650380.0229 | 1225900.7437 | 2650389.0741 | 1225911.4269 | 2650417.3023 | 1225955.2708 | 2650436.117 | 1225975.7206 | 2650448.7107 | 1225985.19
17 | 2650616.6228 | 1226080.5285 | 2650607.2302 | 1226077.1021 | 2650590.9087 | 1226071.1044
18 | 2650616.6228 | 1226080.5285 | 2650678.0949 | 1226106.4341 | 2650695.9349 | 1226113.0123 | 2650699.0631 | 1226114.1618
19 | 2650616.6228 | 1226080.5285 | 2650625.5321 | 1226057.9124
20 | 2650699.0631 | 1226114.1618 | 2650658.3539 | 1226199.6998
21 | 2650625.5321 | 1226057.9124 | 2650633.6507 | 1226037.2995
22 | 2650658.3539 | 1226199.6998 | 2650654.9989 | 1226206.7492
23 | 2650645.0321 | 1226008.403 | 2650648.9754 | 1225998.397 | 2650645.3112 | 1225996.976 | 2650588.7159 | 1225975.048 | 2650594.4201 | 1225960.3095 | 2650587.885 | 1225957.7746
24 | 2650645.0321 | 1226008.403 | 2650633.6507 | 1226037.2995
25 | 2650555.8896 | 1225997.0384 | 2650573.4467 | 1225952.2263 | 2650587.885 | 1225957.7746

## bus_geodata
| x | y | coords
0 | 2650549.3096 | 1226581.2934
1 | 2650558.0536 | 1226549.7228
2 | 2650578.5717 | 1226555.6787
3 | 2650544.9998 | 1226436.6749
4 | 2650573.3204 | 1226378.0362
5 | 2650590.4442 | 1226342.3911
6 | 2650596.542 | 1226329.5783
7 | 2650619.1085 | 1226352.8598
8 | 2650632.7127 | 1226253.5768
9 | 2650647.8546 | 1226221.7607
10 | 2650394.6488 | 1226309.8913
11 | 2650473.9511 | 1226209.3474
12 | 2650508.8263 | 1226129.9415
13 | 2650510.3466 | 1226118.0938
14 | 2650514.0015 | 1226034.673
15 | 2650448.7107 | 1225985.19
16 | 2650364.2098 | 1225893.8887
17 | 2650590.9087 | 1226071.1044
18 | 2650616.6228 | 1226080.5285
19 | 2650699.0631 | 1226114.1618
20 | 2650625.5321 | 1226057.9124
21 | 2650654.9989 | 1226206.7492
22 | 2650658.3539 | 1226199.6998
23 | 2650645.0321 | 1226008.403
24 | 2650587.885 | 1225957.7746
25 | 2650633.6507 | 1226037.2995
26 | 2650555.8896 | 1225997.0384
27 | 2650514.0015 | 1226034.673

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97006 | -0.57797 | 0.072499 | 0.01817
1 | 0.9708 | -0.56332 | 0 | 0
2 | 0.97073 | -0.56467 | 0.0034118 | 0.00085508
3 | 0.97318 | -0.51628 | 0 | 0
4 | 0.97411 | -0.49809 | 0.03002 | 0.0075238
5 | 0.97489 | -0.48271 | 0 | 0
6 | 0.97519 | -0.47687 | 0.0013641 | 0.00034187
7 | 0.97471 | -0.48625 | 0.0063188 | 0.0015836
8 | 0.97697 | -0.44186 | 0.0022021 | 0.00055191
9 | 0.97773 | -0.42696 | 0.01339 | 0.0033559
10 | 0.98941 | -0.20369 | 0.043285 | 0.010848
11 | 0.99453 | -0.1048 | 0.025505 | 0.0063921
12 | 1 | 0 | -0.51203 | -0.13139
13 | 0.99904 | -0.018033 | 0.030739 | 0.0077039
14 | 0.99279 | -0.13619 | 0 | 0
15 | 0.99209 | -0.1499 | 0.0089268 | 0.0022373
16 | 0.99204 | -0.15072 | 0.00036247 | 9.0844e-05
17 | 0.98649 | -0.25702 | 0.053159 | 0.013323
18 | 0.98476 | -0.29038 | 0 | 0
19 | 0.98167 | -0.35022 | 0 | 0
20 | 0.98407 | -0.30372 | 0 | 0
21 | 0.97813 | -0.41913 | 0.03558 | 0.0089173
22 | 0.97837 | -0.41444 | 0.02192 | 0.0054937
23 | 0.98292 | -0.3261 | 0 | 0
24 | 0.97875 | -0.40708 | 0 | 0
25 | 0.98344 | -0.3159 | 0.061566 | 0.01543
26 | 0.97336 | -0.51292 | 0.091039 | 0.022817
27 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.072499 | -0.01817 | 0.07255 | 0.018201 | 5.0644e-05 | 3.1198e-05 | 0.11121 | 0.11121 | 0.11121 | 0.97006 | -0.57797 | 0.9708 | -0.56332 | 10.184
1 | 0.003412 | 0.00085496 | -0.0034118 | -0.00085508 | 2.1914e-07 | -1.239e-07 | 0.0052298 | 0.0052299 | 0.0052299 | 0.9708 | -0.56332 | 0.97073 | -0.56467 | 1.4368
2 | -0.075962 | -0.019056 | 0.076133 | 0.019155 | 0.00017074 | 9.8867e-05 | 0.11644 | 0.11644 | 0.11644 | 0.9708 | -0.56332 | 0.97318 | -0.51628 | 6.3977
3 | -0.076133 | -0.019155 | 0.076199 | 0.019193 | 6.6212e-05 | 3.8326e-05 | 0.11644 | 0.11643 | 0.11644 | 0.97318 | -0.51628 | 0.97411 | -0.49809 | 6.3975
4 | -0.10622 | -0.026717 | 0.1063 | 0.026765 | 7.8116e-05 | 4.7531e-05 | 0.16229 | 0.16229 | 0.16229 | 0.97411 | -0.49809 | 0.97489 | -0.48271 | 8.9171
5 | -0.11262 | -0.028349 | 0.11265 | 0.028368 | 3.1461e-05 | 1.925e-05 | 0.17194 | 0.17194 | 0.17194 | 0.97489 | -0.48271 | 0.97519 | -0.47687 | 9.4471
6 | 0.0063198 | 0.0015839 | -0.0063188 | -0.0015836 | 1.0648e-06 | 3.0107e-07 | 0.0096462 | 0.0096464 | 0.0096464 | 0.97489 | -0.48271 | 0.97471 | -0.48625 | 2.6501
7 | -0.11401 | -0.02871 | 0.1142 | 0.028827 | 0.00019116 | 0.00011708 | 0.17402 | 0.17402 | 0.17402 | 0.97519 | -0.47687 | 0.97697 | -0.44186 | 9.5614
8 | -0.11641 | -0.029379 | 0.11649 | 0.02943 | 8.3138e-05 | 5.1001e-05 | 0.17737 | 0.17737 | 0.17737 | 0.97697 | -0.44186 | 0.97773 | -0.42696 | 9.7456
9 | -0.12988 | -0.032786 | 0.12993 | 0.032816 | 4.8757e-05 | 3.0162e-05 | 0.19775 | 0.19775 | 0.19775 | 0.97773 | -0.42696 | 0.97813 | -0.41913 | 10.8653
10 | -0.043285 | -0.010848 | 0.04349 | 0.010978 | 0.00020495 | 0.00012951 | 0.065098 | 0.065097 | 0.065098 | 0.98941 | -0.20369 | 0.99453 | -0.1048 | 17.884
11 | -0.068995 | -0.01737 | 0.069342 | 0.017591 | 0.00034755 | 0.0002213 | 0.10326 | 0.10326 | 0.10326 | 0.99453 | -0.1048 | 1 | 0 | 28.3675
12 | 0.44104 | 0.11379 | -0.44065 | -0.11355 | 0.00038721 | 0.00024703 | 0.65743 | 0.65743 | 0.65743 | 1 | 0 | 0.99904 | -0.018033 | 36.1226
13 | 0.40991 | 0.10584 | -0.40756 | -0.10435 | 0.0023471 | 0.0014967 | 0.61165 | 0.61165 | 0.61165 | 0.99904 | -0.018033 | 0.99279 | -0.13619 | 33.6071
14 | 0.39827 | 0.10202 | -0.39595 | -0.10054 | 0.0023169 | 0.0014772 | 0.59772 | 0.59772 | 0.59772 | 0.99279 | -0.13619 | 0.98649 | -0.25702 | 32.8418
15 | 0.0092954 | 0.0023293 | -0.0092893 | -0.0023265 | 6.0656e-06 | 2.8052e-06 | 0.013932 | 0.013932 | 0.013932 | 0.99279 | -0.13619 | 0.99209 | -0.1499 | 3.8276
16 | 0.00036249 | 8.9213e-05 | -0.00036247 | -9.0844e-05 | 1.4067e-08 | -1.6313e-06 | 0.00054311 | 0.00054369 | 0.00054369 | 0.99209 | -0.1499 | 0.99204 | -0.15072 | 0.14937
17 | 0.34279 | 0.087217 | -0.34224 | -0.086866 | 0.00055015 | 0.00035035 | 0.51754 | 0.51754 | 0.51754 | 0.98649 | -0.25702 | 0.98476 | -0.29038 | 28.436
18 | 0.18859 | 0.047955 | -0.18804 | -0.047614 | 0.00054195 | 0.00034121 | 0.28521 | 0.28521 | 0.28521 | 0.98476 | -0.29038 | 0.98167 | -0.35022 | 15.671
19 | 0.15366 | 0.038911 | -0.15356 | -0.03885 | 9.8379e-05 | 6.1418e-05 | 0.23233 | 0.23233 | 0.23233 | 0.98476 | -0.29038 | 0.98407 | -0.30372 | 12.7652
20 | 0.18804 | 0.047614 | -0.18747 | -0.04725 | 0.00057795 | 0.00036392 | 0.28521 | 0.28521 | 0.28521 | 0.98167 | -0.35022 | 0.97837 | -0.41444 | 15.6711
21 | 0.15356 | 0.03885 | -0.15347 | -0.038794 | 8.9684e-05 | 5.5991e-05 | 0.23233 | 0.23233 | 0.23233 | 0.98407 | -0.30372 | 0.98344 | -0.3159 | 12.7653
22 | -0.16551 | -0.041733 | 0.16555 | 0.041756 | 3.7147e-05 | 2.3284e-05 | 0.25188 | 0.25188 | 0.25188 | 0.97813 | -0.41913 | 0.97837 | -0.41444 | 13.8393
23 | 0.091857 | 0.023337 | -0.091501 | -0.023111 | 0.00035662 | 0.00022576 | 0.13917 | 0.13918 | 0.13918 | 0.98292 | -0.3261 | 0.97875 | -0.40708 | 19.1175
24 | -0.091857 | -0.023337 | 0.091903 | 0.023364 | 4.5117e-05 | 2.6906e-05 | 0.13917 | 0.13917 | 0.13917 | 0.98292 | -0.3261 | 0.98344 | -0.3159 | 7.6469
25 | 0.091501 | 0.023111 | -0.091039 | -0.022817 | 0.00046158 | 0.00029462 | 0.13918 | 0.13918 | 0.13918 | 0.97875 | -0.40708 | 0.97336 | -0.51292 | 38.2351

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.55494 | 0.14214

## res_load
| p_mw | q_mvar
0 | 0.072499 | 0.01817
1 | 0.0034118 | 0.00085508
2 | 0.03002 | 0.0075238
3 | 0.0013641 | 0.00034187
4 | 0.0063188 | 0.0015836
5 | 0.0022021 | 0.00055191
6 | 0.01339 | 0.0033559
7 | 0.043285 | 0.010848
8 | 0.025505 | 0.0063921
9 | 0.042913 | 0.010755
10 | 0.030739 | 0.0077039
11 | 0.0089268 | 0.0022373
12 | 0.00036247 | 9.0844e-05
13 | 0.053159 | 0.013323
14 | 0.03558 | 0.0089173
15 | 0.02192 | 0.0054937
16 | 0.061566 | 0.01543
17 | 0.091039 | 0.022817

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1