## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1103-9_1_2_node_54 | 0.4 | n |  | TRUE
1 | bus_LV_1103-9_1_2_node_52 | 0.4 | n |  | TRUE
2 | bus_LV_1103-9_1_2_node_56 | 0.4 | n |  | TRUE
3 | bus_LV_1103-9_1_2_node_57 | 0.4 | n |  | TRUE
4 | bus_LV_1103-9_1_2_node_28 | 0.4 | n |  | TRUE
5 | bus_LV_1103-9_1_2_node_27 | 0.4 | n |  | TRUE
6 | bus_LV_1103-9_1_2_node_25 | 0.4 | n |  | TRUE
7 | bus_LV_1103-9_1_2_node_33 | 0.4 | n |  | TRUE
8 | bus_LV_1103-9_1_2_node_60 | 0.4 | n |  | TRUE
9 | bus_LV_1103-9_1_2_node_59 | 0.4 | n |  | TRUE
10 | bus_LV_1103-9_1_2_node_71 | 0.4 | n |  | TRUE
11 | bus_LV_1103-9_1_2_node_67 | 0.4 | n |  | TRUE
12 | bus_LV_1103-9_1_2_node_55 | 0.4 | n |  | TRUE
13 | bus_LV_1103-9_1_2_node_31 | 0.4 | n |  | TRUE
14 | bus_LV_1103-9_1_2_node_32 | 0.4 | n |  | TRUE
15 | bus_LV_1103-9_1_2_node_30 | 0.4 | n |  | TRUE
16 | bus_LV_1103-9_1_2_node_47 | 0.4 | n |  | TRUE
17 | bus_LV_1103-9_1_2_node_26 | 0.4 | n |  | TRUE
18 | bus_LV_1103-9_1_2_node_29 | 0.4 | n |  | TRUE
19 | bus_LV_1103-9_1_2_node_34 | 0.4 | n |  | TRUE
20 | bus_LV_1103-9_1_2_node_35 | 0.4 | n |  | TRUE
21 | bus_LV_1103-9_1_2_node_36 | 0.4 | n |  | TRUE
22 | bus_LV_1103-9_1_2_node_37 | 0.4 | n |  | TRUE
23 | bus_LV_1103-9_1_2_node_68 | 0.4 | n |  | TRUE
24 | bus_LV_1103-9_1_2_node_58 | 0.4 | n |  | TRUE
25 | bus_LV_1103-9_1_2_node_38 | 0.4 | n |  | TRUE
26 | bus_LV_1103-9_1_2_node_43 | 0.4 | n |  | TRUE
27 | bus_LV_1103-9_1_2_node_44 | 0.4 | n |  | TRUE
28 | bus_LV_1103-9_1_2_node_45 | 0.4 | n |  | TRUE
29 | bus_LV_1103-9_1_2_node_46 | 0.4 | n |  | TRUE
30 | bus_LV_1103-9_1_2_node_61 | 0.4 | n |  | TRUE
31 | bus_LV_1103-9_1_2_node_48 | 0.4 | n |  | TRUE
32 | bus_LV_1103-9_1_2_node_49 | 0.4 | n |  | TRUE
33 | bus_LV_1103-9_1_2_node_50 | 0.4 | n |  | TRUE
34 | bus_LV_1103-9_1_2_node_62 | 0.4 | n |  | TRUE
35 | bus_LV_1103-9_1_2_node_65 | 0.4 | n |  | TRUE
36 | bus_LV_1103-9_1_2_node_66 | 0.4 | n |  | TRUE
37 | bus_LV_1103-9_1_2_node_51 | 0.4 | n |  | TRUE
38 | bus_LV_1103-9_1_2_node_53 | 0.4 | n |  | TRUE
39 | bus_LV_1103-9_1_2_node_70 | 0.4 | n |  | TRUE
40 | bus_LV_1103-9_1_2_node_63 | 0.4 | n |  | TRUE
41 | bus_LV_1103-9_1_2_node_64 | 0.4 | n |  | TRUE
42 | bus_LV_1103-9_1_2_node_69 | 0.4 | n |  | TRUE
43 | bus_MV_131_1_node_148 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1103-9_1_2_load_54 | 0 | 0.0033504 | 0.0008397 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1103-9_1_2_load_52 | 1 | 0.0024593 | 0.00061636 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1103-9_1_2_load_56 | 2 | 0.0074725 | 0.0018728 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1103-9_1_2_load_28 | 4 | 0.014608 | 0.0036612 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1103-9_1_2_load_60 | 8 | 0.00063719 | 0.0001597 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1103-9_1_2_load_71 | 10 | 0.0010547 | 0.00026435 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1103-9_1_2_load_67 | 11 | 0.0044639 | 0.0011188 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1103-9_1_2_load_55 | 12 | 0.001709 | 0.00042831 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1103-9_1_2_load_32 | 14 | 0.029674 | 0.0074371 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1103-9_1_2_load_30 | 15 | 0.0017723 | 0.00044419 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1103-9_1_2_load_26 | 17 | 0.0064796 | 0.0016239 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1103-9_1_2_load_29 | 18 | 0.018048 | 0.0045233 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1103-9_1_2_load_36 | 21 | 0.0020846 | 0.00052245 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1103-9_1_2_load_37 | 22 | 0.0029168 | 0.00073101 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1103-9_1_2_load_68 | 23 | 0.0026053 | 0.00065295 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1103-9_1_2_load_58 | 24 | 0.0010659 | 0.00026715 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1103-9_1_2_load_38 | 25 | 0.0029298 | 0.00073428 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1103-9_1_2_load_43 | 26 | 0.002475 | 0.0006203 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1103-9_1_2_load_44 | 27 | 0.0047591 | 0.0011927 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1103-9_1_2_load_45 | 28 | 0.0029136 | 0.00073021 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1103-9_1_2_load_46 | 29 | 0.0046491 | 0.0011652 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1103-9_1_2_load_61 | 30 | 0.0030957 | 0.00077586 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1103-9_1_2_load_50 | 33 | 0.00092357 | 0.00023147 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1103-9_1_2_load_62 | 34 | 0.0016695 | 0.00041842 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1103-9_1_2_load_65 | 35 | 0.0024564 | 0.00061562 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1103-9_1_2_load_66 | 36 | 0.0018635 | 0.00046705 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1103-9_1_2_load_51 | 37 | 0.0024888 | 0.00062374 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1103-9_1_2_load_53 | 38 | 0.002297 | 0.00057568 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1103-9_1_2_load_70 | 39 | 0.0035598 | 0.00089217 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1103-9_1_2_load_63 | 40 | 0.0018672 | 0.00046796 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1103-9_1_2_load_64 | 41 | 0.002947 | 0.00073859 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1103-9_1_2_load_69 | 42 | 0.0013351 | 0.00033461 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 19 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1103-9_1_2_line_0 |  | 0 | 1 | 0.011094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1103-9_1_2_line_1 |  | 1 | 37 | 0.010637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1103-9_1_2_line_2 |  | 2 | 3 | 0.034208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1103-9_1_2_line_3 |  | 3 | 24 | 0.025654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1103-9_1_2_line_4 |  | 3 | 20 | 0.036988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1103-9_1_2_line_5 |  | 4 | 5 | 0.034403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1103-9_1_2_line_6 |  | 5 | 18 | 0.020095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1103-9_1_2_line_7 |  | 5 | 17 | 0.009854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1103-9_1_2_line_8 |  | 6 | 7 | 0.047696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1103-9_1_2_line_9 |  | 6 | 8 | 0.021405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1103-9_1_2_line_10 |  | 7 | 13 | 0.047527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1103-9_1_2_line_11 |  | 8 | 16 | 0.013956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1103-9_1_2_line_12 |  | 9 | 10 | 0.018296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1103-9_1_2_line_13 |  | 9 | 11 | 0.029459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1103-9_1_2_line_14 |  | 9 | 12 | 0.029373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1103-9_1_2_line_15 |  | 10 | 39 | 0.020524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1103-9_1_2_line_16 |  | 11 | 32 | 0.0017763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1103-9_1_2_line_17 |  | 12 | 38 | 0.012949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1103-9_1_2_line_18 |  | 13 | 14 | 0.053848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1103-9_1_2_line_19 |  | 13 | 15 | 0.035865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1103-9_1_2_line_20 |  | 16 | 30 | 0.036422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1103-9_1_2_line_21 |  | 16 | 28 | 0.013523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1103-9_1_2_line_22 |  | 18 | 19 | 0.073223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1103-9_1_2_line_23 |  | 19 | 20 | 0.016992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1103-9_1_2_line_24 |  | 20 | 23 | 0.0064526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1103-9_1_2_line_25 |  | 21 | 22 | 0.019382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1103-9_1_2_line_26 |  | 22 | 25 | 0.02036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1103-9_1_2_line_27 |  | 23 | 25 | 0.018068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1103-9_1_2_line_28 |  | 24 | 33 | 0.0081355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1103-9_1_2_line_29 |  | 26 | 27 | 0.033789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1103-9_1_2_line_30 |  | 26 | 28 | 0.011503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1103-9_1_2_line_31 |  | 27 | 29 | 0.04126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1103-9_1_2_line_32 |  | 30 | 34 | 0.0088722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1103-9_1_2_line_33 |  | 31 | 32 | 0.014261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1103-9_1_2_line_34 |  | 31 | 33 | 0.007431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1103-9_1_2_line_35 |  | 32 | 35 | 0.020491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1103-9_1_2_line_36 |  | 34 | 40 | 0.017423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1103-9_1_2_line_37 |  | 35 | 36 | 0.018021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1103-9_1_2_line_38 |  | 37 | 38 | 0.0083272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1103-9_1_2_line_39 |  | 39 | 42 | 0.0036418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1103-9_1_2_line_40 |  | 40 | 41 | 0.0069239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1103-9_1_2_line_41 |  | 41 | 42 | 0.023689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1103-9_1_2_trafo_34 | 0.63 MVA 20/0.4 kV | 43 | 19 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2650135.355 | 1225117.6329 | 2650127.79 | 1225125.747
1 | 2650142.6083 | 1225109.853 | 2650135.355 | 1225117.6329
2 | 2650239.1429 | 1225133.3667 | 2650213.5637 | 1225156.0792
3 | 2650239.1429 | 1225133.3667 | 2650224.6724 | 1225119.6806 | 2650220.8664 | 1225115.388
4 | 2650239.1429 | 1225133.3667 | 2650267.3953 | 1225109.4014
5 | 2650337.6073 | 1225169.0647 | 2650311.0941 | 1225190.9874
6 | 2650337.6073 | 1225169.0647 | 2650324.9223 | 1225153.4794
7 | 2650337.6073 | 1225169.0647 | 2650343.8223 | 1225176.7116
8 | 2650322.7429 | 1224991.2957 | 2650347.9095 | 1225007.7964 | 2650351.5594 | 1225010.0953 | 2650351.7946 | 1225013.6551 | 2650351.1211 | 1225018.8859 | 2650349.8796 | 1225023.1559
9 | 2650322.7429 | 1224991.2957 | 2650309.0404 | 1224996.1496 | 2650302.4359 | 1224998.0336
10 | 2650349.8796 | 1225023.1559 | 2650356.1078 | 1225019.9955 | 2650365.3189 | 1225019.1061 | 2650383.9762 | 1225032.55 | 2650377.8563 | 1225038.1462
11 | 2650289.0155 | 1225001.8618 | 2650302.4359 | 1224998.0336
12 | 2650177.1474 | 1225072.8066 | 2650190.017 | 1225059.8027
13 | 2650177.1474 | 1225072.8066 | 2650198.7576 | 1225092.8278
14 | 2650177.1474 | 1225072.8066 | 2650157.117 | 1225094.291
15 | 2650190.017 | 1225059.8027 | 2650204.4541 | 1225045.215
16 | 2650200.0606 | 1225094.035 | 2650198.7576 | 1225092.8278
17 | 2650157.117 | 1225094.291 | 2650148.2868 | 1225103.7623
18 | 2650377.8563 | 1225038.1462 | 2650365.9383 | 1225026.5382 | 2650360.1046 | 1225025.188 | 2650354.2996 | 1225027.6182 | 2650341.0838 | 1225038.5799 | 2650335.1386 | 1225043.5675
19 | 2650377.8563 | 1225038.1462 | 2650401.3493 | 1225065.2455
20 | 2650289.0155 | 1225001.8618 | 2650264.2039 | 1225007.9339 | 2650253.9772 | 1225011.6406
21 | 2650289.0155 | 1225001.8618 | 2650293.0606 | 1225014.7652
22 | 2650278.7 | 1225096.6889 | 2650324.9223 | 1225153.4794
23 | 2650267.3953 | 1225109.4014 | 2650278.7 | 1225096.6889
24 | 2650267.3953 | 1225109.4014 | 2650267.0024 | 1225102.9607
25 | 2650306.0725 | 1225061.0563 | 2650294.4235 | 1225070.6389 | 2650291.1248 | 1225073.3938
26 | 2650291.1248 | 1225073.3938 | 2650283.2077 | 1225080.0056 | 2650277.2414 | 1225088.0868
27 | 2650267.0024 | 1225102.9607 | 2650269.1169 | 1225099.4431 | 2650275.5234 | 1225090.4138 | 2650277.2414 | 1225088.0868
28 | 2650220.8664 | 1225115.388 | 2650215.4691 | 1225109.3007
29 | 2650295.8334 | 1225025.8726 | 2650296.2113 | 1225030.4291 | 2650293.7439 | 1225037.1235 | 2650288.439 | 1225042.2819 | 2650276.5355 | 1225050.8776
30 | 2650295.8334 | 1225025.8726 | 2650295.5783 | 1225022.7968 | 2650293.0606 | 1225014.7652
31 | 2650243.3861 | 1225075.414 | 2650247.6537 | 1225071.7337 | 2650276.5355 | 1225050.8776
32 | 2650253.9772 | 1225011.6406 | 2650248.2268 | 1225013.7249 | 2650245.7588 | 1225014.9509
33 | 2650210.5392 | 1225103.7405 | 2650200.0606 | 1225094.035
34 | 2650210.5392 | 1225103.7405 | 2650215.4691 | 1225109.3007
35 | 2650200.0606 | 1225094.035 | 2650185.4823 | 1225108.4349
36 | 2650245.7588 | 1225014.9509 | 2650232.9548 | 1225021.3118 | 2650230.3611 | 1225023.0567
37 | 2650172.6617 | 1225121.0987 | 2650185.4823 | 1225108.4349
38 | 2650142.6083 | 1225109.853 | 2650148.2868 | 1225103.7623
39 | 2650204.4541 | 1225045.215 | 2650207.0159 | 1225042.6265
40 | 2650224.6162 | 1225026.9214 | 2650230.3611 | 1225023.0567
41 | 2650224.6162 | 1225026.9214 | 2650218.4606 | 1225031.0623 | 2650207.0159 | 1225042.6265

## bus_geodata
| x | y | coords
0 | 2650127.79 | 1225125.747
1 | 2650135.355 | 1225117.6329
2 | 2650213.5637 | 1225156.0792
3 | 2650239.1429 | 1225133.3667
4 | 2650311.0941 | 1225190.9874
5 | 2650337.6073 | 1225169.0647
6 | 2650322.7428 | 1224991.2957
7 | 2650349.8796 | 1225023.1559
8 | 2650302.4359 | 1224998.0336
9 | 2650177.1474 | 1225072.8066
10 | 2650190.017 | 1225059.8027
11 | 2650198.7576 | 1225092.8278
12 | 2650157.117 | 1225094.291
13 | 2650377.8563 | 1225038.1462
14 | 2650335.1386 | 1225043.5675
15 | 2650401.3493 | 1225065.2455
16 | 2650289.0155 | 1225001.8618
17 | 2650343.8223 | 1225176.7116
18 | 2650324.9223 | 1225153.4794
19 | 2650278.7 | 1225096.6889
20 | 2650267.3953 | 1225109.4014
21 | 2650306.0725 | 1225061.0563
22 | 2650291.1248 | 1225073.3938
23 | 2650267.0024 | 1225102.9607
24 | 2650220.8664 | 1225115.388
25 | 2650277.2414 | 1225088.0868
26 | 2650295.8334 | 1225025.8726
27 | 2650276.5355 | 1225050.8776
28 | 2650293.0606 | 1225014.7652
29 | 2650243.3861 | 1225075.414
30 | 2650253.9772 | 1225011.6406
31 | 2650210.5392 | 1225103.7405
32 | 2650200.0606 | 1225094.035
33 | 2650215.4691 | 1225109.3007
34 | 2650245.7588 | 1225014.9509
35 | 2650185.4823 | 1225108.4349
36 | 2650172.6617 | 1225121.0987
37 | 2650142.6083 | 1225109.853
38 | 2650148.2868 | 1225103.7623
39 | 2650204.4541 | 1225045.215
40 | 2650230.3611 | 1225023.0567
41 | 2650224.6162 | 1225026.9214
42 | 2650207.0159 | 1225042.6265
43 | 2650267.3953 | 1225109.4014

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98809 | -0.22754 | 0.0033504 | 0.0008397
1 | 0.98813 | -0.22688 | 0.0024593 | 0.00061636
2 | 0.99497 | -0.09554 | 0.0074725 | 0.0018728
3 | 0.9952 | -0.09104 | 0 | 0
4 | 0.99655 | -0.066327 | 0.014608 | 0.0036612
5 | 0.99701 | -0.05751 | 0 | 0
6 | 0.98084 | -0.36829 | 0 | 0
7 | 0.97944 | -0.39551 | 0 | 0
8 | 0.98146 | -0.3561 | 0.00063719 | 0.0001597
9 | 0.98871 | -0.21565 | 0 | 0
10 | 0.98765 | -0.23603 | 0.0010547 | 0.00026435
11 | 0.99074 | -0.17647 | 0.0044639 | 0.0011188
12 | 0.98837 | -0.22209 | 0.001709 | 0.00042831
13 | 0.97806 | -0.4227 | 0 | 0
14 | 0.97657 | -0.45186 | 0.029674 | 0.0074371
15 | 0.978 | -0.42386 | 0.0017723 | 0.00044419
16 | 0.98188 | -0.348 | 0 | 0
17 | 0.99695 | -0.05863 | 0.0064796 | 0.0016239
18 | 0.99739 | -0.050082 | 0.018048 | 0.0045233
19 | 1 | 0 | -0.14584 | -0.036729
20 | 0.99838 | -0.030709 | 0 | 0
21 | 0.99806 | -0.036894 | 0.0020846 | 0.00052245
22 | 0.99809 | -0.036187 | 0.0029168 | 0.00073101
23 | 0.99832 | -0.031898 | 0.0026053 | 0.00065295
24 | 0.99318 | -0.12972 | 0.0010659 | 0.00026715
25 | 0.99819 | -0.034405 | 0.0029298 | 0.00073428
26 | 0.98157 | -0.35409 | 0.002475 | 0.0006203
27 | 0.98127 | -0.35985 | 0.0047591 | 0.0011927
28 | 0.98169 | -0.35162 | 0.0029136 | 0.00073021
29 | 0.98109 | -0.36332 | 0.0046491 | 0.0011652
30 | 0.98346 | -0.31717 | 0.0030957 | 0.00077586
31 | 0.99197 | -0.15286 | 0 | 0
32 | 0.99087 | -0.17398 | 0 | 0
33 | 0.99254 | -0.14187 | 0.00092357 | 0.00023147
34 | 0.98387 | -0.30919 | 0.0016695 | 0.00041842
35 | 0.99079 | -0.17555 | 0.0024564 | 0.00061562
36 | 0.99076 | -0.17614 | 0.0018635 | 0.00046705
37 | 0.98818 | -0.22578 | 0.0024888 | 0.00062374
38 | 0.98825 | -0.22454 | 0.002297 | 0.00057568
39 | 0.98648 | -0.25856 | 0.0035598 | 0.00089217
40 | 0.9847 | -0.29299 | 0.0018672 | 0.00046796
41 | 0.98505 | -0.28633 | 0.002947 | 0.00073859
42 | 0.98629 | -0.26233 | 0.0013351 | 0.00033461
43 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0033504 | -0.0008397 | 0.0033505 | 0.00083963 | 1.0591e-07 | -7.432e-08 | 0.0050456 | 0.0050455 | 0.0050456 | 0.98809 | -0.22754 | 0.98813 | -0.22688 | 1.3861
1 | -0.0058098 | -0.001456 | 0.0058101 | 0.001456 | 3.0531e-07 | 5.9141e-08 | 0.008749 | 0.0087489 | 0.008749 | 0.98813 | -0.22688 | 0.98818 | -0.22578 | 2.4036
2 | -0.0074725 | -0.0018728 | 0.0074741 | 0.0018734 | 1.602e-06 | 5.8093e-07 | 0.011175 | 0.011175 | 0.011175 | 0.99497 | -0.09554 | 0.9952 | -0.09104 | 3.0702
3 | 0.086499 | 0.022064 | -0.086337 | -0.021961 | 0.00016126 | 0.00010287 | 0.12947 | 0.12947 | 0.12947 | 0.9952 | -0.09104 | 0.99318 | -0.12972 | 35.5683
4 | -0.093973 | -0.023937 | 0.094247 | 0.024112 | 0.00027437 | 0.00017511 | 0.14064 | 0.14064 | 0.14064 | 0.9952 | -0.09104 | 0.99838 | -0.030709 | 38.6384
5 | -0.014608 | -0.0036612 | 0.014614 | 0.0036647 | 6.1382e-06 | 3.48e-06 | 0.021813 | 0.021812 | 0.021813 | 0.99655 | -0.066327 | 0.99701 | -0.05751 | 5.9925
6 | -0.021094 | -0.0052887 | 0.021102 | 0.0052932 | 7.4695e-06 | 4.5183e-06 | 0.031484 | 0.031484 | 0.031484 | 0.99701 | -0.05751 | 0.99739 | -0.050082 | 8.6494
7 | 0.0064799 | 0.001624 | -0.0064796 | -0.0016239 | 3.4563e-07 | 9.2703e-08 | 0.0096712 | 0.0096712 | 0.0096712 | 0.99701 | -0.05751 | 0.99695 | -0.05863 | 2.6569
8 | 0.03157 | 0.0079579 | -0.031529 | -0.0079322 | 4.1057e-05 | 2.5675e-05 | 0.047911 | 0.047911 | 0.047911 | 0.98084 | -0.36829 | 0.97944 | -0.39551 | 13.1624
9 | -0.03157 | -0.0079579 | 0.031589 | 0.0079694 | 1.8425e-05 | 1.1522e-05 | 0.047911 | 0.047911 | 0.047911 | 0.98084 | -0.36829 | 0.98146 | -0.3561 | 13.1624
10 | 0.031529 | 0.0079322 | -0.031488 | -0.0079067 | 4.0912e-05 | 2.5586e-05 | 0.047911 | 0.047911 | 0.047911 | 0.97944 | -0.39551 | 0.97806 | -0.4227 | 13.1625
11 | -0.032226 | -0.0081291 | 0.032238 | 0.008137 | 1.2502e-05 | 7.8251e-06 | 0.048877 | 0.048877 | 0.048877 | 0.98146 | -0.3561 | 0.98188 | -0.348 | 13.4278
12 | 0.062922 | 0.015963 | -0.06286 | -0.015924 | 6.1617e-05 | 3.92e-05 | 0.094768 | 0.094768 | 0.094768 | 0.98871 | -0.21565 | 0.98765 | -0.23603 | 26.0351
13 | -0.075232 | -0.01905 | 0.075374 | 0.01914 | 0.0001418 | 9.0373e-05 | 0.1133 | 0.1133 | 0.1133 | 0.98871 | -0.21565 | 0.99074 | -0.17647 | 31.1251
14 | 0.01231 | 0.0030866 | -0.012307 | -0.0030846 | 3.7812e-06 | 2.0434e-06 | 0.018528 | 0.018528 | 0.018528 | 0.98871 | -0.21565 | 0.98837 | -0.22209 | 5.0901
15 | 0.061806 | 0.01566 | -0.061739 | -0.015617 | 6.6823e-05 | 4.2504e-05 | 0.093179 | 0.093179 | 0.093179 | 0.98765 | -0.23603 | 0.98648 | -0.25856 | 25.5985
16 | -0.079838 | -0.020259 | 0.079848 | 0.020265 | 9.592e-06 | 6.116e-06 | 0.12 | 0.12 | 0.12 | 0.99074 | -0.17647 | 0.99087 | -0.17398 | 32.9669
17 | 0.010598 | 0.0026563 | -0.010596 | -0.0026557 | 1.2361e-06 | 6.2519e-07 | 0.015955 | 0.015955 | 0.015955 | 0.98837 | -0.22209 | 0.98825 | -0.22454 | 4.3833
18 | 0.029716 | 0.0074629 | -0.029674 | -0.0074371 | 4.1283e-05 | 2.5746e-05 | 0.045215 | 0.045215 | 0.045215 | 0.97806 | -0.4227 | 0.97657 | -0.45186 | 12.4218
19 | 0.0017724 | 0.0004438 | -0.0017723 | -0.00044419 | 9.7791e-08 | -3.8748e-07 | 0.0026964 | 0.0026966 | 0.0026966 | 0.97806 | -0.4227 | 0.978 | -0.42386 | 0.74082
20 | -0.047042 | -0.011849 | 0.047112 | 0.011893 | 6.9459e-05 | 4.3992e-05 | 0.071313 | 0.071313 | 0.071313 | 0.98188 | -0.348 | 0.98346 | -0.31717 | 19.5915
21 | 0.014804 | 0.0037119 | -0.014802 | -0.0037104 | 2.5526e-06 | 1.4627e-06 | 0.022436 | 0.022436 | 0.022436 | 0.98188 | -0.348 | 0.98169 | -0.35162 | 6.1638
22 | -0.03915 | -0.0098165 | 0.039244 | 0.0098755 | 9.3681e-05 | 5.8998e-05 | 0.05841 | 0.05841 | 0.05841 | 0.99739 | -0.050082 | 1 | 0 | 16.0467
23 | 0.10494 | 0.026853 | -0.10479 | -0.026754 | 0.00015577 | 9.9468e-05 | 0.15635 | 0.15635 | 0.15635 | 1 | 0 | 0.99838 | -0.030709 | 42.9534
24 | 0.010539 | 0.0026412 | -0.010538 | -0.0026409 | 5.9697e-07 | 2.9769e-07 | 0.015707 | 0.015707 | 0.015707 | 0.99838 | -0.030709 | 0.99832 | -0.031898 | 4.3151
25 | -0.0020846 | -0.00052245 | 0.0020847 | 0.00052225 | 7.0205e-08 | -2.0837e-07 | 0.003108 | 0.0031079 | 0.003108 | 0.99806 | -0.036894 | 0.99809 | -0.036187 | 0.85384
26 | -0.0050015 | -0.0012533 | 0.0050019 | 0.0012533 | 4.2448e-07 | 5.5533e-09 | 0.0074564 | 0.0074563 | 0.0074564 | 0.99809 | -0.036187 | 0.99819 | -0.034405 | 2.0485
27 | 0.0079327 | 0.0019879 | -0.0079317 | -0.0019875 | 9.4723e-07 | 3.7002e-07 | 0.011824 | 0.011824 | 0.011824 | 0.99832 | -0.031898 | 0.99819 | -0.034405 | 3.2483
28 | 0.085271 | 0.021694 | -0.085222 | -0.021662 | 4.9884e-05 | 3.1821e-05 | 0.12787 | 0.12787 | 0.12787 | 0.99318 | -0.12972 | 0.99254 | -0.14187 | 35.1296
29 | 0.0094116 | 0.0023591 | -0.009409 | -0.0023579 | 2.5794e-06 | 1.2239e-06 | 0.014268 | 0.014268 | 0.014268 | 0.98157 | -0.35409 | 0.98127 | -0.35985 | 3.9198
30 | -0.011887 | -0.0029794 | 0.011888 | 0.0029802 | 1.4007e-06 | 7.5105e-07 | 0.01802 | 0.01802 | 0.01802 | 0.98157 | -0.35409 | 0.98169 | -0.35162 | 4.9505
31 | 0.0046499 | 0.0011652 | -0.0046491 | -0.0011652 | 7.6929e-07 | -2.8778e-08 | 0.0070511 | 0.0070513 | 0.0070513 | 0.98127 | -0.35985 | 0.98109 | -0.36332 | 1.9372
32 | -0.050208 | -0.012669 | 0.050227 | 0.012681 | 1.9216e-05 | 1.2185e-05 | 0.075997 | 0.075997 | 0.075997 | 0.98346 | -0.31717 | 0.98387 | -0.30919 | 20.8782
33 | 0.084253 | 0.021402 | -0.084168 | -0.021348 | 8.5561e-05 | 5.4575e-05 | 0.12649 | 0.12649 | 0.12649 | 0.99197 | -0.15286 | 0.99087 | -0.17398 | 34.7492
34 | -0.084253 | -0.021402 | 0.084298 | 0.021431 | 4.4583e-05 | 2.8437e-05 | 0.12649 | 0.12649 | 0.12649 | 0.99197 | -0.15286 | 0.99254 | -0.14187 | 34.7492
35 | 0.0043203 | 0.0010824 | -0.00432 | -0.0010825 | 3.2344e-07 | -5.692e-08 | 0.0064878 | 0.0064878 | 0.0064878 | 0.99087 | -0.17398 | 0.99079 | -0.17555 | 1.7824
36 | -0.051896 | -0.013099 | 0.051937 | 0.013125 | 4.0284e-05 | 2.556e-05 | 0.078522 | 0.078522 | 0.078522 | 0.98387 | -0.30919 | 0.9847 | -0.29299 | 21.5719
37 | 0.0018636 | 0.00046685 | -0.0018635 | -0.00046705 | 5.2935e-08 | -1.982e-07 | 0.0027988 | 0.0027988 | 0.0027988 | 0.99079 | -0.17555 | 0.99076 | -0.17614 | 0.76891
38 | -0.0082989 | -0.0020798 | 0.0082994 | 0.00208 | 4.8765e-07 | 2.0541e-07 | 0.012497 | 0.012496 | 0.012497 | 0.98818 | -0.22578 | 0.98825 | -0.22454 | 3.4331
39 | 0.058179 | 0.014725 | -0.058168 | -0.014718 | 1.053e-05 | 6.6928e-06 | 0.087809 | 0.087809 | 0.087809 | 0.98648 | -0.25856 | 0.98629 | -0.26233 | 24.1234
40 | -0.053804 | -0.013593 | 0.053821 | 0.013604 | 1.718e-05 | 1.0907e-05 | 0.081343 | 0.081343 | 0.081343 | 0.9847 | -0.29299 | 0.98505 | -0.28633 | 22.347
41 | -0.056768 | -0.014342 | 0.056833 | 0.014384 | 6.5388e-05 | 4.1546e-05 | 0.085795 | 0.085795 | 0.085795 | 0.98505 | -0.28633 | 0.98629 | -0.26233 | 23.57

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.14584 | 0.036729

## res_load
| p_mw | q_mvar
0 | 0.0033504 | 0.0008397
1 | 0.0024593 | 0.00061636
2 | 0.0074725 | 0.0018728
3 | 0.014608 | 0.0036612
4 | 0.00063719 | 0.0001597
5 | 0.0010547 | 0.00026435
6 | 0.0044639 | 0.0011188
7 | 0.001709 | 0.00042831
8 | 0.029674 | 0.0074371
9 | 0.0017723 | 0.00044419
10 | 0.0064796 | 0.0016239
11 | 0.018048 | 0.0045233
12 | 0.0020846 | 0.00052245
13 | 0.0029168 | 0.00073101
14 | 0.0026053 | 0.00065295
15 | 0.0010659 | 0.00026715
16 | 0.0029298 | 0.00073428
17 | 0.002475 | 0.0006203
18 | 0.0047591 | 0.0011927
19 | 0.0029136 | 0.00073021
20 | 0.0046491 | 0.0011652
21 | 0.0030957 | 0.00077586
22 | 0.00092357 | 0.00023147
23 | 0.0016695 | 0.00041842
24 | 0.0024564 | 0.00061562
25 | 0.0018635 | 0.00046705
26 | 0.0024888 | 0.00062374
27 | 0.002297 | 0.00057568
28 | 0.0035598 | 0.00089217
29 | 0.0018672 | 0.00046796
30 | 0.002947 | 0.00073859
31 | 0.0013351 | 0.00033461

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1