## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_113-10_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_113-10_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_113-10_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_113-10_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_113-10_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_113-10_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_113-10_0_4_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_113-10_0_4_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_113-10_0_4_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_113-10_0_4_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_113-10_0_4_node_10 | 0.4 | n |  | TRUE
11 | bus_LV_113-10_0_4_node_13 | 0.4 | n |  | TRUE
12 | bus_LV_113-10_0_4_node_14 | 0.4 | n |  | TRUE
13 | bus_LV_113-10_0_4_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_113-10_0_4_node_12 | 0.4 | n |  | TRUE
15 | bus_LV_113-10_0_4_node_15 | 0.4 | n |  | TRUE
16 | bus_LV_113-10_0_4_node_16 | 0.4 | n |  | TRUE
17 | bus_LV_113-10_0_4_node_116 | 0.4 | n |  | TRUE
18 | bus_LV_113-10_0_4_node_122 | 0.4 | n |  | TRUE
19 | bus_LV_113-10_0_4_node_114 | 0.4 | n |  | TRUE
20 | bus_LV_113-10_0_4_node_34 | 0.4 | n |  | TRUE
21 | bus_LV_113-10_0_4_node_35 | 0.4 | n |  | TRUE
22 | bus_LV_113-10_0_4_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_113-10_0_4_node_19 | 0.4 | n |  | TRUE
24 | bus_LV_113-10_0_4_node_21 | 0.4 | n |  | TRUE
25 | bus_LV_113-10_0_4_node_23 | 0.4 | n |  | TRUE
26 | bus_LV_113-10_0_4_node_24 | 0.4 | n |  | TRUE
27 | bus_LV_113-10_0_4_node_22 | 0.4 | n |  | TRUE
28 | bus_LV_113-10_0_4_node_25 | 0.4 | n |  | TRUE
29 | bus_LV_113-10_0_4_node_26 | 0.4 | n |  | TRUE
30 | bus_LV_113-10_0_4_node_50 | 0.4 | n |  | TRUE
31 | bus_LV_113-10_0_4_node_47 | 0.4 | n |  | TRUE
32 | bus_LV_113-10_0_4_node_53 | 0.4 | n |  | TRUE
33 | bus_LV_113-10_0_4_node_56 | 0.4 | n |  | TRUE
34 | bus_LV_113-10_0_4_node_41 | 0.4 | n |  | TRUE
35 | bus_LV_113-10_0_4_node_51 | 0.4 | n |  | TRUE
36 | bus_LV_113-10_0_4_node_48 | 0.4 | n |  | TRUE
37 | bus_LV_113-10_0_4_node_52 | 0.4 | n |  | TRUE
38 | bus_LV_113-10_0_4_node_55 | 0.4 | n |  | TRUE
39 | bus_LV_113-10_0_4_node_36 | 0.4 | n |  | TRUE
40 | bus_LV_113-10_0_4_node_27 | 0.4 | n |  | TRUE
41 | bus_LV_113-10_0_4_node_28 | 0.4 | n |  | TRUE
42 | bus_LV_113-10_0_4_node_29 | 0.4 | n |  | TRUE
43 | bus_LV_113-10_0_4_node_30 | 0.4 | n |  | TRUE
44 | bus_LV_113-10_0_4_node_31 | 0.4 | n |  | TRUE
45 | bus_LV_113-10_0_4_node_32 | 0.4 | n |  | TRUE
46 | bus_LV_113-10_0_4_node_33 | 0.4 | n |  | TRUE
47 | bus_LV_113-10_0_4_node_54 | 0.4 | n |  | TRUE
48 | bus_LV_113-10_0_4_node_38 | 0.4 | n |  | TRUE
49 | bus_LV_113-10_0_4_node_69 | 0.4 | n |  | TRUE
50 | bus_LV_113-10_0_4_node_39 | 0.4 | n |  | TRUE
51 | bus_LV_113-10_0_4_node_40 | 0.4 | n |  | TRUE
52 | bus_LV_113-10_0_4_node_42 | 0.4 | n |  | TRUE
53 | bus_LV_113-10_0_4_node_43 | 0.4 | n |  | TRUE
54 | bus_LV_113-10_0_4_node_45 | 0.4 | n |  | TRUE
55 | bus_LV_113-10_0_4_node_46 | 0.4 | n |  | TRUE
56 | bus_LV_113-10_0_4_node_49 | 0.4 | n |  | TRUE
57 | bus_LV_113-10_0_4_node_65 | 0.4 | n |  | TRUE
58 | bus_LV_113-10_0_4_node_64 | 0.4 | n |  | TRUE
59 | bus_LV_113-10_0_4_node_57 | 0.4 | n |  | TRUE
60 | bus_LV_113-10_0_4_node_58 | 0.4 | n |  | TRUE
61 | bus_LV_113-10_0_4_node_59 | 0.4 | n |  | TRUE
62 | bus_LV_113-10_0_4_node_60 | 0.4 | n |  | TRUE
63 | bus_LV_113-10_0_4_node_61 | 0.4 | n |  | TRUE
64 | bus_LV_113-10_0_4_node_62 | 0.4 | n |  | TRUE
65 | bus_LV_113-10_0_4_node_63 | 0.4 | n |  | TRUE
66 | bus_LV_113-10_0_4_node_109 | 0.4 | n |  | TRUE
67 | bus_LV_113-10_0_4_node_66 | 0.4 | n |  | TRUE
68 | bus_LV_113-10_0_4_node_108 | 0.4 | n |  | TRUE
69 | bus_LV_113-10_0_4_node_67 | 0.4 | n |  | TRUE
70 | bus_LV_113-10_0_4_node_68 | 0.4 | n |  | TRUE
71 | bus_LV_113-10_0_4_node_99 | 0.4 | n |  | TRUE
72 | bus_LV_113-10_0_4_node_100 | 0.4 | n |  | TRUE
73 | bus_LV_113-10_0_4_node_70 | 0.4 | n |  | TRUE
74 | bus_LV_113-10_0_4_node_71 | 0.4 | n |  | TRUE
75 | bus_LV_113-10_0_4_node_72 | 0.4 | n |  | TRUE
76 | bus_LV_113-10_0_4_node_73 | 0.4 | n |  | TRUE
77 | bus_LV_113-10_0_4_node_74 | 0.4 | n |  | TRUE
78 | bus_LV_113-10_0_4_node_75 | 0.4 | n |  | TRUE
79 | bus_LV_113-10_0_4_node_76 | 0.4 | n |  | TRUE
80 | bus_LV_113-10_0_4_node_86 | 0.4 | n |  | TRUE
81 | bus_LV_113-10_0_4_node_110 | 0.4 | n |  | TRUE
82 | bus_LV_113-10_0_4_node_85 | 0.4 | n |  | TRUE
83 | bus_LV_113-10_0_4_node_111 | 0.4 | n |  | TRUE
84 | bus_LV_113-10_0_4_node_112 | 0.4 | n |  | TRUE
85 | bus_LV_113-10_0_4_node_77 | 0.4 | n |  | TRUE
86 | bus_LV_113-10_0_4_node_78 | 0.4 | n |  | TRUE
87 | bus_LV_113-10_0_4_node_79 | 0.4 | n |  | TRUE
88 | bus_LV_113-10_0_4_node_80 | 0.4 | n |  | TRUE
89 | bus_LV_113-10_0_4_node_81 | 0.4 | n |  | TRUE
90 | bus_LV_113-10_0_4_node_82 | 0.4 | n |  | TRUE
91 | bus_LV_113-10_0_4_node_84 | 0.4 | n |  | TRUE
92 | bus_LV_113-10_0_4_node_83 | 0.4 | n |  | TRUE
93 | bus_LV_113-10_0_4_node_106 | 0.4 | n |  | TRUE
94 | bus_LV_113-10_0_4_node_101 | 0.4 | n |  | TRUE
95 | bus_LV_113-10_0_4_node_105 | 0.4 | n |  | TRUE
96 | bus_LV_113-10_0_4_node_88 | 0.4 | n |  | TRUE
97 | bus_LV_113-10_0_4_node_89 | 0.4 | n |  | TRUE
98 | bus_LV_113-10_0_4_node_119 | 0.4 | n |  | TRUE
99 | bus_LV_113-10_0_4_node_90 | 0.4 | n |  | TRUE
100 | bus_LV_113-10_0_4_node_118 | 0.4 | n |  | TRUE
101 | bus_LV_113-10_0_4_node_91 | 0.4 | n |  | TRUE
102 | bus_LV_113-10_0_4_node_92 | 0.4 | n |  | TRUE
103 | bus_LV_113-10_0_4_node_93 | 0.4 | n |  | TRUE
104 | bus_LV_113-10_0_4_node_94 | 0.4 | n |  | TRUE
105 | bus_LV_113-10_0_4_node_95 | 0.4 | n |  | TRUE
106 | bus_LV_113-10_0_4_node_96 | 0.4 | n |  | TRUE
107 | bus_LV_113-10_0_4_node_97 | 0.4 | n |  | TRUE
108 | bus_LV_113-10_0_4_node_98 | 0.4 | n |  | TRUE
109 | bus_LV_113-10_0_4_node_107 | 0.4 | n |  | TRUE
110 | bus_LV_113-10_0_4_node_102 | 0.4 | n |  | TRUE
111 | bus_LV_113-10_0_4_node_103 | 0.4 | n |  | TRUE
112 | bus_LV_113-10_0_4_node_104 | 0.4 | n |  | TRUE
113 | bus_LV_113-10_0_4_node_117 | 0.4 | n |  | TRUE
114 | bus_LV_113-10_0_4_node_113 | 0.4 | n |  | TRUE
115 | bus_LV_113-10_0_4_node_121 | 0.4 | n |  | TRUE
116 | bus_LV_113-10_0_4_node_115 | 0.4 | n |  | TRUE
117 | bus_LV_113-10_0_4_node_120 | 0.4 | n |  | TRUE
118 | bus_MV_9_2_node_19 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_113-10_0_4_load_0 | 0 | 0.0039452 | 0.00098876 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_113-10_0_4_load_3 | 3 | 0.0036102 | 0.00090481 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_113-10_0_4_load_4 | 4 | 0.0036061 | 0.00090378 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_113-10_0_4_load_8 | 8 | 0.0039774 | 0.00099682 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_113-10_0_4_load_9 | 9 | 0.0029257 | 0.00073326 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_113-10_0_4_load_10 | 10 | 0.0034792 | 0.00087197 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_113-10_0_4_load_14 | 12 | 0.0024027 | 0.00060217 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_113-10_0_4_load_11 | 13 | 0.0044325 | 0.0011109 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_113-10_0_4_load_12 | 14 | 0.0049419 | 0.0012385 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_113-10_0_4_load_15 | 15 | 0.0054035 | 0.0013542 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_113-10_0_4_load_16 | 16 | 0.0023893 | 0.00059881 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_113-10_0_4_load_116 | 17 | 0.0035924 | 0.00090034 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_113-10_0_4_load_122 | 18 | 0.0054346 | 0.001362 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_113-10_0_4_load_34 | 20 | 0.0029591 | 0.00074162 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_113-10_0_4_load_35 | 21 | 0.002227 | 0.00055815 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_113-10_0_4_load_18 | 22 | 0.016789 | 0.0042077 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_113-10_0_4_load_19 | 23 | 0.0097474 | 0.0024429 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_113-10_0_4_load_23 | 25 | 0.0059748 | 0.0014974 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_113-10_0_4_load_24 | 26 | 0.0052468 | 0.001315 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_113-10_0_4_load_26 | 29 | 0.0021308 | 0.00053404 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_113-10_0_4_load_50 | 30 | 0.012015 | 0.0030113 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_113-10_0_4_load_47 | 31 | 0.010445 | 0.0026178 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_113-10_0_4_load_53 | 32 | 0.0017371 | 0.00043535 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_113-10_0_4_load_56 | 33 | 0.001693 | 0.00042431 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_113-10_0_4_load_41 | 34 | 0.0020338 | 0.00050972 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_113-10_0_4_load_51 | 35 | 0.00081003 | 0.00020301 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_113-10_0_4_load_48 | 36 | 0.010193 | 0.0025546 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_113-10_0_4_load_52 | 37 | 0.00075398 | 0.00018897 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_113-10_0_4_load_55 | 38 | 0.00049877 | 0.000125 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_113-10_0_4_load_27 | 40 | 0.0017816 | 0.00044652 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_113-10_0_4_load_28 | 41 | 0.00061202 | 0.00015339 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_113-10_0_4_load_30 | 43 | 0.0019716 | 0.00049412 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_113-10_0_4_load_31 | 44 | 0.00046705 | 0.00011705 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_113-10_0_4_load_33 | 46 | 0.00037843 | 9.4844e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_113-10_0_4_load_54 | 47 | 0.002796 | 0.00070075 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_113-10_0_4_load_38 | 48 | 0.00037562 | 9.414e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_113-10_0_4_load_69 | 49 | 0.0042045 | 0.0010537 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_113-10_0_4_load_39 | 50 | 0.00046459 | 0.00011644 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_113-10_0_4_load_40 | 51 | 0.0016314 | 0.00040887 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_113-10_0_4_load_42 | 52 | 0.0018603 | 0.00046623 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_113-10_0_4_load_43 | 53 | 0.003144 | 0.00078797 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_113-10_0_4_load_45 | 54 | 0.0018763 | 0.00047024 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_113-10_0_4_load_46 | 55 | 0.0020419 | 0.00051175 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_113-10_0_4_load_49 | 56 | 0.0074678 | 0.0018716 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_113-10_0_4_load_65 | 57 | 0.025277 | 0.006335 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_113-10_0_4_load_64 | 58 | 0.005361 | 0.0013436 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_113-10_0_4_load_57 | 59 | 0.0037247 | 0.00093349 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_113-10_0_4_load_58 | 60 | 0.0017171 | 0.00043036 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_113-10_0_4_load_59 | 61 | 0.0056734 | 0.0014219 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_113-10_0_4_load_61 | 63 | 0.01346 | 0.0033734 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_113-10_0_4_load_63 | 65 | 0.0073284 | 0.0018367 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_113-10_0_4_load_109 | 66 | 0.0017228 | 0.00043177 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_113-10_0_4_load_108 | 68 | 0.0026906 | 0.00067432 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_113-10_0_4_load_67 | 69 | 0.003477 | 0.00087142 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_113-10_0_4_load_68 | 70 | 0.0023639 | 0.00059245 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_113-10_0_4_load_99 | 71 | 0.0051602 | 0.0012933 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_113-10_0_4_load_100 | 72 | 0.0019992 | 0.00050105 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_113-10_0_4_load_70 | 73 | 0.0049284 | 0.0012352 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_113-10_0_4_load_71 | 74 | 0.0019717 | 0.00049415 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_113-10_0_4_load_72 | 75 | 0.0027781 | 0.00069626 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_113-10_0_4_load_73 | 76 | 0.0014896 | 0.00037333 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_113-10_0_4_load_74 | 77 | 0.0014706 | 0.00036857 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_113-10_0_4_load_75 | 78 | 0.0022433 | 0.00056223 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_113-10_0_4_load_76 | 79 | 0.0035171 | 0.00088146 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_113-10_0_4_load_86 | 80 | 0.00095291 | 0.00023882 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_113-10_0_4_load_85 | 82 | 0.0080813 | 0.0020254 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_113-10_0_4_load_111 | 83 | 0.0039393 | 0.00098729 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_113-10_0_4_load_112 | 84 | 0.0090861 | 0.0022772 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_113-10_0_4_load_77 | 85 | 0.0011779 | 0.00029521 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_113-10_0_4_load_78 | 86 | 0.002747 | 0.00068846 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_113-10_0_4_load_79 | 87 | 0.00089908 | 0.00022533 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_113-10_0_4_load_80 | 88 | 0.0016369 | 0.00041025 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_113-10_0_4_load_82 | 90 | 0.0012918 | 0.00032377 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_113-10_0_4_load_84 | 91 | 0.0019772 | 0.00049552 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_113-10_0_4_load_83 | 92 | 0.0048307 | 0.0012107 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_113-10_0_4_load_106 | 93 | 0.0013743 | 0.00034443 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_113-10_0_4_load_101 | 94 | 0.0043776 | 0.0010971 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_113-10_0_4_load_88 | 96 | 0.00151 | 0.00037845 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_113-10_0_4_load_89 | 97 | 0.0013657 | 0.00034228 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_113-10_0_4_load_119 | 98 | 0.0019043 | 0.00047725 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_113-10_0_4_load_90 | 99 | 0.0011006 | 0.00027584 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_113-10_0_4_load_118 | 100 | 0.0017691 | 0.00044338 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_113-10_0_4_load_91 | 101 | 0.0032679 | 0.00081901 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_113-10_0_4_load_92 | 102 | 0.002967 | 0.0007436 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_113-10_0_4_load_93 | 103 | 0.00055412 | 0.00013888 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_113-10_0_4_load_94 | 104 | 0.000577 | 0.00014461 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_113-10_0_4_load_95 | 105 | 0.00067845 | 0.00017004 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_113-10_0_4_load_96 | 106 | 0.0013371 | 0.0003351 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_113-10_0_4_load_97 | 107 | 0.00059079 | 0.00014807 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_113-10_0_4_load_98 | 108 | 0.0014873 | 0.00037276 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_113-10_0_4_load_107 | 109 | 0.0021842 | 0.00054741 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_113-10_0_4_load_102 | 110 | 0.0041977 | 0.001052 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_113-10_0_4_load_103 | 111 | 0.0021122 | 0.00052938 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_113-10_0_4_load_104 | 112 | 0.0013925 | 0.00034899 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_113-10_0_4_load_117 | 113 | 0.0030437 | 0.00076282 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_113-10_0_4_load_113 | 114 | 0.0031515 | 0.00078985 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_113-10_0_4_load_121 | 115 | 0.0038197 | 0.0009573 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_113-10_0_4_load_115 | 116 | 0.0038316 | 0.00096028 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_113-10_0_4_load_120 | 117 | 0.0040573 | 0.0010169 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 23 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_113-10_0_4_line_0 |  | 0 | 1 | 0.017593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_113-10_0_4_line_1 |  | 0 | 2 | 0.020544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_113-10_0_4_line_2 |  | 1 | 3 | 0.026071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_113-10_0_4_line_3 |  | 1 | 4 | 0.014358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_113-10_0_4_line_4 |  | 2 | 5 | 0.02492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_113-10_0_4_line_5 |  | 3 | 6 | 0.016439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_113-10_0_4_line_6 |  | 4 | 7 | 0.02456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_113-10_0_4_line_7 |  | 5 | 8 | 0.0016271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_113-10_0_4_line_8 |  | 6 | 9 | 0.023652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_113-10_0_4_line_9 |  | 6 | 10 | 0.02329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_113-10_0_4_line_10 |  | 7 | 11 | 0.011581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_113-10_0_4_line_11 |  | 7 | 12 | 0.0034085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_113-10_0_4_line_12 |  | 9 | 13 | 0.017652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_113-10_0_4_line_13 |  | 10 | 14 | 0.016153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_113-10_0_4_line_14 |  | 11 | 15 | 0.015852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_113-10_0_4_line_15 |  | 11 | 16 | 0.036303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_113-10_0_4_line_16 |  | 13 | 17 | 0.0022186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_113-10_0_4_line_17 |  | 14 | 18 | 0.022852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_113-10_0_4_line_18 |  | 16 | 20 | 0.0067039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_113-10_0_4_line_19 |  | 17 | 19 | 0.0087197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_113-10_0_4_line_20 |  | 19 | 114 | 0.012767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_113-10_0_4_line_21 |  | 20 | 21 | 0.031043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_113-10_0_4_line_22 |  | 21 | 39 | 0.013679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
23 | LV_113-10_0_4_line_23 |  | 22 | 23 | 0.024087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_113-10_0_4_line_24 |  | 23 | 24 | 0.041167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
25 | LV_113-10_0_4_line_25 |  | 24 | 25 | 0.01047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_113-10_0_4_line_26 |  | 24 | 26 | 0.010401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_113-10_0_4_line_27 |  | 25 | 30 | 0.011564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_113-10_0_4_line_28 |  | 26 | 31 | 0.0018934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_113-10_0_4_line_29 |  | 27 | 28 | 0.008531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
30 | LV_113-10_0_4_line_30 |  | 27 | 29 | 0.0087093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_113-10_0_4_line_31 |  | 28 | 32 | 0.011483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
32 | LV_113-10_0_4_line_32 |  | 28 | 33 | 0.022834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_113-10_0_4_line_33 |  | 29 | 34 | 0.019207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
34 | LV_113-10_0_4_line_34 |  | 30 | 35 | 0.013754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_113-10_0_4_line_35 |  | 31 | 36 | 0.015728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
36 | LV_113-10_0_4_line_36 |  | 32 | 37 | 0.0059553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
37 | LV_113-10_0_4_line_37 |  | 33 | 38 | 0.014571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_113-10_0_4_line_38 |  | 34 | 39 | 0.0045771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
39 | LV_113-10_0_4_line_39 |  | 35 | 37 | 0.024618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
40 | LV_113-10_0_4_line_40 |  | 36 | 56 | 0.019486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_113-10_0_4_line_41 |  | 38 | 50 | 0.016921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_113-10_0_4_line_42 |  | 39 | 51 | 0.0086104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_113-10_0_4_line_43 |  | 40 | 41 | 0.021092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_113-10_0_4_line_44 |  | 40 | 42 | 0.038707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_113-10_0_4_line_45 |  | 41 | 43 | 0.022751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_113-10_0_4_line_46 |  | 42 | 44 | 0.039396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_113-10_0_4_line_47 |  | 43 | 45 | 0.034446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_113-10_0_4_line_48 |  | 44 | 46 | 0.0021244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_113-10_0_4_line_49 |  | 45 | 47 | 0.03499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_113-10_0_4_line_50 |  | 46 | 48 | 0.016964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_113-10_0_4_line_51 |  | 47 | 49 | 0.011491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_113-10_0_4_line_52 |  | 48 | 50 | 0.00039593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_113-10_0_4_line_53 |  | 49 | 55 | 0.010674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_113-10_0_4_line_54 |  | 51 | 52 | 0.0095282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_113-10_0_4_line_55 |  | 52 | 53 | 0.0093865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_113-10_0_4_line_56 |  | 54 | 55 | 0.0097517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_113-10_0_4_line_57 |  | 56 | 57 | 0.0055248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_113-10_0_4_line_58 |  | 57 | 58 | 0.021247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_113-10_0_4_line_59 |  | 58 | 67 | 0.016962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_113-10_0_4_line_60 |  | 59 | 60 | 0.0064114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_113-10_0_4_line_61 |  | 59 | 61 | 0.023399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_113-10_0_4_line_62 |  | 60 | 62 | 0.026822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_113-10_0_4_line_63 |  | 61 | 63 | 0.012184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_113-10_0_4_line_64 |  | 62 | 64 | 0.023038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_113-10_0_4_line_65 |  | 63 | 65 | 0.019012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_113-10_0_4_line_66 |  | 64 | 66 | 0.012109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_113-10_0_4_line_67 |  | 65 | 67 | 0.015827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_113-10_0_4_line_68 |  | 66 | 68 | 0.021117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_113-10_0_4_line_69 |  | 67 | 69 | 0.013863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_113-10_0_4_line_70 |  | 68 | 109 | 0.0051461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_113-10_0_4_line_71 |  | 69 | 70 | 0.014796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_113-10_0_4_line_72 |  | 70 | 71 | 0.019202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_113-10_0_4_line_73 |  | 71 | 72 | 0.015256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_113-10_0_4_line_74 |  | 72 | 94 | 0.019951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_113-10_0_4_line_75 |  | 73 | 74 | 0.010002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_113-10_0_4_line_76 |  | 73 | 75 | 0.0024448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_113-10_0_4_line_77 |  | 74 | 76 | 0.013772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_113-10_0_4_line_78 |  | 75 | 77 | 0.017896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_113-10_0_4_line_79 |  | 76 | 78 | 0.0083119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_113-10_0_4_line_80 |  | 77 | 79 | 0.0056786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_113-10_0_4_line_81 |  | 78 | 80 | 0.011186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_113-10_0_4_line_82 |  | 79 | 81 | 0.0021259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_113-10_0_4_line_83 |  | 80 | 82 | 0.0059094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_113-10_0_4_line_84 |  | 81 | 83 | 0.0094129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_113-10_0_4_line_85 |  | 81 | 84 | 0.01718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_113-10_0_4_line_86 |  | 83 | 113 | 0.03094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_113-10_0_4_line_87 |  | 84 | 114 | 0.010175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_113-10_0_4_line_88 |  | 85 | 86 | 0.001208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_113-10_0_4_line_89 |  | 85 | 87 | 0.011936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_113-10_0_4_line_90 |  | 86 | 88 | 0.0039241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_113-10_0_4_line_91 |  | 87 | 89 | 0.003459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_113-10_0_4_line_92 |  | 88 | 90 | 0.0205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_113-10_0_4_line_93 |  | 89 | 91 | 0.024575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_113-10_0_4_line_94 |  | 91 | 94 | 0.0055277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_113-10_0_4_line_95 |  | 92 | 93 | 0.023937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_113-10_0_4_line_96 |  | 93 | 95 | 0.0096979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_113-10_0_4_line_97 |  | 95 | 100 | 0.0026386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_113-10_0_4_line_98 |  | 95 | 112 | 0.025622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_113-10_0_4_line_99 |  | 96 | 97 | 0.024115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_113-10_0_4_line_100 |  | 97 | 98 | 0.0018837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_113-10_0_4_line_101 |  | 97 | 99 | 0.07227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_113-10_0_4_line_102 |  | 98 | 100 | 0.020334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_113-10_0_4_line_103 |  | 99 | 101 | 0.058429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_113-10_0_4_line_104 |  | 102 | 103 | 0.00033805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_113-10_0_4_line_105 |  | 102 | 104 | 0.010376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_113-10_0_4_line_106 |  | 103 | 105 | 0.0083118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_113-10_0_4_line_107 |  | 104 | 106 | 0.0088237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_113-10_0_4_line_108 |  | 105 | 107 | 0.0098607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_113-10_0_4_line_109 |  | 106 | 108 | 0.012218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_113-10_0_4_line_110 |  | 107 | 109 | 0.0097286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_113-10_0_4_line_111 |  | 108 | 110 | 0.0033574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_113-10_0_4_line_112 |  | 110 | 111 | 0.011071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_113-10_0_4_line_113 |  | 111 | 112 | 0.014917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_113-10_0_4_line_114 |  | 113 | 115 | 0.017898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_113-10_0_4_line_115 |  | 115 | 117 | 0.017699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_113-10_0_4_line_116 |  | 116 | 117 | 0.01906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_113-10_0_4_trafo_19 | 0.63 MVA 20/0.4 kV | 118 | 23 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2706879.5172 | 1236153.4996 | 2706862.2604 | 1236156.9208
1 | 2706844.5985 | 1236157.4635 | 2706844.9628 | 1236160.3501 | 2706862.2604 | 1236156.9208
2 | 2706879.5172 | 1236153.4996 | 2706882.9119 | 1236156.652 | 2706884.5765 | 1236165.9336 | 2706887.7634 | 1236177.5114
3 | 2706879.5172 | 1236153.4996 | 2706878.5632 | 1236139.1731
4 | 2706844.5985 | 1236157.4635 | 2706843.5181 | 1236150.2052 | 2706826.1324 | 1236153.1392
5 | 2706893.6399 | 1236192.228 | 2706891.4391 | 1236190.8651 | 2706887.7634 | 1236177.5114
6 | 2706876.9314 | 1236114.6677 | 2706878.5632 | 1236139.1731
7 | 2706826.1324 | 1236153.1392 | 2706825.9781 | 1236151.5194
8 | 2706893.6399 | 1236192.228 | 2706874.3562 | 1236198.4303 | 2706871.1916 | 1236199.6612
9 | 2706893.6399 | 1236192.228 | 2706892.4008 | 1236215.4853
10 | 2706888.4482 | 1236113.1626 | 2706876.9314 | 1236114.6677
11 | 2706876.9314 | 1236114.6677 | 2706874.9096 | 1236113.4526 | 2706873.8605 | 1236113.4887
12 | 2706854.7399 | 1236206.0601 | 2706871.1916 | 1236199.6612
13 | 2706891.8328 | 1236231.6279 | 2706892.2336 | 1236218.623 | 2706892.4008 | 1236215.4853
14 | 2706888.4482 | 1236113.1626 | 2706904.2539 | 1236111.9477
15 | 2706888.4482 | 1236113.1626 | 2706887.8204 | 1236102.6321 | 2706888.641 | 1236091.1047 | 2706891.2616 | 1236077.1518
16 | 2706854.7399 | 1236206.0601 | 2706852.6722 | 1236206.8644
17 | 2706891.8328 | 1236231.6279 | 2706891.1288 | 1236254.4688
18 | 2706892.499 | 1236070.5631 | 2706891.2616 | 1236077.1518
19 | 2706844.5456 | 1236210.0252 | 2706852.6722 | 1236206.8644
20 | 2706844.5456 | 1236210.0252 | 2706832.6465 | 1236214.6516
21 | 2706886.226 | 1236046.9346 | 2706886.5977 | 1236057.8757 | 2706894.702 | 1236058.8333 | 2706892.499 | 1236070.5631
22 | 2706885.7616 | 1236033.2639 | 2706886.226 | 1236046.9346
23 | 2706799.5225 | 1236082.74 | 2706799.5225 | 1236082.74 | 2706775.8429 | 1236087.1511
24 | 2706768.5028 | 1236046.6436 | 2706775.8429 | 1236087.1511
25 | 2706768.5028 | 1236046.6436 | 2706778.8119 | 1236044.8145
26 | 2706768.5028 | 1236046.6436 | 2706758.2328 | 1236048.292
27 | 2706778.8119 | 1236044.8145 | 2706790.1982 | 1236042.7943
28 | 2706758.2328 | 1236048.292 | 2706756.3633 | 1236048.592
29 | 2706853.578 | 1236031.5726 | 2706845.1498 | 1236033.0444
30 | 2706853.578 | 1236031.5726 | 2706862.2188 | 1236030.4827 | 2706862.2188 | 1236030.4827
31 | 2706845.1498 | 1236033.0444 | 2706833.8438 | 1236035.0504
32 | 2706845.1498 | 1236033.0444 | 2706841.3841 | 1236010.5234
33 | 2706862.2188 | 1236030.4827 | 2706870.8006 | 1236030.5705 | 2706881.2569 | 1236032.4529
34 | 2706803.7409 | 1236040.3914 | 2706790.1982 | 1236042.7943
35 | 2706740.8344 | 1236051.0844 | 2706756.3633 | 1236048.592
36 | 2706827.9801 | 1236036.0907 | 2706833.8438 | 1236035.0504
37 | 2706838.9811 | 1235996.1523 | 2706841.3841 | 1236010.5234
38 | 2706885.7616 | 1236033.2639 | 2706881.2569 | 1236032.4529
39 | 2706803.7409 | 1236040.3914 | 2706827.9801 | 1236036.0907
40 | 2706740.8344 | 1236051.0844 | 2706721.5949 | 1236054.1724
41 | 2706838.9811 | 1235996.1523 | 2706836.1906 | 1235979.4632
42 | 2706885.7616 | 1236033.2639 | 2706894.2179 | 1236034.8854
43 | 2706885.6711 | 1235912.8963 | 2706884.4448 | 1235913.0144 | 2706864.7894 | 1235915.8543
44 | 2706826.4802 | 1235921.3894 | 2706864.7894 | 1235915.8543
45 | 2706885.6711 | 1235912.8963 | 2706906.6233 | 1235910.8784 | 2706908.3251 | 1235910.9164
46 | 2706826.4802 | 1235921.3894 | 2706832.9772 | 1235960.2456
47 | 2706933.9541 | 1235930.73 | 2706923.5135 | 1235916.1642 | 2706914.3938 | 1235911.0517 | 2706908.3251 | 1235910.9164
48 | 2706833.3276 | 1235962.3409 | 2706832.9772 | 1235960.2456
49 | 2706933.9541 | 1235930.73 | 2706938.263 | 1235965.4541
50 | 2706836.1253 | 1235979.0727 | 2706833.3276 | 1235962.3409
51 | 2706939.6781 | 1235976.8574 | 2706939.6781 | 1235976.8574 | 2706938.263 | 1235965.4541
52 | 2706836.1906 | 1235979.4632 | 2706836.1253 | 1235979.0727
53 | 2706939.6781 | 1235976.8574 | 2706941.538 | 1235987.3678
54 | 2706903.5395 | 1236036.8269 | 2706902.1451 | 1236036.4055 | 2706894.2179 | 1236034.8854
55 | 2706912.5246 | 1236039.5423 | 2706903.5395 | 1236036.8269
56 | 2706941.538 | 1235987.3678 | 2706943.2372 | 1235996.9704
57 | 2706721.5949 | 1236054.1724 | 2706716.1398 | 1236055.0479
58 | 2706695.1609 | 1236058.4151 | 2706716.1398 | 1236055.0479
59 | 2706678.4133 | 1236061.1031 | 2706695.1609 | 1236058.4151
60 | 2706608.9139 | 1236057.7217 | 2706602.6276 | 1236056.4612
61 | 2706608.9139 | 1236057.7217 | 2706631.8563 | 1236062.322
62 | 2706578.0436 | 1236047.836 | 2706581.5699 | 1236051.68 | 2706589.3507 | 1236053.799 | 2706602.6276 | 1236056.4612
63 | 2706643.8638 | 1236064.2494 | 2706640.3942 | 1236064.0339 | 2706631.8563 | 1236062.322
64 | 2706561.6826 | 1236064.0995 | 2706578.0436 | 1236047.836
65 | 2706643.8638 | 1236064.2494 | 2706651.4781 | 1236064.7223 | 2706662.8209 | 1236063.7657
66 | 2706561.6826 | 1236064.0995 | 2706566.7185 | 1236075.1116
67 | 2706678.4133 | 1236061.1031 | 2706664.9563 | 1236063.5856 | 2706662.8209 | 1236063.7657
68 | 2706566.7185 | 1236075.1116 | 2706575.5008 | 1236094.3162
69 | 2706678.4133 | 1236061.1031 | 2706680.6115 | 1236074.7907
70 | 2706577.6409 | 1236098.9962 | 2706575.5008 | 1236094.3162
71 | 2706682.9576 | 1236089.399 | 2706680.6115 | 1236074.7907
72 | 2706686.0024 | 1236108.3582 | 2706682.9576 | 1236089.399
73 | 2706686.0024 | 1236108.3582 | 2706688.4216 | 1236123.4216
74 | 2706688.4216 | 1236123.4216 | 2706691.0952 | 1236140.0693 | 2706691.4964 | 1236143.1332
75 | 2706780.6213 | 1236233.8822 | 2706771.0122 | 1236236.6577
76 | 2706780.6213 | 1236233.8822 | 2706782.97 | 1236233.2038
77 | 2706771.0122 | 1236236.6577 | 2706757.7815 | 1236240.4792
78 | 2706799.8781 | 1236227.3947 | 2706790.6567 | 1236230.9836 | 2706782.97 | 1236233.2038
79 | 2706757.7815 | 1236240.4792 | 2706749.7961 | 1236242.7857
80 | 2706799.8781 | 1236227.3947 | 2706805.17 | 1236225.3351
81 | 2706749.7961 | 1236242.7857 | 2706739.0492 | 1236245.8898 | 2706739.0492 | 1236245.8898
82 | 2706807.1512 | 1236224.564 | 2706805.17 | 1236225.3351
83 | 2706733.1765 | 1236246.547 | 2706739.0492 | 1236245.8898
84 | 2706807.1512 | 1236224.564 | 2706810.2922 | 1236233.4373
85 | 2706807.1512 | 1236224.564 | 2706823.1631 | 1236218.3386
86 | 2706813.1162 | 1236263.9924 | 2706813.1423 | 1236257.9864 | 2706812.4596 | 1236239.5599 | 2706810.2922 | 1236233.4373
87 | 2706823.1631 | 1236218.3386 | 2706832.6465 | 1236214.6516
88 | 2706696.3142 | 1236186.458 | 2706696.5432 | 1236187.644
89 | 2706696.3142 | 1236186.458 | 2706694.0523 | 1236174.738
90 | 2706696.5432 | 1236187.644 | 2706697.2868 | 1236191.4971
91 | 2706691.1182 | 1236172.9061 | 2706694.0523 | 1236174.738
92 | 2706697.2868 | 1236191.4971 | 2706701.1717 | 1236211.6261
93 | 2706691.1182 | 1236172.9061 | 2706692.6234 | 1236168.3296 | 2706692.9637 | 1236161.1858 | 2706692.6393 | 1236151.8617 | 2706692.2141 | 1236148.6141
94 | 2706692.2141 | 1236148.6141 | 2706691.4964 | 1236143.1332
95 | 2706666.6392 | 1236183.9663 | 2706648.0652 | 1236187.2886 | 2706643.2758 | 1236188.9468
96 | 2706636.8174 | 1236195.7376 | 2706641.1344 | 1236189.6883 | 2706643.2758 | 1236188.9468
97 | 2706636.8174 | 1236195.7376 | 2706638.8732 | 1236197.3917
98 | 2706636.8174 | 1236195.7376 | 2706628.6299 | 1236188.4629 | 2706618.7351 | 1236177.6325
99 | 2706678.2448 | 1236221.5668 | 2706675.0314 | 1236219.82 | 2706657.0755 | 1236210.0181
100 | 2706657.0755 | 1236210.0181 | 2706655.422 | 1236209.1155
101 | 2706657.0755 | 1236210.0181 | 2706629.8521 | 1236276.9646
102 | 2706638.8732 | 1236197.3917 | 2706644.1964 | 1236201.6747 | 2706650.6191 | 1236206.4937 | 2706655.422 | 1236209.1155
103 | 2706573.7709 | 1236293.3556 | 2706574.831 | 1236292.9779 | 2706629.8521 | 1236276.9646
104 | 2706589.3851 | 1236124.6775 | 2706589.2445 | 1236124.37
105 | 2706589.3851 | 1236124.6775 | 2706590.0357 | 1236126.1002 | 2706593.7649 | 1236134.0833
106 | 2706585.7878 | 1236116.8111 | 2706589.2445 | 1236124.37
107 | 2706597.4995 | 1236142.0777 | 2706593.7649 | 1236134.0833
108 | 2706585.7878 | 1236116.8111 | 2706581.6869 | 1236107.8436
109 | 2706597.4995 | 1236142.0777 | 2706602.6706 | 1236153.1473
110 | 2706577.6409 | 1236098.9962 | 2706581.6869 | 1236107.8436
111 | 2706604.2566 | 1236156.1041 | 2706603.0899 | 1236154.0448 | 2706602.6706 | 1236153.1473
112 | 2706604.2566 | 1236156.1041 | 2706607.1249 | 1236161.1671 | 2706609.9419 | 1236165.5997
113 | 2706609.9419 | 1236165.5997 | 2706612.3217 | 1236169.3444 | 2706618.7351 | 1236177.6325
114 | 2706813.1162 | 1236263.9924 | 2706813.0771 | 1236272.9634 | 2706821.9955 | 1236272.5687
115 | 2706839.6446 | 1236271.3016 | 2706829.3327 | 1236272.244 | 2706821.9955 | 1236272.5687
116 | 2706839.6446 | 1236271.3016 | 2706846.0039 | 1236270.7204 | 2706850.5081 | 1236268.5775 | 2706850.4639 | 1236260.8914

## bus_geodata
| x | y | coords
0 | 2706862.2604 | 1236156.9208
1 | 2706879.5172 | 1236153.4996
2 | 2706844.5985 | 1236157.4635
3 | 2706887.7634 | 1236177.5114
4 | 2706878.5632 | 1236139.1731
5 | 2706826.1324 | 1236153.1392
6 | 2706893.6399 | 1236192.228
7 | 2706876.9314 | 1236114.6677
8 | 2706825.9781 | 1236151.5194
9 | 2706871.1916 | 1236199.6612
10 | 2706892.4008 | 1236215.4853
11 | 2706888.4482 | 1236113.1626
12 | 2706873.8605 | 1236113.4887
13 | 2706854.7399 | 1236206.0601
14 | 2706891.8328 | 1236231.6279
15 | 2706904.2539 | 1236111.9477
16 | 2706891.2616 | 1236077.1518
17 | 2706852.6722 | 1236206.8644
18 | 2706891.1288 | 1236254.4688
19 | 2706844.5456 | 1236210.0252
20 | 2706892.499 | 1236070.5631
21 | 2706886.226 | 1236046.9346
22 | 2706799.5225 | 1236082.74
23 | 2706775.8429 | 1236087.1511
24 | 2706768.5028 | 1236046.6436
25 | 2706778.8119 | 1236044.8145
26 | 2706758.2328 | 1236048.292
27 | 2706853.578 | 1236031.5726
28 | 2706845.1498 | 1236033.0444
29 | 2706862.2188 | 1236030.4827
30 | 2706790.1982 | 1236042.7943
31 | 2706756.3633 | 1236048.592
32 | 2706833.8438 | 1236035.0504
33 | 2706841.3841 | 1236010.5234
34 | 2706881.2569 | 1236032.4529
35 | 2706803.7409 | 1236040.3914
36 | 2706740.8344 | 1236051.0844
37 | 2706827.9801 | 1236036.0907
38 | 2706838.9811 | 1235996.1523
39 | 2706885.7616 | 1236033.2639
40 | 2706864.7894 | 1235915.8543
41 | 2706885.6711 | 1235912.8963
42 | 2706826.4802 | 1235921.3894
43 | 2706908.3251 | 1235910.9164
44 | 2706832.9772 | 1235960.2456
45 | 2706933.9541 | 1235930.73
46 | 2706833.3276 | 1235962.3409
47 | 2706938.263 | 1235965.4541
48 | 2706836.1253 | 1235979.0727
49 | 2706939.6781 | 1235976.8574
50 | 2706836.1906 | 1235979.4632
51 | 2706894.2179 | 1236034.8854
52 | 2706903.5395 | 1236036.8269
53 | 2706912.5246 | 1236039.5423
54 | 2706943.2372 | 1235996.9704
55 | 2706941.538 | 1235987.3678
56 | 2706721.5949 | 1236054.1724
57 | 2706716.1398 | 1236055.0479
58 | 2706695.1609 | 1236058.4151
59 | 2706608.9139 | 1236057.7217
60 | 2706602.6276 | 1236056.4612
61 | 2706631.8563 | 1236062.3219
62 | 2706578.0436 | 1236047.836
63 | 2706643.8638 | 1236064.2494
64 | 2706561.6826 | 1236064.0995
65 | 2706662.8209 | 1236063.7657
66 | 2706566.7185 | 1236075.1116
67 | 2706678.4133 | 1236061.1031
68 | 2706575.5008 | 1236094.3162
69 | 2706680.6115 | 1236074.7907
70 | 2706682.9576 | 1236089.399
71 | 2706686.0024 | 1236108.3582
72 | 2706688.4216 | 1236123.4216
73 | 2706780.6213 | 1236233.8822
74 | 2706771.0122 | 1236236.6577
75 | 2706782.97 | 1236233.2038
76 | 2706757.7815 | 1236240.4792
77 | 2706799.8781 | 1236227.3947
78 | 2706749.7961 | 1236242.7857
79 | 2706805.17 | 1236225.3351
80 | 2706739.0492 | 1236245.8898
81 | 2706807.1512 | 1236224.564
82 | 2706733.1765 | 1236246.547
83 | 2706810.2922 | 1236233.4373
84 | 2706823.1631 | 1236218.3386
85 | 2706696.3142 | 1236186.458
86 | 2706696.5432 | 1236187.644
87 | 2706694.0523 | 1236174.738
88 | 2706697.2868 | 1236191.4971
89 | 2706691.1182 | 1236172.9061
90 | 2706701.1717 | 1236211.6261
91 | 2706692.2141 | 1236148.6141
92 | 2706666.6392 | 1236183.9663
93 | 2706643.2758 | 1236188.9468
94 | 2706691.4964 | 1236143.1332
95 | 2706636.8174 | 1236195.7376
96 | 2706678.2448 | 1236221.5668
97 | 2706657.0755 | 1236210.0181
98 | 2706655.422 | 1236209.1155
99 | 2706629.8521 | 1236276.9646
100 | 2706638.8732 | 1236197.3917
101 | 2706573.7709 | 1236293.3556
102 | 2706589.3851 | 1236124.6775
103 | 2706589.2445 | 1236124.37
104 | 2706593.7649 | 1236134.0833
105 | 2706585.7878 | 1236116.8111
106 | 2706597.4995 | 1236142.0777
107 | 2706581.6869 | 1236107.8436
108 | 2706602.6706 | 1236153.1473
109 | 2706577.6409 | 1236098.9962
110 | 2706604.2566 | 1236156.1041
111 | 2706609.9419 | 1236165.5997
112 | 2706618.7351 | 1236177.6325
113 | 2706813.1162 | 1236263.9924
114 | 2706832.6465 | 1236214.6516
115 | 2706821.9955 | 1236272.5687
116 | 2706850.4639 | 1236260.8914
117 | 2706839.6446 | 1236271.3016
118 | 2706768.5028 | 1236046.6436

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98011 | -0.38076 | 0.0039452 | 0.00098876
1 | 0.98024 | -0.37823 | 0 | 0
2 | 0.98004 | -0.38225 | 0 | 0
3 | 0.97813 | -0.41937 | 0.0036102 | 0.00090481
4 | 0.98151 | -0.3536 | 0.0036061 | 0.00090378
5 | 0.97995 | -0.38405 | 0 | 0
6 | 0.97686 | -0.44431 | 0 | 0
7 | 0.98376 | -0.31001 | 0 | 0
8 | 0.97994 | -0.38416 | 0.0039774 | 0.00099682
9 | 0.97533 | -0.4743 | 0.0029257 | 0.00073326
10 | 0.97656 | -0.4502 | 0.0034792 | 0.00087197
11 | 0.98485 | -0.28902 | 0 | 0
12 | 0.98375 | -0.31016 | 0.0024027 | 0.00060217
13 | 0.97423 | -0.4958 | 0.0044325 | 0.0011109
14 | 0.9764 | -0.45327 | 0.0049419 | 0.0012385
15 | 0.98477 | -0.29056 | 0.0054035 | 0.0013542
16 | 0.98844 | -0.22004 | 0.0023893 | 0.00059881
17 | 0.97411 | -0.49832 | 0.0035924 | 0.00090034
18 | 0.97629 | -0.45554 | 0.0054346 | 0.001362
19 | 0.97363 | -0.50768 | 0 | 0
20 | 0.98911 | -0.20707 | 0.0029591 | 0.00074162
21 | 0.99019 | -0.18654 | 0.002227 | 0.00055815
22 | 0.99963 | -0.007051 | 0.016789 | 0.0042077
23 | 1 | 0 | -0.35103 | -0.089492
24 | 0.99585 | -0.078687 | 0 | 0
25 | 0.99532 | -0.088812 | 0.0059748 | 0.0014974
26 | 0.99533 | -0.088603 | 0.0052468 | 0.001315
27 | 0.9919 | -0.15376 | 0 | 0
28 | 0.99223 | -0.14749 | 0 | 0
29 | 0.99157 | -0.16017 | 0.0021308 | 0.00053404
30 | 0.99475 | -0.099602 | 0.012015 | 0.0030113
31 | 0.99524 | -0.09035 | 0.010445 | 0.0026178
32 | 0.99274 | -0.13776 | 0.0017371 | 0.00043535
33 | 0.99183 | -0.15525 | 0.001693 | 0.00042431
34 | 0.99084 | -0.17407 | 0.0020338 | 0.00050972
35 | 0.99412 | -0.11148 | 0.00081003 | 0.00020301
36 | 0.99418 | -0.11071 | 0.010193 | 0.0025546
37 | 0.99301 | -0.13266 | 0.00075398 | 0.00018897
38 | 0.9916 | -0.15976 | 0.00049877 | 0.000125
39 | 0.99067 | -0.17733 | 0 | 0
40 | 0.98995 | -0.19163 | 0.0017816 | 0.00044652
41 | 0.98969 | -0.1967 | 0.00061202 | 0.00015339
42 | 0.9905 | -0.18112 | 0 | 0
43 | 0.98942 | -0.20192 | 0.0019716 | 0.00049412
44 | 0.99105 | -0.17042 | 0.00046705 | 0.00011705
45 | 0.98908 | -0.20862 | 0 | 0
46 | 0.99108 | -0.16983 | 0.00037843 | 9.4844e-05
47 | 0.98873 | -0.21543 | 0.002796 | 0.00070075
48 | 0.99133 | -0.16497 | 0.00037562 | 9.414e-05
49 | 0.98864 | -0.2171 | 0.0042045 | 0.0010537
50 | 0.99134 | -0.16485 | 0.00046459 | 0.00011644
51 | 0.99062 | -0.17835 | 0.0016314 | 0.00040887
52 | 0.99057 | -0.17919 | 0.0018603 | 0.00046623
53 | 0.99055 | -0.17972 | 0.003144 | 0.00078797
54 | 0.98859 | -0.21817 | 0.0018763 | 0.00047024
55 | 0.98861 | -0.21784 | 0.0020419 | 0.00051175
56 | 0.99172 | -0.15781 | 0.0074678 | 0.0018716
57 | 0.99106 | -0.17048 | 0.025277 | 0.006335
58 | 0.98903 | -0.20978 | 0.005361 | 0.0013436
59 | 0.98376 | -0.31187 | 0.0037247 | 0.00093349
60 | 0.98351 | -0.31664 | 0.0017171 | 0.00043036
61 | 0.98473 | -0.29289 | 0.0056734 | 0.0014219
62 | 0.98253 | -0.33581 | 0 | 0
63 | 0.98531 | -0.28178 | 0.01346 | 0.0033734
64 | 0.98168 | -0.35231 | 0 | 0
65 | 0.98644 | -0.2599 | 0.0073284 | 0.0018367
66 | 0.98124 | -0.36099 | 0.0017228 | 0.00043177
67 | 0.98748 | -0.23964 | 0 | 0
68 | 0.9805 | -0.37549 | 0.0026906 | 0.00067432
69 | 0.98714 | -0.24636 | 0.003477 | 0.00087142
70 | 0.98681 | -0.25261 | 0.0023639 | 0.00059245
71 | 0.98644 | -0.25993 | 0.0051602 | 0.0012933
72 | 0.98621 | -0.26433 | 0.0019992 | 0.00050105
73 | 0.97107 | -0.55825 | 0.0049284 | 0.0012352
74 | 0.97093 | -0.56098 | 0.0019717 | 0.00049415
75 | 0.97111 | -0.55736 | 0.0027781 | 0.00069626
76 | 0.97077 | -0.56423 | 0.0014896 | 0.00037333
77 | 0.97149 | -0.54994 | 0.0014706 | 0.00036857
78 | 0.97068 | -0.56596 | 0.0022433 | 0.00056223
79 | 0.97162 | -0.54743 | 0.0035171 | 0.00088146
80 | 0.97058 | -0.56783 | 0.00095291 | 0.00023882
81 | 0.97167 | -0.54636 | 0 | 0
82 | 0.97054 | -0.56872 | 0.0080813 | 0.0020254
83 | 0.97151 | -0.54961 | 0.0039393 | 0.00098729
84 | 0.97241 | -0.53174 | 0.0090861 | 0.0022772
85 | 0.98563 | -0.27571 | 0.0011779 | 0.00029521
86 | 0.98562 | -0.27583 | 0.002747 | 0.00068846
87 | 0.9857 | -0.27424 | 0.00089908 | 0.00022533
88 | 0.98561 | -0.27604 | 0.0016369 | 0.00041025
89 | 0.98573 | -0.27376 | 0 | 0
90 | 0.98559 | -0.27651 | 0.0012918 | 0.00032377
91 | 0.9859 | -0.27034 | 0.0019772 | 0.00049552
92 | 0.97757 | -0.43292 | 0.0048307 | 0.0012107
93 | 0.97768 | -0.43081 | 0.0013743 | 0.00034443
94 | 0.98595 | -0.26938 | 0.0043776 | 0.0010971
95 | 0.97773 | -0.42972 | 0 | 0
96 | 0.97749 | -0.43455 | 0.00151 | 0.00037845
97 | 0.97752 | -0.43388 | 0.0013657 | 0.00034228
98 | 0.97753 | -0.43364 | 0.0019043 | 0.00047725
99 | 0.97723 | -0.43965 | 0.0011006 | 0.00027584
100 | 0.97771 | -0.43024 | 0.0017691 | 0.00044338
101 | 0.97705 | -0.44314 | 0.0032679 | 0.00081901
102 | 0.97948 | -0.3954 | 0.002967 | 0.0007436
103 | 0.97949 | -0.39521 | 0.00055412 | 0.00013888
104 | 0.97921 | -0.40072 | 0.000577 | 0.00014461
105 | 0.97973 | -0.39041 | 0.00067845 | 0.00017004
106 | 0.97898 | -0.40516 | 0.0013371 | 0.0003351
107 | 0.98003 | -0.3846 | 0.00059079 | 0.00014807
108 | 0.97868 | -0.41101 | 0.0014873 | 0.00037276
109 | 0.98033 | -0.37878 | 0.0021842 | 0.00054741
110 | 0.97861 | -0.41253 | 0.0041977 | 0.001052
111 | 0.97839 | -0.41668 | 0.0021122 | 0.00052938
112 | 0.97814 | -0.42172 | 0.0013925 | 0.00034899
113 | 0.97108 | -0.55804 | 0.0030437 | 0.00076282
114 | 0.97293 | -0.52139 | 0.0031515 | 0.00078985
115 | 0.97088 | -0.56192 | 0.0038197 | 0.0009573
116 | 0.97069 | -0.56585 | 0.0038316 | 0.00096028
117 | 0.97075 | -0.5645 | 0.0040573 | 0.0010169
118 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0079232 | -0.0019854 | 0.0079242 | 0.0019858 | 9.5459e-07 | 3.8919e-07 | 0.012029 | 0.012029 | 0.012029 | 0.98011 | -0.38076 | 0.98024 | -0.37823 | 3.3047
1 | 0.003978 | 0.00099664 | -0.0039777 | -0.00099672 | 2.8099e-07 | -7.9051e-08 | 0.0060393 | 0.0060394 | 0.0060394 | 0.98011 | -0.38076 | 0.98004 | -0.38225 | 1.6592
2 | 0.087388 | 0.022134 | -0.087215 | -0.022024 | 0.00017226 | 0.00010992 | 0.13274 | 0.13274 | 0.13274 | 0.98024 | -0.37823 | 0.97813 | -0.41937 | 36.4667
3 | -0.095312 | -0.02412 | 0.095425 | 0.024192 | 0.00011284 | 7.2038e-05 | 0.14477 | 0.14477 | 0.14477 | 0.98024 | -0.37823 | 0.98151 | -0.3536 | 39.7713
4 | 0.0039777 | 0.00099672 | -0.0039774 | -0.00099682 | 3.4086e-07 | -9.583e-08 | 0.0060394 | 0.0060395 | 0.0060395 | 0.98004 | -0.38225 | 0.97995 | -0.38405 | 1.6592
5 | 0.083605 | 0.021119 | -0.083505 | -0.021056 | 9.9816e-05 | 6.3676e-05 | 0.12725 | 0.12725 | 0.12725 | 0.97813 | -0.41937 | 0.97686 | -0.44431 | 34.9579
6 | -0.099031 | -0.025096 | 0.099239 | 0.025228 | 0.00020787 | 0.00013273 | 0.15023 | 0.15023 | 0.15023 | 0.98151 | -0.3536 | 0.98376 | -0.31001 | 41.2732
7 | 0.0039774 | 0.00099682 | -0.0039774 | -0.00099682 | 2.2256e-08 | -6.2547e-09 | 0.0060395 | 0.0060395 | 0.0060395 | 0.97995 | -0.38405 | 0.97994 | -0.38416 | 1.6592
8 | 0.069644 | 0.01758 | -0.069544 | -0.017516 | 9.9905e-05 | 6.3644e-05 | 0.10613 | 0.10613 | 0.10613 | 0.97686 | -0.44431 | 0.97533 | -0.4743 | 29.157
9 | 0.013862 | 0.0034756 | -0.013858 | -0.0034734 | 3.8941e-06 | 2.2008e-06 | 0.021116 | 0.021116 | 0.021116 | 0.97686 | -0.44431 | 0.97656 | -0.4502 | 5.801
10 | -0.10164 | -0.02583 | 0.10174 | 0.025896 | 0.00010282 | 6.5658e-05 | 0.15387 | 0.15387 | 0.15387 | 0.98376 | -0.31001 | 0.98485 | -0.28902 | 42.2716
11 | 0.0024027 | 0.00060213 | -0.0024027 | -0.00060217 | 1.6882e-08 | -3.2472e-08 | 0.0036343 | 0.0036343 | 0.0036343 | 0.98376 | -0.31001 | 0.98375 | -0.31016 | 0.99842
12 | 0.066618 | 0.016783 | -0.06655 | -0.016739 | 6.8423e-05 | 4.357e-05 | 0.10167 | 0.10167 | 0.10167 | 0.97533 | -0.4743 | 0.97423 | -0.4958 | 27.9307
13 | 0.010379 | 0.0026014 | -0.010377 | -0.0026007 | 1.5149e-06 | 7.6748e-07 | 0.015814 | 0.015814 | 0.015814 | 0.97656 | -0.4502 | 0.9764 | -0.45327 | 4.3446
14 | 0.0054039 | 0.0013543 | -0.0054035 | -0.0013542 | 3.9629e-07 | 5.1927e-08 | 0.0081648 | 0.0081648 | 0.0081648 | 0.98485 | -0.28902 | 0.98477 | -0.29056 | 2.2431
15 | -0.10715 | -0.02725 | 0.10751 | 0.027479 | 0.00035742 | 0.00022828 | 0.16203 | 0.16203 | 0.16203 | 0.98485 | -0.28902 | 0.98844 | -0.22004 | 44.5147
16 | 0.062117 | 0.015629 | -0.06211 | -0.015624 | 7.4923e-06 | 4.7674e-06 | 0.094898 | 0.094898 | 0.094898 | 0.97423 | -0.4958 | 0.97411 | -0.49832 | 26.0708
17 | 0.0054351 | 0.0013621 | -0.0054346 | -0.001362 | 5.8794e-07 | 9.0499e-08 | 0.008283 | 0.0082831 | 0.0082831 | 0.9764 | -0.45327 | 0.97629 | -0.45554 | 2.2756
18 | -0.10989 | -0.028077 | 0.10996 | 0.028121 | 6.8966e-05 | 4.4052e-05 | 0.16563 | 0.16563 | 0.16563 | 0.98844 | -0.22004 | 0.98911 | -0.20707 | 45.5028
19 | 0.058517 | 0.014723 | -0.058491 | -0.014707 | 2.614e-05 | 1.6621e-05 | 0.08941 | 0.08941 | 0.08941 | 0.97411 | -0.49832 | 0.97363 | -0.50768 | 24.5632
20 | 0.058491 | 0.014707 | -0.058453 | -0.014683 | 3.8273e-05 | 2.4336e-05 | 0.08941 | 0.08941 | 0.08941 | 0.97363 | -0.50768 | 0.97293 | -0.52139 | 24.5633
21 | -0.11292 | -0.028863 | 0.11303 | 0.028934 | 0.00011225 | 7.0644e-05 | 0.17008 | 0.17008 | 0.17008 | 0.98911 | -0.20707 | 0.99019 | -0.18654 | 15.5752
22 | -0.11526 | -0.029492 | 0.11531 | 0.029524 | 5.1427e-05 | 3.2385e-05 | 0.17343 | 0.17343 | 0.17343 | 0.99019 | -0.18654 | 0.99067 | -0.17733 | 15.8817
23 | -0.016789 | -0.0042077 | 0.016794 | 0.004211 | 5.6414e-06 | 3.2946e-06 | 0.024991 | 0.024991 | 0.024991 | 0.99963 | -0.007051 | 1 | 0 | 6.8657
24 | 0.33258 | 0.085281 | -0.33132 | -0.084474 | 0.0012638 | 0.00080722 | 0.49557 | 0.49557 | 0.49557 | 1 | 0 | 0.99585 | -0.078687 | 45.3822
25 | 0.16731 | 0.042834 | -0.16722 | -0.042781 | 8.2001e-05 | 5.2072e-05 | 0.25031 | 0.25031 | 0.25031 | 0.99585 | -0.078687 | 0.99532 | -0.088812 | 22.9223
26 | 0.16401 | 0.04164 | -0.16394 | -0.041591 | 7.8211e-05 | 4.9649e-05 | 0.24526 | 0.24526 | 0.24526 | 0.99585 | -0.078687 | 0.99533 | -0.088603 | 22.4599
27 | 0.16125 | 0.041284 | -0.16116 | -0.041231 | 8.4222e-05 | 5.3451e-05 | 0.24138 | 0.24138 | 0.24138 | 0.99532 | -0.088812 | 0.99475 | -0.099602 | 22.1044
28 | 0.15869 | 0.040276 | -0.15868 | -0.040267 | 1.3341e-05 | 8.4645e-06 | 0.23742 | 0.23742 | 0.23742 | 0.99533 | -0.088603 | 0.99524 | -0.09035 | 21.7416
29 | -0.12626 | -0.032321 | 0.12629 | 0.032345 | 3.8353e-05 | 2.4216e-05 | 0.18965 | 0.18965 | 0.18965 | 0.9919 | -0.15376 | 0.99223 | -0.14749 | 17.3669
30 | 0.12626 | 0.032321 | -0.12622 | -0.032296 | 3.9155e-05 | 2.4722e-05 | 0.18965 | 0.18965 | 0.18965 | 0.9919 | -0.15376 | 0.99157 | -0.16017 | 17.3669
31 | -0.14551 | -0.037175 | 0.14557 | 0.037218 | 6.8502e-05 | 4.3396e-05 | 0.21846 | 0.21846 | 0.21846 | 0.99223 | -0.14749 | 0.99274 | -0.13776 | 20.0056
32 | 0.01921 | 0.0048299 | -0.019203 | -0.0048257 | 7.1095e-06 | 4.2552e-06 | 0.028815 | 0.028815 | 0.028815 | 0.99223 | -0.14749 | 0.99183 | -0.15525 | 7.9162
33 | 0.12409 | 0.031762 | -0.124 | -0.031709 | 8.3461e-05 | 5.2672e-05 | 0.18645 | 0.18645 | 0.18645 | 0.99157 | -0.16017 | 0.99084 | -0.17407 | 17.0741
34 | 0.14915 | 0.038219 | -0.14906 | -0.038165 | 8.581e-05 | 5.4383e-05 | 0.22341 | 0.22341 | 0.22341 | 0.99475 | -0.099602 | 0.99412 | -0.11148 | 20.4585
35 | 0.14823 | 0.037649 | -0.14809 | -0.037557 | 0.00014508 | 9.244e-05 | 0.2218 | 0.2218 | 0.2218 | 0.99524 | -0.09035 | 0.99418 | -0.11071 | 30.4673
36 | -0.14731 | -0.037654 | 0.14735 | 0.037677 | 3.6379e-05 | 2.3051e-05 | 0.22106 | 0.22106 | 0.22106 | 0.99274 | -0.13776 | 0.99301 | -0.13266 | 20.244
37 | 0.01751 | 0.0044013 | -0.017507 | -0.0043991 | 3.7722e-06 | 2.2262e-06 | 0.026275 | 0.026275 | 0.026275 | 0.99183 | -0.15525 | 0.9916 | -0.15976 | 7.2184
38 | 0.12197 | 0.0312 | -0.12195 | -0.031187 | 1.9243e-05 | 1.2139e-05 | 0.1834 | 0.1834 | 0.1834 | 0.99084 | -0.17407 | 0.99067 | -0.17733 | 16.7945
39 | 0.14825 | 0.037962 | -0.1481 | -0.037866 | 0.00015192 | 9.6274e-05 | 0.22219 | 0.22219 | 0.22219 | 0.99412 | -0.11148 | 0.99301 | -0.13266 | 20.3475
40 | 0.13789 | 0.035002 | -0.13758 | -0.034803 | 0.00031173 | 0.00019926 | 0.20655 | 0.20655 | 0.20655 | 0.99418 | -0.11071 | 0.99172 | -0.15781 | 56.7434
41 | 0.017008 | 0.0042741 | -0.017004 | -0.0042717 | 4.1346e-06 | 2.4279e-06 | 0.025526 | 0.025526 | 0.025526 | 0.9916 | -0.15976 | 0.99134 | -0.16485 | 7.0128
42 | 0.0066363 | 0.0016631 | -0.006636 | -0.001663 | 3.2082e-07 | 9.4467e-08 | 0.0099679 | 0.0099679 | 0.0099679 | 0.99067 | -0.17733 | 0.99062 | -0.17835 | 2.7384
43 | 0.013517 | 0.0033913 | -0.013513 | -0.0033895 | 3.2652e-06 | 1.8187e-06 | 0.020318 | 0.020318 | 0.020318 | 0.98995 | -0.19163 | 0.98969 | -0.1967 | 5.582
44 | -0.015298 | -0.0038378 | 0.015306 | 0.0038422 | 7.676e-06 | 4.4147e-06 | 0.022996 | 0.022996 | 0.022996 | 0.98995 | -0.19163 | 0.9905 | -0.18112 | 6.3177
45 | 0.012901 | 0.0032361 | -0.012898 | -0.0032343 | 3.2104e-06 | 1.7624e-06 | 0.019398 | 0.019398 | 0.019398 | 0.98969 | -0.1967 | 0.98942 | -0.20192 | 5.3292
46 | -0.015306 | -0.0038422 | 0.015314 | 0.0038467 | 7.8124e-06 | 4.4926e-06 | 0.022996 | 0.022996 | 0.022996 | 0.9905 | -0.18112 | 0.99105 | -0.17042 | 6.3176
47 | 0.010927 | 0.0027402 | -0.010923 | -0.0027384 | 3.4884e-06 | 1.7903e-06 | 0.016433 | 0.016433 | 0.016433 | 0.98942 | -0.20192 | 0.98908 | -0.20862 | 4.5147
48 | -0.015781 | -0.0039638 | 0.015781 | 0.003964 | 4.4737e-07 | 2.5894e-07 | 0.023697 | 0.023697 | 0.023697 | 0.99105 | -0.17042 | 0.99108 | -0.16983 | 6.5102
49 | 0.010923 | 0.0027384 | -0.010919 | -0.0027366 | 3.5436e-06 | 1.819e-06 | 0.016433 | 0.016434 | 0.016434 | 0.98908 | -0.20862 | 0.98873 | -0.21543 | 4.5147
50 | -0.01616 | -0.0040589 | 0.016163 | 0.0040611 | 3.7457e-06 | 2.1786e-06 | 0.024265 | 0.024265 | 0.024265 | 0.99108 | -0.16983 | 0.99133 | -0.16497 | 6.6663
51 | 0.0081235 | 0.0020358 | -0.0081228 | -0.0020356 | 6.4406e-07 | 2.6484e-07 | 0.012226 | 0.012226 | 0.012226 | 0.98873 | -0.21543 | 0.98864 | -0.2171 | 3.3587
52 | -0.016539 | -0.0041552 | 0.016539 | 0.0041552 | 9.1532e-08 | 5.3475e-08 | 0.024829 | 0.024829 | 0.024829 | 0.99133 | -0.16497 | 0.99134 | -0.16485 | 6.8212
53 | 0.0039184 | 0.00098184 | -0.0039182 | -0.00098189 | 1.3921e-07 | -4.7766e-08 | 0.0058975 | 0.0058975 | 0.0058975 | 0.98864 | -0.2171 | 0.98861 | -0.21784 | 1.6202
54 | 0.0050046 | 0.0012541 | -0.0050044 | -0.0012541 | 2.0192e-07 | 6.5648e-09 | 0.0075174 | 0.0075174 | 0.0075174 | 0.99062 | -0.17835 | 0.99057 | -0.17919 | 2.0652
55 | 0.0031441 | 0.0007879 | -0.003144 | -0.00078797 | 7.8518e-08 | -7.0578e-08 | 0.004723 | 0.004723 | 0.004723 | 0.99057 | -0.17919 | 0.99055 | -0.17972 | 1.2975
56 | -0.0018763 | -0.00047024 | 0.0018763 | 0.00047013 | 2.9167e-08 | -1.0637e-07 | 0.0028242 | 0.0028241 | 0.0028242 | 0.98859 | -0.21817 | 0.98861 | -0.21784 | 0.77587
57 | 0.13011 | 0.032931 | -0.13003 | -0.032881 | 7.9057e-05 | 5.0525e-05 | 0.19534 | 0.19534 | 0.19534 | 0.99172 | -0.15781 | 0.99106 | -0.17048 | 53.6651
58 | 0.10476 | 0.026546 | -0.10456 | -0.02642 | 0.00019737 | 0.00012605 | 0.15739 | 0.15739 | 0.15739 | 0.99106 | -0.17048 | 0.98903 | -0.20978 | 43.2389
59 | 0.099199 | 0.025076 | -0.099057 | -0.024986 | 0.00014183 | 9.0553e-05 | 0.14932 | 0.14932 | 0.14932 | 0.98903 | -0.20978 | 0.98748 | -0.23964 | 41.023
60 | 0.041525 | 0.010477 | -0.041515 | -0.010471 | 9.4924e-06 | 5.9938e-06 | 0.062834 | 0.062834 | 0.062834 | 0.98376 | -0.31187 | 0.98351 | -0.31664 | 17.2622
61 | -0.045249 | -0.01141 | 0.04529 | 0.011436 | 4.1135e-05 | 2.6029e-05 | 0.068468 | 0.068468 | 0.068468 | 0.98376 | -0.31187 | 0.98473 | -0.29289 | 18.8099
62 | 0.039798 | 0.010041 | -0.039761 | -0.010018 | 3.6495e-05 | 2.3017e-05 | 0.060236 | 0.060236 | 0.060236 | 0.98351 | -0.31664 | 0.98253 | -0.33581 | 16.5485
63 | -0.050964 | -0.012858 | 0.050991 | 0.012876 | 2.7119e-05 | 1.7201e-05 | 0.077041 | 0.077041 | 0.077041 | 0.98473 | -0.29289 | 0.98531 | -0.28178 | 21.1651
64 | 0.039761 | 0.010018 | -0.03973 | -0.0099978 | 3.1347e-05 | 1.9771e-05 | 0.060236 | 0.060237 | 0.060237 | 0.98253 | -0.33581 | 0.98168 | -0.35231 | 16.5485
65 | -0.064451 | -0.016249 | 0.064518 | 0.016292 | 6.7592e-05 | 4.3016e-05 | 0.097368 | 0.097368 | 0.097368 | 0.98531 | -0.28178 | 0.98644 | -0.2599 | 26.7496
66 | 0.03973 | 0.0099978 | -0.039714 | -0.0099874 | 1.6476e-05 | 1.0392e-05 | 0.060237 | 0.060237 | 0.060237 | 0.98168 | -0.35231 | 0.98124 | -0.36099 | 16.5485
67 | -0.071847 | -0.018129 | 0.071917 | 0.018173 | 6.9771e-05 | 4.4451e-05 | 0.10842 | 0.10842 | 0.10842 | 0.98644 | -0.2599 | 0.98748 | -0.23964 | 29.7865
68 | 0.037991 | 0.0095556 | -0.037965 | -0.009539 | 2.6296e-05 | 1.6563e-05 | 0.057624 | 0.057624 | 0.057624 | 0.98124 | -0.36099 | 0.9805 | -0.37549 | 15.8308
69 | 0.02714 | 0.0068126 | -0.027132 | -0.0068072 | 8.6967e-06 | 5.3886e-06 | 0.040901 | 0.040901 | 0.040901 | 0.98748 | -0.23964 | 0.98714 | -0.24636 | 11.2365
70 | 0.035274 | 0.0088647 | -0.035268 | -0.0088612 | 5.532e-06 | 3.4756e-06 | 0.053541 | 0.053541 | 0.053541 | 0.9805 | -0.37549 | 0.98033 | -0.37878 | 14.7091
71 | 0.023654 | 0.0059358 | -0.023647 | -0.0059315 | 7.0553e-06 | 4.3263e-06 | 0.03566 | 0.03566 | 0.03566 | 0.98714 | -0.24636 | 0.98681 | -0.25261 | 9.7966
72 | 0.021284 | 0.005339 | -0.021276 | -0.0053345 | 7.4176e-06 | 4.502e-06 | 0.032095 | 0.032095 | 0.032095 | 0.98681 | -0.25261 | 0.98644 | -0.25993 | 8.8174
73 | 0.016116 | 0.0040413 | -0.016113 | -0.0040393 | 3.3814e-06 | 1.9694e-06 | 0.024311 | 0.024311 | 0.024311 | 0.98644 | -0.25993 | 0.98621 | -0.26433 | 6.6789
74 | 0.014113 | 0.0035383 | -0.01411 | -0.0035363 | 3.3927e-06 | 1.9168e-06 | 0.021295 | 0.021295 | 0.021295 | 0.98621 | -0.26433 | 0.98595 | -0.26938 | 5.8503
75 | 0.014745 | 0.0036971 | -0.014743 | -0.003696 | 1.9148e-06 | 1.1018e-06 | 0.022595 | 0.022595 | 0.022595 | 0.97107 | -0.55825 | 0.97093 | -0.56098 | 6.2074
76 | -0.019673 | -0.0049323 | 0.019674 | 0.0049328 | 8.332e-07 | 5.03e-07 | 0.030147 | 0.030147 | 0.030147 | 0.97107 | -0.55825 | 0.97111 | -0.55736 | 8.2821
77 | 0.012771 | 0.0032019 | -0.012769 | -0.0032008 | 1.9785e-06 | 1.0959e-06 | 0.019573 | 0.019573 | 0.019573 | 0.97093 | -0.56098 | 0.97077 | -0.56423 | 5.3772
78 | -0.022452 | -0.005629 | 0.02246 | 0.0056339 | 7.9432e-06 | 4.8621e-06 | 0.034404 | 0.034403 | 0.034404 | 0.97111 | -0.55736 | 0.97149 | -0.54994 | 9.4515
79 | 0.01128 | 0.0028274 | -0.011279 | -0.0028269 | 9.3178e-07 | 4.9359e-07 | 0.01729 | 0.01729 | 0.01729 | 0.97077 | -0.56423 | 0.97068 | -0.56596 | 4.75
80 | -0.023931 | -0.0060025 | 0.023933 | 0.0060042 | 2.8613e-06 | 1.7609e-06 | 0.036656 | 0.036656 | 0.036656 | 0.97149 | -0.54994 | 0.97162 | -0.54743 | 10.0703
81 | 0.0090354 | 0.0022647 | -0.0090346 | -0.0022643 | 8.0478e-07 | 3.768e-07 | 0.013851 | 0.013851 | 0.013851 | 0.97068 | -0.56596 | 0.97058 | -0.56783 | 3.8052
82 | -0.027451 | -0.0068857 | 0.027452 | 0.0068866 | 1.4091e-06 | 8.755e-07 | 0.042042 | 0.042042 | 0.042042 | 0.97162 | -0.54743 | 0.97167 | -0.54636 | 11.5501
83 | 0.0080817 | 0.0020255 | -0.0080813 | -0.0020254 | 3.4019e-07 | 1.4469e-07 | 0.01239 | 0.01239 | 0.01239 | 0.97058 | -0.56783 | 0.97054 | -0.56872 | 3.4039
84 | 0.018704 | 0.0046912 | -0.018701 | -0.0046894 | 2.8962e-06 | 1.737e-06 | 0.028644 | 0.028644 | 0.028644 | 0.97167 | -0.54636 | 0.97151 | -0.54961 | 7.8693
85 | -0.046156 | -0.011578 | 0.046188 | 0.011598 | 3.219e-05 | 2.0388e-05 | 0.070686 | 0.070686 | 0.070686 | 0.97167 | -0.54636 | 0.97241 | -0.53174 | 19.4194
86 | 0.014762 | 0.0037021 | -0.014756 | -0.0036987 | 5.9316e-06 | 3.4133e-06 | 0.022611 | 0.022611 | 0.022611 | 0.97151 | -0.54961 | 0.97108 | -0.55804 | 6.2117
87 | -0.055274 | -0.013875 | 0.055301 | 0.013893 | 2.7302e-05 | 1.7347e-05 | 0.08459 | 0.08459 | 0.08459 | 0.97241 | -0.53174 | 0.97293 | -0.52139 | 23.2391
88 | 0.0056758 | 0.0014222 | -0.0056758 | -0.0014222 | 3.326e-08 | 5.8911e-09 | 0.0085688 | 0.0085688 | 0.0085688 | 0.98563 | -0.27571 | 0.98562 | -0.27583 | 2.3541
89 | -0.0068537 | -0.0017174 | 0.0068542 | 0.0017176 | 4.7921e-07 | 1.5456e-07 | 0.010347 | 0.010347 | 0.010347 | 0.98563 | -0.27571 | 0.9857 | -0.27424 | 2.8426
90 | 0.0029288 | 0.00073374 | -0.0029288 | -0.00073377 | 2.877e-08 | -3.1599e-08 | 0.0044216 | 0.0044216 | 0.0044216 | 0.98562 | -0.27583 | 0.98561 | -0.27604 | 1.2147
91 | -0.0077533 | -0.0019429 | 0.0077535 | 0.001943 | 1.7769e-07 | 6.963e-08 | 0.011704 | 0.011704 | 0.011704 | 0.9857 | -0.27424 | 0.98573 | -0.27376 | 3.2154
92 | 0.0012919 | 0.00032352 | -0.0012918 | -0.00032377 | 2.9243e-08 | -2.4255e-07 | 0.0019503 | 0.0019504 | 0.0019504 | 0.98561 | -0.27604 | 0.98559 | -0.27651 | 0.53582
93 | -0.0077535 | -0.001943 | 0.0077547 | 0.0019435 | 1.2624e-06 | 4.9462e-07 | 0.011704 | 0.011704 | 0.011704 | 0.98573 | -0.27376 | 0.9859 | -0.27034 | 3.2154
94 | -0.0097319 | -0.002439 | 0.0097323 | 0.0024392 | 4.4722e-07 | 2.1572e-07 | 0.014688 | 0.014688 | 0.014688 | 0.9859 | -0.27034 | 0.98595 | -0.26938 | 4.0352
95 | -0.0048307 | -0.0012107 | 0.0048311 | 0.0012107 | 4.8532e-07 | 1.0466e-08 | 0.007353 | 0.0073529 | 0.007353 | 0.97757 | -0.43292 | 0.97768 | -0.43081 | 2.0201
96 | -0.0062055 | -0.0015551 | 0.0062058 | 0.0015552 | 3.244e-07 | 8.5995e-08 | 0.0094446 | 0.0094446 | 0.0094446 | 0.97768 | -0.43081 | 0.97773 | -0.42972 | 2.5947
97 | 0.010921 | 0.0027363 | -0.010921 | -0.0027361 | 2.7334e-07 | 1.4185e-07 | 0.016621 | 0.016621 | 0.016621 | 0.97773 | -0.42972 | 0.97771 | -0.43024 | 4.5662
98 | -0.017127 | -0.0042915 | 0.017134 | 0.0042953 | 6.528e-06 | 3.8564e-06 | 0.026065 | 0.026065 | 0.026065 | 0.97773 | -0.42972 | 0.97814 | -0.42172 | 7.1608
99 | -0.00151 | -0.00037845 | 0.0015101 | 0.00037818 | 4.7781e-08 | -2.7171e-07 | 0.0022987 | 0.0022986 | 0.0022987 | 0.97749 | -0.43455 | 0.97752 | -0.43388 | 0.63151
100 | -0.007246 | -0.0018148 | 0.0072461 | 0.0018148 | 8.5937e-08 | 3.1385e-08 | 0.01103 | 0.01103 | 0.01103 | 0.97752 | -0.43388 | 0.97753 | -0.43364 | 3.0302
101 | 0.0043703 | 0.0010943 | -0.0043691 | -0.0010945 | 1.1993e-06 | -1.3813e-07 | 0.0066522 | 0.0066526 | 0.0066526 | 0.97752 | -0.43388 | 0.97723 | -0.43965 | 1.8276
102 | -0.0091504 | -0.0022921 | 0.0091519 | 0.0022928 | 1.4793e-06 | 6.9179e-07 | 0.013928 | 0.013928 | 0.013928 | 0.97753 | -0.43364 | 0.97771 | -0.43024 | 3.8265
103 | 0.0032684 | 0.00081863 | -0.0032679 | -0.00081901 | 5.427e-07 | -3.8457e-07 | 0.0049767 | 0.0049769 | 0.0049769 | 0.97723 | -0.43965 | 0.97705 | -0.44314 | 1.3673
104 | -0.031235 | -0.0078407 | 0.031235 | 0.0078409 | 2.855e-07 | 1.7847e-07 | 0.047457 | 0.047457 | 0.047457 | 0.97948 | -0.3954 | 0.97949 | -0.39521 | 13.0375
105 | 0.028268 | 0.0070971 | -0.028261 | -0.0070927 | 7.1772e-06 | 4.4628e-06 | 0.042949 | 0.042949 | 0.042949 | 0.97948 | -0.3954 | 0.97921 | -0.40072 | 11.7992
106 | -0.031789 | -0.0079798 | 0.031797 | 0.0079843 | 7.2709e-06 | 4.5487e-06 | 0.048298 | 0.048298 | 0.048298 | 0.97949 | -0.39521 | 0.97973 | -0.39041 | 13.2688
107 | 0.027684 | 0.006948 | -0.027678 | -0.0069444 | 5.857e-06 | 3.6375e-06 | 0.042072 | 0.042072 | 0.042072 | 0.97921 | -0.40072 | 0.97898 | -0.40516 | 11.5583
108 | -0.032475 | -0.0081544 | 0.032484 | 0.00816 | 8.9979e-06 | 5.6344e-06 | 0.049329 | 0.049329 | 0.049329 | 0.97973 | -0.39041 | 0.98003 | -0.3846 | 13.5518
109 | 0.026341 | 0.0066093 | -0.026334 | -0.0066048 | 7.3454e-06 | 4.5475e-06 | 0.04004 | 0.04004 | 0.04004 | 0.97898 | -0.40516 | 0.97868 | -0.41101 | 11
110 | -0.033075 | -0.0083081 | 0.033084 | 0.0083138 | 9.2031e-06 | 5.7674e-06 | 0.050226 | 0.050226 | 0.050226 | 0.98003 | -0.3846 | 0.98033 | -0.37878 | 13.7983
111 | 0.024846 | 0.006232 | -0.024844 | -0.0062309 | 1.7969e-06 | 1.1078e-06 | 0.037779 | 0.037779 | 0.037779 | 0.97868 | -0.41101 | 0.97861 | -0.41253 | 10.3788
112 | 0.020647 | 0.0051788 | -0.020643 | -0.0051764 | 4.0923e-06 | 2.48e-06 | 0.031396 | 0.031396 | 0.031396 | 0.97861 | -0.41253 | 0.97839 | -0.41668 | 8.6253
113 | 0.01853 | 0.004647 | -0.018526 | -0.0046443 | 4.4432e-06 | 2.6563e-06 | 0.028184 | 0.028184 | 0.028184 | 0.97839 | -0.41668 | 0.97814 | -0.42172 | 7.7427
114 | 0.011712 | 0.0029359 | -0.01171 | -0.0029348 | 2.1618e-06 | 1.1622e-06 | 0.017947 | 0.017947 | 0.017947 | 0.97108 | -0.55804 | 0.97088 | -0.56192 | 4.9304
115 | 0.0078901 | 0.0019775 | -0.0078891 | -0.0019771 | 9.7059e-07 | 4.0233e-07 | 0.012093 | 0.012093 | 0.012093 | 0.97088 | -0.56192 | 0.97075 | -0.5645 | 3.3222
116 | -0.0038316 | -0.00096028 | 0.0038318 | 0.00096021 | 2.4658e-07 | -7.7812e-08 | 0.0058736 | 0.0058735 | 0.0058736 | 0.97069 | -0.56585 | 0.97075 | -0.5645 | 1.6136

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.36078 | 0.091935

## res_load
| p_mw | q_mvar
0 | 0.0039452 | 0.00098876
1 | 0.0036102 | 0.00090481
2 | 0.0036061 | 0.00090378
3 | 0.0039774 | 0.00099682
4 | 0.0029257 | 0.00073326
5 | 0.0034792 | 0.00087197
6 | 0.0024027 | 0.00060217
7 | 0.0044325 | 0.0011109
8 | 0.0049419 | 0.0012385
9 | 0.0054035 | 0.0013542
10 | 0.0023893 | 0.00059881
11 | 0.0035924 | 0.00090034
12 | 0.0054346 | 0.001362
13 | 0.0029591 | 0.00074162
14 | 0.002227 | 0.00055815
15 | 0.016789 | 0.0042077
16 | 0.0097474 | 0.0024429
17 | 0.0059748 | 0.0014974
18 | 0.0052468 | 0.001315
19 | 0.0021308 | 0.00053404
20 | 0.012015 | 0.0030113
21 | 0.010445 | 0.0026178
22 | 0.0017371 | 0.00043535
23 | 0.001693 | 0.00042431
24 | 0.0020338 | 0.00050972
25 | 0.00081003 | 0.00020301
26 | 0.010193 | 0.0025546
27 | 0.00075398 | 0.00018897
28 | 0.00049877 | 0.000125
29 | 0.0017816 | 0.00044652
30 | 0.00061202 | 0.00015339
31 | 0.0019716 | 0.00049412
32 | 0.00046705 | 0.00011705
33 | 0.00037843 | 9.4844e-05
34 | 0.002796 | 0.00070075
35 | 0.00037562 | 9.414e-05
36 | 0.0042045 | 0.0010537
37 | 0.00046459 | 0.00011644
38 | 0.0016314 | 0.00040887
39 | 0.0018603 | 0.00046623
40 | 0.003144 | 0.00078797
41 | 0.0018763 | 0.00047024
42 | 0.0020419 | 0.00051175
43 | 0.0074678 | 0.0018716
44 | 0.025277 | 0.006335
45 | 0.005361 | 0.0013436
46 | 0.0037247 | 0.00093349
47 | 0.0017171 | 0.00043036
48 | 0.0056734 | 0.0014219
49 | 0.01346 | 0.0033734
50 | 0.0073284 | 0.0018367
51 | 0.0017228 | 0.00043177
52 | 0.0026906 | 0.00067432
53 | 0.003477 | 0.00087142
54 | 0.0023639 | 0.00059245
55 | 0.0051602 | 0.0012933
56 | 0.0019992 | 0.00050105
57 | 0.0049284 | 0.0012352
58 | 0.0019717 | 0.00049415
59 | 0.0027781 | 0.00069626
60 | 0.0014896 | 0.00037333
61 | 0.0014706 | 0.00036857
62 | 0.0022433 | 0.00056223
63 | 0.0035171 | 0.00088146
64 | 0.00095291 | 0.00023882
65 | 0.0080813 | 0.0020254
66 | 0.0039393 | 0.00098729
67 | 0.0090861 | 0.0022772
68 | 0.0011779 | 0.00029521
69 | 0.002747 | 0.00068846
70 | 0.00089908 | 0.00022533
71 | 0.0016369 | 0.00041025
72 | 0.0012918 | 0.00032377
73 | 0.0019772 | 0.00049552
74 | 0.0048307 | 0.0012107
75 | 0.0013743 | 0.00034443
76 | 0.0043776 | 0.0010971
77 | 0.00151 | 0.00037845
78 | 0.0013657 | 0.00034228
79 | 0.0019043 | 0.00047725
80 | 0.0011006 | 0.00027584
81 | 0.0017691 | 0.00044338
82 | 0.0032679 | 0.00081901
83 | 0.002967 | 0.0007436
84 | 0.00055412 | 0.00013888
85 | 0.000577 | 0.00014461
86 | 0.00067845 | 0.00017004
87 | 0.0013371 | 0.0003351
88 | 0.00059079 | 0.00014807
89 | 0.0014873 | 0.00037276
90 | 0.0021842 | 0.00054741
91 | 0.0041977 | 0.001052
92 | 0.0021122 | 0.00052938
93 | 0.0013925 | 0.00034899
94 | 0.0030437 | 0.00076282
95 | 0.0031515 | 0.00078985
96 | 0.0038197 | 0.0009573
97 | 0.0038316 | 0.00096028
98 | 0.0040573 | 0.0010169

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1