## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_113-12_0_7_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_113-12_0_7_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_113-12_0_7_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_113-12_0_7_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_113-12_0_7_node_99 | 0.4 | n |  | TRUE
5 | bus_LV_113-12_0_7_node_16 | 0.4 | n |  | TRUE
6 | bus_LV_113-12_0_7_node_94 | 0.4 | n |  | TRUE
7 | bus_LV_113-12_0_7_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_113-12_0_7_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_113-12_0_7_node_34 | 0.4 | n |  | TRUE
10 | bus_LV_113-12_0_7_node_15 | 0.4 | n |  | TRUE
11 | bus_LV_113-12_0_7_node_119 | 0.4 | n |  | TRUE
12 | bus_LV_113-12_0_7_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_113-12_0_7_node_46 | 0.4 | n |  | TRUE
14 | bus_LV_113-12_0_7_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_113-12_0_7_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_113-12_0_7_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_113-12_0_7_node_59 | 0.4 | n |  | TRUE
18 | bus_LV_113-12_0_7_node_60 | 0.4 | n |  | TRUE
19 | bus_LV_113-12_0_7_node_61 | 0.4 | n |  | TRUE
20 | bus_LV_113-12_0_7_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_113-12_0_7_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_113-12_0_7_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_113-12_0_7_node_18 | 0.4 | n |  | TRUE
24 | bus_LV_113-12_0_7_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_113-12_0_7_node_37 | 0.4 | n |  | TRUE
26 | bus_LV_113-12_0_7_node_31 | 0.4 | n |  | TRUE
27 | bus_LV_113-12_0_7_node_36 | 0.4 | n |  | TRUE
28 | bus_LV_113-12_0_7_node_19 | 0.4 | n |  | TRUE
29 | bus_LV_113-12_0_7_node_32 | 0.4 | n |  | TRUE
30 | bus_LV_113-12_0_7_node_29 | 0.4 | n |  | TRUE
31 | bus_LV_113-12_0_7_node_40 | 0.4 | n |  | TRUE
32 | bus_LV_113-12_0_7_node_39 | 0.4 | n |  | TRUE
33 | bus_LV_113-12_0_7_node_35 | 0.4 | n |  | TRUE
34 | bus_LV_113-12_0_7_node_33 | 0.4 | n |  | TRUE
35 | bus_LV_113-12_0_7_node_38 | 0.4 | n |  | TRUE
36 | bus_LV_113-12_0_7_node_21 | 0.4 | n |  | TRUE
37 | bus_LV_113-12_0_7_node_20 | 0.4 | n |  | TRUE
38 | bus_LV_113-12_0_7_node_22 | 0.4 | n |  | TRUE
39 | bus_LV_113-12_0_7_node_23 | 0.4 | n |  | TRUE
40 | bus_LV_113-12_0_7_node_26 | 0.4 | n |  | TRUE
41 | bus_LV_113-12_0_7_node_24 | 0.4 | n |  | TRUE
42 | bus_LV_113-12_0_7_node_25 | 0.4 | n |  | TRUE
43 | bus_LV_113-12_0_7_node_27 | 0.4 | n |  | TRUE
44 | bus_LV_113-12_0_7_node_28 | 0.4 | n |  | TRUE
45 | bus_LV_113-12_0_7_node_30 | 0.4 | n |  | TRUE
46 | bus_LV_113-12_0_7_node_41 | 0.4 | n |  | TRUE
47 | bus_LV_113-12_0_7_node_43 | 0.4 | n |  | TRUE
48 | bus_LV_113-12_0_7_node_42 | 0.4 | n |  | TRUE
49 | bus_LV_113-12_0_7_node_44 | 0.4 | n |  | TRUE
50 | bus_LV_113-12_0_7_node_48 | 0.4 | n |  | TRUE
51 | bus_LV_113-12_0_7_node_112 | 0.4 | n |  | TRUE
52 | bus_LV_113-12_0_7_node_45 | 0.4 | n |  | TRUE
53 | bus_LV_113-12_0_7_node_118 | 0.4 | n |  | TRUE
54 | bus_LV_113-12_0_7_node_47 | 0.4 | n |  | TRUE
55 | bus_LV_113-12_0_7_node_98 | 0.4 | n |  | TRUE
56 | bus_LV_113-12_0_7_node_97 | 0.4 | n |  | TRUE
57 | bus_LV_113-12_0_7_node_100 | 0.4 | n |  | TRUE
58 | bus_LV_113-12_0_7_node_110 | 0.4 | n |  | TRUE
59 | bus_LV_113-12_0_7_node_128 | 0.4 | n |  | TRUE
60 | bus_LV_113-12_0_7_node_56 | 0.4 | n |  | TRUE
61 | bus_LV_113-12_0_7_node_55 | 0.4 | n |  | TRUE
62 | bus_LV_113-12_0_7_node_95 | 0.4 | n |  | TRUE
63 | bus_LV_113-12_0_7_node_101 | 0.4 | n |  | TRUE
64 | bus_LV_113-12_0_7_node_49 | 0.4 | n |  | TRUE
65 | bus_LV_113-12_0_7_node_50 | 0.4 | n |  | TRUE
66 | bus_LV_113-12_0_7_node_51 | 0.4 | n |  | TRUE
67 | bus_LV_113-12_0_7_node_52 | 0.4 | n |  | TRUE
68 | bus_LV_113-12_0_7_node_53 | 0.4 | n |  | TRUE
69 | bus_LV_113-12_0_7_node_54 | 0.4 | n |  | TRUE
70 | bus_LV_113-12_0_7_node_57 | 0.4 | n |  | TRUE
71 | bus_LV_113-12_0_7_node_114 | 0.4 | n |  | TRUE
72 | bus_LV_113-12_0_7_node_58 | 0.4 | n |  | TRUE
73 | bus_LV_113-12_0_7_node_115 | 0.4 | n |  | TRUE
74 | bus_LV_113-12_0_7_node_107 | 0.4 | n |  | TRUE
75 | bus_LV_113-12_0_7_node_63 | 0.4 | n |  | TRUE
76 | bus_LV_113-12_0_7_node_64 | 0.4 | n |  | TRUE
77 | bus_LV_113-12_0_7_node_65 | 0.4 | n |  | TRUE
78 | bus_LV_113-12_0_7_node_66 | 0.4 | n |  | TRUE
79 | bus_LV_113-12_0_7_node_67 | 0.4 | n |  | TRUE
80 | bus_LV_113-12_0_7_node_68 | 0.4 | n |  | TRUE
81 | bus_LV_113-12_0_7_node_70 | 0.4 | n |  | TRUE
82 | bus_LV_113-12_0_7_node_123 | 0.4 | n |  | TRUE
83 | bus_LV_113-12_0_7_node_69 | 0.4 | n |  | TRUE
84 | bus_LV_113-12_0_7_node_124 | 0.4 | n |  | TRUE
85 | bus_LV_113-12_0_7_node_71 | 0.4 | n |  | TRUE
86 | bus_LV_113-12_0_7_node_72 | 0.4 | n |  | TRUE
87 | bus_LV_113-12_0_7_node_117 | 0.4 | n |  | TRUE
88 | bus_LV_113-12_0_7_node_73 | 0.4 | n |  | TRUE
89 | bus_LV_113-12_0_7_node_88 | 0.4 | n |  | TRUE
90 | bus_LV_113-12_0_7_node_120 | 0.4 | n |  | TRUE
91 | bus_LV_113-12_0_7_node_108 | 0.4 | n |  | TRUE
92 | bus_LV_113-12_0_7_node_86 | 0.4 | n |  | TRUE
93 | bus_LV_113-12_0_7_node_85 | 0.4 | n |  | TRUE
94 | bus_LV_113-12_0_7_node_74 | 0.4 | n |  | TRUE
95 | bus_LV_113-12_0_7_node_75 | 0.4 | n |  | TRUE
96 | bus_LV_113-12_0_7_node_76 | 0.4 | n |  | TRUE
97 | bus_LV_113-12_0_7_node_77 | 0.4 | n |  | TRUE
98 | bus_LV_113-12_0_7_node_78 | 0.4 | n |  | TRUE
99 | bus_LV_113-12_0_7_node_79 | 0.4 | n |  | TRUE
100 | bus_LV_113-12_0_7_node_84 | 0.4 | n |  | TRUE
101 | bus_LV_113-12_0_7_node_121 | 0.4 | n |  | TRUE
102 | bus_LV_113-12_0_7_node_125 | 0.4 | n |  | TRUE
103 | bus_LV_113-12_0_7_node_82 | 0.4 | n |  | TRUE
104 | bus_LV_113-12_0_7_node_122 | 0.4 | n |  | TRUE
105 | bus_LV_113-12_0_7_node_80 | 0.4 | n |  | TRUE
106 | bus_LV_113-12_0_7_node_81 | 0.4 | n |  | TRUE
107 | bus_LV_113-12_0_7_node_83 | 0.4 | n |  | TRUE
108 | bus_LV_113-12_0_7_node_87 | 0.4 | n |  | TRUE
109 | bus_LV_113-12_0_7_node_89 | 0.4 | n |  | TRUE
110 | bus_LV_113-12_0_7_node_90 | 0.4 | n |  | TRUE
111 | bus_LV_113-12_0_7_node_92 | 0.4 | n |  | TRUE
112 | bus_LV_113-12_0_7_node_91 | 0.4 | n |  | TRUE
113 | bus_LV_113-12_0_7_node_93 | 0.4 | n |  | TRUE
114 | bus_LV_113-12_0_7_node_96 | 0.4 | n |  | TRUE
115 | bus_LV_113-12_0_7_node_102 | 0.4 | n |  | TRUE
116 | bus_LV_113-12_0_7_node_126 | 0.4 | n |  | TRUE
117 | bus_LV_113-12_0_7_node_105 | 0.4 | n |  | TRUE
118 | bus_LV_113-12_0_7_node_127 | 0.4 | n |  | TRUE
119 | bus_LV_113-12_0_7_node_103 | 0.4 | n |  | TRUE
120 | bus_LV_113-12_0_7_node_104 | 0.4 | n |  | TRUE
121 | bus_LV_113-12_0_7_node_106 | 0.4 | n |  | TRUE
122 | bus_LV_113-12_0_7_node_109 | 0.4 | n |  | TRUE
123 | bus_LV_113-12_0_7_node_111 | 0.4 | n |  | TRUE
124 | bus_LV_113-12_0_7_node_113 | 0.4 | n |  | TRUE
125 | bus_LV_113-12_0_7_node_116 | 0.4 | n |  | TRUE
126 | bus_MV_8_1_node_152 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_113-12_0_7_load_0 | 0 | 0.00082501 | 0.00020677 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_113-12_0_7_load_3 | 2 | 0.0015411 | 0.00038624 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_113-12_0_7_load_99 | 4 | 0.00044351 | 0.00011115 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_113-12_0_7_load_5 | 7 | 0.001485 | 0.00037217 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_113-12_0_7_load_8 | 8 | 0.0024611 | 0.00061682 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_113-12_0_7_load_119 | 11 | 0.0014456 | 0.0003623 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_113-12_0_7_load_7 | 12 | 0.0012077 | 0.00030268 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_113-12_0_7_load_9 | 14 | 0.00171 | 0.00042857 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_113-12_0_7_load_10 | 15 | 0.0030019 | 0.00075236 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_113-12_0_7_load_11 | 16 | 0.00085783 | 0.00021499 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_113-12_0_7_load_59 | 17 | 0.0022535 | 0.00056478 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_113-12_0_7_load_60 | 18 | 0.0011558 | 0.00028967 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_113-12_0_7_load_61 | 19 | 0.0017655 | 0.00044247 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_113-12_0_7_load_12 | 20 | 0.00083291 | 0.00020875 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_113-12_0_7_load_14 | 22 | 0.003334 | 0.00083557 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_113-12_0_7_load_18 | 23 | 0.00058588 | 0.00014683 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_113-12_0_7_load_37 | 25 | 0.0389 | 0.0097493 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_113-12_0_7_load_36 | 27 | 0.0019068 | 0.00047789 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_113-12_0_7_load_19 | 28 | 0.00080782 | 0.00020246 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_113-12_0_7_load_29 | 30 | 0.001108 | 0.00027768 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_113-12_0_7_load_40 | 31 | 0.052841 | 0.013243 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_113-12_0_7_load_39 | 32 | 0.0023803 | 0.00059656 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_113-12_0_7_load_33 | 34 | 0.091777 | 0.023001 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_113-12_0_7_load_38 | 35 | 0.024859 | 0.0062303 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_113-12_0_7_load_21 | 36 | 0.00053191 | 0.00013331 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_113-12_0_7_load_20 | 37 | 0.001065 | 0.0002669 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_113-12_0_7_load_22 | 38 | 0.00083645 | 0.00020963 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_113-12_0_7_load_23 | 39 | 0.00045732 | 0.00011461 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_113-12_0_7_load_26 | 40 | 0.00058102 | 0.00014562 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_113-12_0_7_load_24 | 41 | 0.0055839 | 0.0013995 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_113-12_0_7_load_25 | 42 | 0.0023067 | 0.00057813 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_113-12_0_7_load_27 | 43 | 0.0023786 | 0.00059614 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_113-12_0_7_load_30 | 45 | 0.0064423 | 0.0016146 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_113-12_0_7_load_41 | 46 | 0.0019439 | 0.00048718 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_113-12_0_7_load_44 | 49 | 0.0017029 | 0.00042678 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_113-12_0_7_load_48 | 50 | 0.0017539 | 0.00043957 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_113-12_0_7_load_112 | 51 | 0.0018083 | 0.00045321 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_113-12_0_7_load_98 | 55 | 0.00070169 | 0.00017586 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_113-12_0_7_load_97 | 56 | 0.0005148 | 0.00012902 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_113-12_0_7_load_100 | 57 | 0.00164 | 0.00041102 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_113-12_0_7_load_110 | 58 | 0.0017048 | 0.00042725 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_113-12_0_7_load_128 | 59 | 0.002246 | 0.0005629 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_113-12_0_7_load_56 | 60 | 0.0016348 | 0.00040973 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_113-12_0_7_load_55 | 61 | 0.0016357 | 0.00040994 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_113-12_0_7_load_95 | 62 | 0.00050715 | 0.0001271 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_113-12_0_7_load_101 | 63 | 0.0016401 | 0.00041105 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_113-12_0_7_load_49 | 64 | 0.0024057 | 0.00060292 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_113-12_0_7_load_50 | 65 | 0.0070098 | 0.0017568 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_113-12_0_7_load_52 | 67 | 0.0019365 | 0.00048532 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_113-12_0_7_load_53 | 68 | 0.0028002 | 0.00070179 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_113-12_0_7_load_54 | 69 | 0.001749 | 0.00043833 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_113-12_0_7_load_57 | 70 | 0.0032488 | 0.00081422 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_113-12_0_7_load_58 | 72 | 0.0068559 | 0.0017182 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_113-12_0_7_load_115 | 73 | 0.001745 | 0.00043734 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_113-12_0_7_load_107 | 74 | 0.0017441 | 0.00043711 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_113-12_0_7_load_63 | 75 | 0.0071237 | 0.0017854 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_113-12_0_7_load_64 | 76 | 0.0013806 | 0.000346 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_113-12_0_7_load_65 | 77 | 0.0014357 | 0.00035982 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_113-12_0_7_load_66 | 78 | 0.0013842 | 0.00034691 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_113-12_0_7_load_67 | 79 | 0.0014384 | 0.0003605 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_113-12_0_7_load_68 | 80 | 0.0013819 | 0.00034633 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_113-12_0_7_load_70 | 81 | 0.0014367 | 0.00036007 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_113-12_0_7_load_123 | 82 | 0.0013842 | 0.00034691 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_113-12_0_7_load_69 | 83 | 0.0014367 | 0.00036007 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_113-12_0_7_load_124 | 84 | 0.0013819 | 0.00034633 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_113-12_0_7_load_72 | 86 | 0.001635 | 0.00040978 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_113-12_0_7_load_117 | 87 | 0.0016327 | 0.00040918 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_113-12_0_7_load_88 | 89 | 0.0014316 | 0.00035878 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_113-12_0_7_load_120 | 90 | 0.0013565 | 0.00033997 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_113-12_0_7_load_108 | 91 | 0.001635 | 0.00040978 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_113-12_0_7_load_86 | 92 | 0.0014332 | 0.00035919 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_113-12_0_7_load_85 | 93 | 0.0013552 | 0.00033964 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_113-12_0_7_load_74 | 94 | 0.0014372 | 0.00036021 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_113-12_0_7_load_75 | 95 | 0.00144 | 0.00036089 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_113-12_0_7_load_77 | 97 | 0.0014404 | 0.000361 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_113-12_0_7_load_78 | 98 | 0.0014372 | 0.00036021 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_113-12_0_7_load_84 | 100 | 0.0014386 | 0.00036055 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_113-12_0_7_load_121 | 101 | 0.0014389 | 0.00036061 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_113-12_0_7_load_125 | 102 | 0.0087509 | 0.0021932 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_113-12_0_7_load_82 | 103 | 0.001439 | 0.00036066 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_113-12_0_7_load_122 | 104 | 0.0028745 | 0.00072042 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_113-12_0_7_load_80 | 105 | 0.0014386 | 0.00036055 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_113-12_0_7_load_81 | 106 | 0.0013565 | 0.00033997 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_113-12_0_7_load_83 | 107 | 0.0013552 | 0.00033964 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_113-12_0_7_load_87 | 108 | 0.0013932 | 0.00034916 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_113-12_0_7_load_89 | 109 | 0.0013934 | 0.00034923 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_113-12_0_7_load_90 | 110 | 0.00044362 | 0.00011118 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_113-12_0_7_load_91 | 112 | 0.0015066 | 0.00037759 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_113-12_0_7_load_126 | 116 | 0.0015058 | 0.00037739 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_113-12_0_7_load_105 | 117 | 0.0016404 | 0.00041112 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_113-12_0_7_load_127 | 118 | 0.001744 | 0.00043708 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_113-12_0_7_load_103 | 119 | 0.0016406 | 0.00041117 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_113-12_0_7_load_104 | 120 | 0.0018292 | 0.00045843 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_113-12_0_7_load_109 | 122 | 0.0017238 | 0.00043202 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_113-12_0_7_load_111 | 123 | 0.0017253 | 0.00043241 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_113-12_0_7_load_113 | 124 | 0.0017037 | 0.00042699 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_113-12_0_7_load_116 | 125 | 0.0017849 | 0.00044733 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 9 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_113-12_0_7_line_0 |  | 0 | 1 | 0.018933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_113-12_0_7_line_1 |  | 1 | 2 | 0.0261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_113-12_0_7_line_2 |  | 1 | 3 | 0.16076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_113-12_0_7_line_3 |  | 2 | 7 | 0.068103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_113-12_0_7_line_4 |  | 3 | 8 | 0.06807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_113-12_0_7_line_5 |  | 4 | 5 | 0.24801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
6 | LV_113-12_0_7_line_6 |  | 4 | 6 | 0.030155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
7 | LV_113-12_0_7_line_7 |  | 5 | 9 | 0.2576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
8 | LV_113-12_0_7_line_8 |  | 5 | 10 | 0.052785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
9 | LV_113-12_0_7_line_9 |  | 6 | 55 | 0.0064713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
10 | LV_113-12_0_7_line_10 |  | 7 | 11 | 0.3069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_113-12_0_7_line_11 |  | 8 | 12 | 0.014231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_113-12_0_7_line_12 |  | 9 | 33 | 0.014064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_113-12_0_7_line_13 |  | 9 | 34 | 0.062657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_113-12_0_7_line_14 |  | 10 | 24 | 0.029569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_113-12_0_7_line_15 |  | 11 | 13 | 0.066948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_113-12_0_7_line_16 |  | 13 | 48 | 0.077163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_113-12_0_7_line_17 |  | 13 | 52 | 0.077566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_113-12_0_7_line_18 |  | 14 | 15 | 0.035679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_113-12_0_7_line_19 |  | 15 | 16 | 0.017683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_113-12_0_7_line_20 |  | 16 | 17 | 0.355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_113-12_0_7_line_21 |  | 17 | 18 | 0.064766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_113-12_0_7_line_22 |  | 17 | 19 | 0.026114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_113-12_0_7_line_23 |  | 18 | 33 | 0.22731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_113-12_0_7_line_24 |  | 20 | 21 | 0.079764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_113-12_0_7_line_25 |  | 21 | 22 | 0.038741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_113-12_0_7_line_26 |  | 22 | 23 | 0.0027057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_113-12_0_7_line_27 |  | 23 | 28 | 0.0013436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_113-12_0_7_line_28 |  | 24 | 25 | 0.014358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_113-12_0_7_line_29 |  | 24 | 26 | 0.12493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_113-12_0_7_line_30 |  | 24 | 27 | 0.042089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_113-12_0_7_line_31 |  | 25 | 35 | 0.003332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_113-12_0_7_line_32 |  | 26 | 29 | 0.12224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_113-12_0_7_line_33 |  | 26 | 30 | 0.032311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_113-12_0_7_line_34 |  | 28 | 36 | 0.0011398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_113-12_0_7_line_35 |  | 29 | 44 | 0.054432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_113-12_0_7_line_36 |  | 30 | 45 | 0.0042931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_113-12_0_7_line_37 |  | 31 | 32 | 0.025946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_113-12_0_7_line_38 |  | 32 | 35 | 0.016391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_113-12_0_7_line_39 |  | 36 | 37 | 0.013048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_113-12_0_7_line_40 |  | 37 | 38 | 0.029813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_113-12_0_7_line_41 |  | 38 | 39 | 0.0010127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_113-12_0_7_line_42 |  | 39 | 40 | 0.00069044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_113-12_0_7_line_43 |  | 40 | 41 | 0.013885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_113-12_0_7_line_44 |  | 41 | 42 | 0.0049849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_113-12_0_7_line_45 |  | 42 | 43 | 0.045951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_113-12_0_7_line_46 |  | 43 | 44 | 0.09197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_113-12_0_7_line_47 |  | 46 | 47 | 0.0035369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_113-12_0_7_line_48 |  | 47 | 50 | 0.017433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_113-12_0_7_line_49 |  | 48 | 49 | 0.012866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_113-12_0_7_line_50 |  | 49 | 51 | 0.0046487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_113-12_0_7_line_51 |  | 50 | 57 | 0.009841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_113-12_0_7_line_52 |  | 51 | 58 | 0.0023951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_113-12_0_7_line_53 |  | 52 | 53 | 0.092975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_113-12_0_7_line_54 |  | 53 | 59 | 0.15574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_113-12_0_7_line_55 |  | 54 | 55 | 0.023199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
56 | LV_113-12_0_7_line_56 |  | 54 | 56 | 0.020022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
57 | LV_113-12_0_7_line_57 |  | 56 | 62 | 0.01007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
58 | LV_113-12_0_7_line_58 |  | 57 | 63 | 0.0070719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_113-12_0_7_line_59 |  | 58 | 122 | 0.007133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_113-12_0_7_line_60 |  | 60 | 61 | 0.0070112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_113-12_0_7_line_61 |  | 61 | 68 | 0.0067558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_113-12_0_7_line_62 |  | 62 | 113 | 0.013093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
63 | LV_113-12_0_7_line_63 |  | 63 | 115 | 0.0082955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_113-12_0_7_line_64 |  | 64 | 65 | 0.012432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_113-12_0_7_line_65 |  | 64 | 66 | 0.023647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_113-12_0_7_line_66 |  | 65 | 67 | 0.011705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_113-12_0_7_line_67 |  | 66 | 68 | 0.0044483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_113-12_0_7_line_68 |  | 66 | 69 | 0.0072374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_113-12_0_7_line_69 |  | 67 | 70 | 0.024948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_113-12_0_7_line_70 |  | 69 | 71 | 0.014739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_113-12_0_7_line_71 |  | 70 | 72 | 0.0082084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_113-12_0_7_line_72 |  | 71 | 73 | 0.012569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_113-12_0_7_line_73 |  | 71 | 74 | 0.0081249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
74 | LV_113-12_0_7_line_74 |  | 73 | 125 | 0.0092523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_113-12_0_7_line_75 |  | 74 | 121 | 0.011093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
76 | LV_113-12_0_7_line_76 |  | 75 | 76 | 0.0094731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_113-12_0_7_line_77 |  | 75 | 77 | 0.0045818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_113-12_0_7_line_78 |  | 76 | 78 | 0.006048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_113-12_0_7_line_79 |  | 77 | 79 | 0.0061088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_113-12_0_7_line_80 |  | 78 | 80 | 0.006048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_113-12_0_7_line_81 |  | 79 | 81 | 0.006108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_113-12_0_7_line_82 |  | 80 | 82 | 0.006048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_113-12_0_7_line_83 |  | 81 | 83 | 0.0061062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_113-12_0_7_line_84 |  | 82 | 84 | 0.006048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_113-12_0_7_line_85 |  | 83 | 85 | 0.019579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_113-12_0_7_line_86 |  | 85 | 86 | 0.017608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_113-12_0_7_line_87 |  | 86 | 87 | 0.0070681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_113-12_0_7_line_88 |  | 87 | 91 | 0.0070681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_113-12_0_7_line_89 |  | 88 | 89 | 0.011003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_113-12_0_7_line_90 |  | 88 | 90 | 0.016432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_113-12_0_7_line_91 |  | 89 | 92 | 0.00035825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_113-12_0_7_line_92 |  | 90 | 93 | 0.0031144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_113-12_0_7_line_93 |  | 91 | 121 | 0.014518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_113-12_0_7_line_94 |  | 92 | 108 | 0.020717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_113-12_0_7_line_95 |  | 93 | 107 | 0.003118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_113-12_0_7_line_96 |  | 94 | 95 | 0.013645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_113-12_0_7_line_97 |  | 94 | 96 | 0.0058184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_113-12_0_7_line_98 |  | 95 | 97 | 0.0046484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_113-12_0_7_line_99 |  | 96 | 98 | 0.0080767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_113-12_0_7_line_100 |  | 96 | 99 | 0.007786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_113-12_0_7_line_101 |  | 97 | 100 | 0.0046484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_113-12_0_7_line_102 |  | 98 | 101 | 0.0060531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_113-12_0_7_line_103 |  | 99 | 102 | 0.032588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_113-12_0_7_line_104 |  | 100 | 103 | 0.0046484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_113-12_0_7_line_105 |  | 101 | 104 | 0.0016389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_113-12_0_7_line_106 |  | 103 | 105 | 0.0046483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_113-12_0_7_line_107 |  | 105 | 106 | 0.015557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_113-12_0_7_line_108 |  | 106 | 107 | 0.0031144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_113-12_0_7_line_109 |  | 108 | 109 | 0.00013642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_113-12_0_7_line_110 |  | 109 | 110 | 0.024959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_113-12_0_7_line_111 |  | 110 | 111 | 0.00070648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_113-12_0_7_line_112 |  | 111 | 112 | 0.021045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_113-12_0_7_line_113 |  | 112 | 113 | 0.00063007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_113-12_0_7_line_114 |  | 113 | 114 | 0.006514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
115 | LV_113-12_0_7_line_115 |  | 114 | 115 | 0.020831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
116 | LV_113-12_0_7_line_116 |  | 114 | 116 | 0.013996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_113-12_0_7_line_117 |  | 115 | 117 | 0.014599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
118 | LV_113-12_0_7_line_118 |  | 116 | 118 | 0.0065442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_113-12_0_7_line_119 |  | 117 | 119 | 0.0066645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
120 | LV_113-12_0_7_line_120 |  | 119 | 120 | 0.0086026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
121 | LV_113-12_0_7_line_121 |  | 120 | 121 | 0.0071753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
122 | LV_113-12_0_7_line_122 |  | 122 | 123 | 0.0071712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_113-12_0_7_line_123 |  | 123 | 124 | 0.01072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_113-12_0_7_line_124 |  | 124 | 125 | 0.010034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_113-12_0_7_trafo_34 | 0.63 MVA 20/0.4 kV | 126 | 9 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27
0 | 2705471.9386 | 1236653.8055 | 2705461.2773 | 1236638.1595
1 | 2705471.9386 | 1236653.8055 | 2705485.1785 | 1236668.1183 | 2705491.5578 | 1236669.8216
2 | 2705606.1037 | 1236565.5881 | 2705488.5525 | 1236637.5325 | 2705471.9386 | 1236653.8055
3 | 2705491.5578 | 1236669.8216 | 2705525.1985 | 1236678.8039 | 2705558.2139 | 1236683.0217
4 | 2705606.1037 | 1236565.5881 | 2705608.8089 | 1236570.9291 | 2705611.0073 | 1236574.5599 | 2705616.5891 | 1236579.0181 | 2705619.7042 | 1236582.1648 | 2705620.8566 | 1236586.7332 | 2705619.7029 | 1236590.7491 | 2705617.2413 | 1236593.8299 | 2705612.1625 | 1236596.4083 | 2705601.8564 | 1236599.7054 | 2705595.4577 | 1236603.7281 | 2705590.1888 | 1236611.4626 | 2705590.1888 | 1236611.4626
5 | 2705192.9785 | 1236847.8414 | 2705200.5335 | 1236848.9983 | 2705202.6668 | 1236845.6335 | 2705204.0001 | 1236843.422 | 2705205.1912 | 1236841.9754 | 2705206.4854 | 1236841.1198 | 2705208.239 | 1236840.8173 | 2705210.3952 | 1236840.8555 | 2705281.3021 | 1236860.7715 | 2705315.7415 | 1236872.0017 | 2705322.5813 | 1236880.1959 | 2705352.1566 | 1236939.0544 | 2705355.4251 | 1236942.0813 | 2705374.2104 | 1236953.4899 | 2705386.5875 | 1236959.093
6 | 2705414.8377 | 1236968.6557 | 2705407.3232 | 1236965.6534 | 2705400.0062 | 1236965.1676 | 2705386.5875 | 1236959.093
7 | 2705126.8741 | 1237025.4962 | 2705135.6415 | 1237028.2646 | 2705155.7344 | 1237034.2137 | 2705165.7737 | 1237031.4004 | 2705173.8518 | 1237024.805 | 2705179.1075 | 1237014.3456 | 2705181.4495 | 1237009.45 | 2705189.3163 | 1236992.9989 | 2705196.6175 | 1236977.7276 | 2705204.3981 | 1236961.4529 | 2705212.0684 | 1236945.4209 | 2705218.531 | 1236930.5017 | 2705227.0685 | 1236909.5257 | 2705228.0068 | 1236906.1175 | 2705228.5597 | 1236902.6802 | 2705228.2299 | 1236898.6602 | 2705227.0578 | 1236895.1923 | 2705224.286 | 1236891.0289 | 2705220.8265 | 1236887.2425 | 2705216.3914 | 1236883.4166 | 2705211.4256 | 1236880.0705 | 2705199.2696 | 1236873.7726 | 2705196.1041 | 1236871.3258 | 2705193.5279 | 1236868.5114 | 2705191.7638 | 1236865.5668 | 2705191.0738 | 1236862.6523 | 2705191.1127 | 1236859.1726 | 2705192.9785 | 1236847.8414
8 | 2705148.756 | 1236829.1997 | 2705159.1505 | 1236829.8509 | 2705171.1785 | 1236831.4206 | 2705176.6174 | 1236834.5526 | 2705180.0114 | 1236835.6357 | 2705182.088 | 1236837.1737 | 2705183.7116 | 1236839.0817 | 2705184.7244 | 1236841.2902 | 2705185.6432 | 1236846.6661 | 2705192.9785 | 1236847.8414
9 | 2705414.8377 | 1236968.6557 | 2705420.5733 | 1236971.6527
10 | 2705476.3354 | 1236978.7996 | 2705558.2139 | 1236683.0217
11 | 2705579.7914 | 1236620.2565 | 2705587.2683 | 1236616.092 | 2705589.2832 | 1236614.2931 | 2705590.1888 | 1236611.4626
12 | 2705126.8741 | 1237025.4962 | 2705122.3849 | 1237038.827
13 | 2705126.8741 | 1237025.4962 | 2705066.7235 | 1237007.9517
14 | 2705119.1382 | 1236827.73 | 2705125.8169 | 1236827.9483 | 2705142.716 | 1236828.8147 | 2705148.756 | 1236829.1997
15 | 2705525.0195 | 1237024.755 | 2705476.3354 | 1236978.7996
16 | 2705525.0195 | 1237024.755 | 2705500.3787 | 1237049.036 | 2705470.8801 | 1237018.3442
17 | 2705525.0195 | 1237024.755 | 2705500.3787 | 1237049.036 | 2705530.1517 | 1237080.022
18 | 2705235.7576 | 1237517.927 | 2705235.0119 | 1237508.5372 | 2705236.4005 | 1237501.0672 | 2705243.3741 | 1237492.7177 | 2705246.5197 | 1237485.5987
19 | 2705246.5197 | 1237485.5987 | 2705249.4681 | 1237478.9262 | 2705259.4663 | 1237476.1054
20 | 2705393.3723 | 1237147.3305 | 2705259.4663 | 1237476.1054
21 | 2705393.3723 | 1237147.3305 | 2705391.7194 | 1237146.7377 | 2705356.6236 | 1237132.0817 | 2705333.7936 | 1237121.9517
22 | 2705393.3723 | 1237147.3305 | 2705410.5412 | 1237153.488 | 2705418.0684 | 1237155.7994
23 | 2705122.3849 | 1237038.827 | 2705142.6747 | 1237045.6246 | 2705211.9253 | 1237070.4809 | 2705255.7839 | 1237087.3375 | 2705333.7936 | 1237121.9517
24 | 2705071.7015 | 1236713.1697 | 2705064.6739 | 1236705.2949 | 2705058.1289 | 1236698.7964 | 2705051.4522 | 1236692.8961 | 2705043.8192 | 1236687.5792 | 2705037.4751 | 1236683.842 | 2705030.5562 | 1236680.0834 | 2705021.7885 | 1236676.0142 | 2705013.6795 | 1236672.7906 | 2705005.9652 | 1236670.1774
25 | 2705071.7015 | 1236713.1697 | 2705049.6175 | 1236731.9935 | 2705046.45 | 1236735.2178 | 2705044.202 | 1236738.2248 | 2705043.4518 | 1236739.4639
26 | 2705042.0503 | 1236741.7783 | 2705043.4518 | 1236739.4639
27 | 2705041.5583 | 1236743.0286 | 2705042.0503 | 1236741.7783 | 2705042.0503 | 1236741.7783
28 | 2705119.1382 | 1236827.73 | 2705118.3041 | 1236842.0642
29 | 2705001.7679 | 1236839.6078 | 2705020.4923 | 1236834.8351 | 2705039.416 | 1236830.344 | 2705056.7858 | 1236827.2822 | 2705076.6215 | 1236824.7199 | 2705093.3375 | 1236823.1033 | 2705119.464 | 1236822.1537 | 2705119.1382 | 1236827.73
30 | 2705119.1382 | 1236827.73 | 2705113.8964 | 1236827.5704 | 2705087.4449 | 1236828.9257 | 2705077.151 | 1236830.0844
31 | 2705118.1105 | 1236845.3905 | 2705118.3041 | 1236842.0642
32 | 2704915.1271 | 1236900.1233 | 2704913.921 | 1236899.0011 | 2704908.3967 | 1236892.1317 | 2704910.7451 | 1236889.8603 | 2704912.2792 | 1236886.9852 | 2704912.8582 | 1236883.7707 | 2704912.4158 | 1236880.5382 | 2704919.6879 | 1236875.4405 | 2704932.2851 | 1236869.2138 | 2704945.3363 | 1236863.4177 | 2704961.6949 | 1236856.7572 | 2704988.6964 | 1236846.9713 | 2704998.8485 | 1236840.3567 | 2705001.7679 | 1236839.6078
33 | 2705001.7679 | 1236839.6078 | 2705000.8232 | 1236835.2544 | 2705001.855 | 1236825.6987 | 2705002.3851 | 1236820.1149 | 2705001.3 | 1236814.2912 | 2704998.4241 | 1236808.2262
34 | 2705041.5583 | 1236743.0286 | 2705041.1409 | 1236744.0893
35 | 2704888.9535 | 1236866.0795 | 2704895.8608 | 1236875.1973 | 2704893.4225 | 1236877.8452 | 2704892.0169 | 1236881.1562 | 2704891.8173 | 1236884.7443 | 2704892.8309 | 1236888.1982 | 2704894.9294 | 1236891.0708 | 2704897.8679 | 1236893.0909 | 2704901.4158 | 1236894.032 | 2704905.077 | 1236893.6964 | 2704908.3967 | 1236892.1317 | 2704913.921 | 1236899.0011 | 2704915.1271 | 1236900.1233
36 | 2704998.4241 | 1236808.2262 | 2704996.5847 | 1236804.3471
37 | 2705117.1583 | 1236861.7543 | 2705142.9176 | 1236864.857
38 | 2705118.1105 | 1236845.3905 | 2705117.1583 | 1236861.7543
39 | 2705039.2494 | 1236756.9088 | 2705039.4997 | 1236755.4771 | 2705039.7083 | 1236749.6763 | 2705040.4337 | 1236745.8862 | 2705041.1409 | 1236744.0893
40 | 2705039.2494 | 1236756.9088 | 2705038.8681 | 1236759.0909 | 2705037.5353 | 1236762.5589 | 2705035.7825 | 1236765.3856 | 2705033.335 | 1236768.1222 | 2705030.4613 | 1236770.5621 | 2705023.1245 | 1236774.6022 | 2705018.8944 | 1236776.7412
41 | 2705017.9906 | 1236777.1981 | 2705018.8944 | 1236776.7412
42 | 2705017.9906 | 1236777.1981 | 2705017.3745 | 1236777.5097
43 | 2705004.9946 | 1236783.7981 | 2705010.8223 | 1236780.8228 | 2705017.3745 | 1236777.5097
44 | 2705004.9946 | 1236783.7981 | 2705000.5549 | 1236786.0648
45 | 2705000.5549 | 1236786.0648 | 2704973.5842 | 1236799.8348 | 2704962.741 | 1236806.5817 | 2704960.3606 | 1236808.2339
46 | 2704888.9535 | 1236866.0795 | 2704896.2167 | 1236858.9134 | 2704947.2022 | 1236817.8046 | 2704955.5234 | 1236811.5913 | 2704960.3606 | 1236808.2339
47 | 2705455.9823 | 1237002.8344 | 2705458.4324 | 1237005.3852
48 | 2705455.9823 | 1237002.8344 | 2705447.9402 | 1237010.3641 | 2705442.3301 | 1237013.4769
49 | 2705470.8801 | 1237018.3442 | 2705461.733 | 1237026.7327 | 2705461.3388 | 1237026.9598
50 | 2705457.3108 | 1237029.2805 | 2705461.3388 | 1237026.9598
51 | 2705442.3301 | 1237013.4769 | 2705433.7249 | 1237018.2515
52 | 2705457.3108 | 1237029.2805 | 2705455.2354 | 1237030.4762
53 | 2705530.1517 | 1237080.022 | 2705561.5046 | 1237113.2157 | 2705594.4325 | 1237147.1937
54 | 2705594.4325 | 1237147.1937 | 2705554.7932 | 1237145.9215 | 2705517.0488 | 1237147.4632 | 2705480.9181 | 1237145.4978 | 2705445.1106 | 1237138.5456 | 2705439.1056 | 1237139.6176
55 | 2705439.0334 | 1236985.1978 | 2705431.5138 | 1236977.3695 | 2705420.5733 | 1236971.6527
56 | 2705439.0334 | 1236985.1978 | 2705430.2592 | 1236995.172 | 2705424.3871 | 1236998.4754
57 | 2705415.611 | 1237003.4125 | 2705424.3871 | 1236998.4754
58 | 2705433.7249 | 1237018.2515 | 2705427.5412 | 1237021.6826
59 | 2705449.0549 | 1237034.0372 | 2705455.2354 | 1237030.4762
60 | 2705451.3112 | 1237077.6617 | 2705444.3018 | 1237077.8165
61 | 2705437.5477 | 1237077.9656 | 2705444.3018 | 1237077.8165
62 | 2705404.2003 | 1237009.8319 | 2705415.611 | 1237003.4125
63 | 2705420.2874 | 1237025.7073 | 2705427.5412 | 1237021.6826
64 | 2705409.8097 | 1237082.1184 | 2705397.6646 | 1237084.7759
65 | 2705433.1005 | 1237078.0638 | 2705414.8781 | 1237081.0093 | 2705409.8097 | 1237082.1184
66 | 2705386.2298 | 1237087.278 | 2705397.6646 | 1237084.7759
67 | 2705433.1005 | 1237078.0638 | 2705437.5477 | 1237077.9656
68 | 2705433.1005 | 1237078.0638 | 2705427.7209 | 1237073.2223
69 | 2705386.2298 | 1237087.278 | 2705361.8589 | 1237092.6108
70 | 2705416.7656 | 1237063.3626 | 2705427.7209 | 1237073.2223
71 | 2705361.8589 | 1237092.6108 | 2705353.8403 | 1237094.3654
72 | 2705416.7656 | 1237063.3626 | 2705423.7487 | 1237056.2255 | 2705426.003 | 1237054.9622
73 | 2705416.7656 | 1237063.3626 | 2705410.7252 | 1237057.9287
74 | 2705434.0744 | 1237050.439 | 2705426.003 | 1237054.9622
75 | 2705401.9491 | 1237051.3683 | 2705404.5721 | 1237052.3934 | 2705410.7252 | 1237057.9287
76 | 2705316.2146 | 1237068.4163 | 2705312.2201 | 1237068.3454 | 2705308.6282 | 1237068.6153 | 2705306.8004 | 1237069.0377
77 | 2705316.2146 | 1237068.4163 | 2705316.2146 | 1237068.4163 | 2705320.6876 | 1237067.4241
78 | 2705306.8004 | 1237069.0377 | 2705300.9078 | 1237070.3994
79 | 2705326.6514 | 1237066.1012 | 2705320.6876 | 1237067.4241
80 | 2705300.9078 | 1237070.3994 | 2705295.0151 | 1237071.7612
81 | 2705332.6144 | 1237064.7785 | 2705326.6514 | 1237066.1012
82 | 2705295.0151 | 1237071.7612 | 2705289.1224 | 1237073.1229
83 | 2705338.5757 | 1237063.4562 | 2705332.6144 | 1237064.7785
84 | 2705289.1224 | 1237073.1229 | 2705283.2298 | 1237074.4847
85 | 2705357.3135 | 1237061.2396 | 2705346.0303 | 1237064.2084 | 2705342.5327 | 1237062.5785 | 2705338.5757 | 1237063.4562
86 | 2705357.3135 | 1237061.2396 | 2705374.3444 | 1237056.7704
87 | 2705374.3444 | 1237056.7704 | 2705381.1811 | 1237054.9764
88 | 2705388.0178 | 1237053.1823 | 2705381.1811 | 1237054.9764
89 | 2705353.2993 | 1237032.8577 | 2705360.9126 | 1237024.9138
90 | 2705353.2993 | 1237032.8577 | 2705337.3034 | 1237036.6175
91 | 2705360.9126 | 1237024.9138 | 2705361.1604 | 1237024.6552
92 | 2705337.3034 | 1237036.6175 | 2705334.2717 | 1237037.3301
93 | 2705401.9491 | 1237051.3683 | 2705399.146 | 1237050.2621 | 2705388.0178 | 1237053.1823
94 | 2705361.1604 | 1237024.6552 | 2705375.4951 | 1237009.6979
95 | 2705334.2717 | 1237037.3301 | 2705331.2364 | 1237038.0436
96 | 2705281.6772 | 1237049.6923 | 2705294.9599 | 1237046.5703
97 | 2705276.0131 | 1237051.0237 | 2705281.6772 | 1237049.6923
98 | 2705299.485 | 1237045.5067 | 2705294.9599 | 1237046.5703
99 | 2705276.0131 | 1237051.0237 | 2705269.1702 | 1237046.7332
100 | 2705272.5745 | 1237058.0125 | 2705276.0131 | 1237051.0237
101 | 2705304.01 | 1237044.4431 | 2705299.485 | 1237045.5067
102 | 2705269.1702 | 1237046.7332 | 2705264.0418 | 1237043.5177
103 | 2705272.5745 | 1237058.0125 | 2705265.0798 | 1237072.2462 | 2705250.1858 | 1237065.0323
104 | 2705308.535 | 1237043.3795 | 2705304.01 | 1237044.4431
105 | 2705262.6533 | 1237042.6472 | 2705264.0418 | 1237043.5177
106 | 2705313.0601 | 1237042.3159 | 2705308.535 | 1237043.3795
107 | 2705313.0601 | 1237042.3159 | 2705328.2046 | 1237038.7562
108 | 2705328.2046 | 1237038.7562 | 2705331.2364 | 1237038.0436
109 | 2705375.4951 | 1237009.6979 | 2705375.5895 | 1237009.5994
110 | 2705392.8594 | 1236991.5794 | 2705375.5895 | 1237009.5994
111 | 2705392.8594 | 1236991.5794 | 2705393.3482 | 1236991.0694
112 | 2705393.3482 | 1236991.0694 | 2705403.8848 | 1237009.2865
113 | 2705404.2003 | 1237009.8319 | 2705403.8848 | 1237009.2865
114 | 2705407.4678 | 1237015.472 | 2705404.2003 | 1237009.8319
115 | 2705407.4678 | 1237015.472 | 2705412.9401 | 1237012.8671 | 2705420.2874 | 1237025.7073
116 | 2705407.4678 | 1237015.472 | 2705395.5241 | 1237022.7677
117 | 2705420.2874 | 1237025.7073 | 2705423.4581 | 1237031.2567 | 2705416.3603 | 1237035.3772
118 | 2705390.5605 | 1237027.0253 | 2705395.2265 | 1237022.9494 | 2705395.5241 | 1237022.7677
119 | 2705410.5966 | 1237038.7231 | 2705416.3603 | 1237035.3772
120 | 2705410.5966 | 1237038.7231 | 2705410.5966 | 1237038.7231 | 2705404.615 | 1237044.9058
121 | 2705401.9491 | 1237051.3683 | 2705402.4908 | 1237048.5646 | 2705403.373 | 1237046.1896 | 2705404.615 | 1237044.9058
122 | 2705449.0549 | 1237034.0372 | 2705442.8412 | 1237037.6173
123 | 2705442.8277 | 1237045.5337 | 2705442.8277 | 1237045.5337 | 2705439.4907 | 1237039.5477 | 2705442.8412 | 1237037.6173
124 | 2705434.0744 | 1237050.439 | 2705442.8277 | 1237045.5337

## bus_geodata
| x | y | coords
0 | 2705461.2773 | 1236638.1595
1 | 2705471.9386 | 1236653.8055
2 | 2705491.5578 | 1236669.8216
3 | 2705606.1037 | 1236565.5881
4 | 2705386.5875 | 1236959.093
5 | 2705192.9785 | 1236847.8414
6 | 2705414.8377 | 1236968.6557
7 | 2705558.2139 | 1236683.0217
8 | 2705590.1888 | 1236611.4626
9 | 2705126.8741 | 1237025.4962
10 | 2705148.756 | 1236829.1997
11 | 2705476.3354 | 1236978.7996
12 | 2705579.7914 | 1236620.2565
13 | 2705525.0195 | 1237024.755
14 | 2705235.7576 | 1237517.927
15 | 2705246.5197 | 1237485.5987
16 | 2705259.4663 | 1237476.1054
17 | 2705393.3723 | 1237147.3305
18 | 2705333.7936 | 1237121.9517
19 | 2705418.0684 | 1237155.7994
20 | 2705005.9652 | 1236670.1774
21 | 2705071.7015 | 1236713.1697
22 | 2705043.4518 | 1236739.4639
23 | 2705042.0503 | 1236741.7783
24 | 2705119.1382 | 1236827.73
25 | 2705118.3041 | 1236842.0642
26 | 2705001.7679 | 1236839.6078
27 | 2705077.151 | 1236830.0844
28 | 2705041.5583 | 1236743.0286
29 | 2704915.1271 | 1236900.1233
30 | 2704998.4241 | 1236808.2262
31 | 2705142.9176 | 1236864.857
32 | 2705117.1583 | 1236861.7543
33 | 2705122.3849 | 1237038.827
34 | 2705066.7235 | 1237007.9517
35 | 2705118.1105 | 1236845.3905
36 | 2705041.1409 | 1236744.0893
37 | 2705039.2494 | 1236756.9088
38 | 2705018.8943 | 1236776.7412
39 | 2705017.9906 | 1236777.1981
40 | 2705017.3745 | 1236777.5097
41 | 2705004.9946 | 1236783.7981
42 | 2705000.5549 | 1236786.0649
43 | 2704960.3606 | 1236808.2339
44 | 2704888.9535 | 1236866.0795
45 | 2704996.5847 | 1236804.3471
46 | 2705458.4324 | 1237005.3852
47 | 2705455.9823 | 1237002.8344
48 | 2705470.8801 | 1237018.3442
49 | 2705461.3388 | 1237026.9598
50 | 2705442.3301 | 1237013.4769
51 | 2705457.3108 | 1237029.2805
52 | 2705530.1517 | 1237080.022
53 | 2705594.4325 | 1237147.1937
54 | 2705439.0334 | 1236985.1978
55 | 2705420.5733 | 1236971.6527
56 | 2705424.3871 | 1236998.4754
57 | 2705433.7249 | 1237018.2515
58 | 2705455.2354 | 1237030.4762
59 | 2705439.1056 | 1237139.6176
60 | 2705451.3113 | 1237077.6617
61 | 2705444.3018 | 1237077.8165
62 | 2705415.611 | 1237003.4125
63 | 2705427.5412 | 1237021.6826
64 | 2705409.8097 | 1237082.1184
65 | 2705397.6646 | 1237084.7759
66 | 2705433.1005 | 1237078.0638
67 | 2705386.2298 | 1237087.278
68 | 2705437.5477 | 1237077.9656
69 | 2705427.7209 | 1237073.2223
70 | 2705361.8589 | 1237092.6108
71 | 2705416.7656 | 1237063.3626
72 | 2705353.8403 | 1237094.3654
73 | 2705426.003 | 1237054.9622
74 | 2705410.7252 | 1237057.9287
75 | 2705316.2146 | 1237068.4163
76 | 2705306.8004 | 1237069.0377
77 | 2705320.6876 | 1237067.4241
78 | 2705300.9078 | 1237070.3994
79 | 2705326.6514 | 1237066.1012
80 | 2705295.0151 | 1237071.7612
81 | 2705332.6144 | 1237064.7785
82 | 2705289.1224 | 1237073.1229
83 | 2705338.5757 | 1237063.4562
84 | 2705283.2298 | 1237074.4847
85 | 2705357.3135 | 1237061.2396
86 | 2705374.3444 | 1237056.7704
87 | 2705381.1811 | 1237054.9764
88 | 2705353.2993 | 1237032.8577
89 | 2705360.9126 | 1237024.9138
90 | 2705337.3034 | 1237036.6175
91 | 2705388.0178 | 1237053.1823
92 | 2705361.1604 | 1237024.6552
93 | 2705334.2717 | 1237037.3301
94 | 2705281.6772 | 1237049.6923
95 | 2705294.9599 | 1237046.5703
96 | 2705276.0131 | 1237051.0237
97 | 2705299.485 | 1237045.5067
98 | 2705269.1702 | 1237046.7332
99 | 2705272.5745 | 1237058.0125
100 | 2705304.01 | 1237044.4431
101 | 2705264.0418 | 1237043.5177
102 | 2705250.1858 | 1237065.0323
103 | 2705308.535 | 1237043.3795
104 | 2705262.6533 | 1237042.6472
105 | 2705313.0601 | 1237042.3159
106 | 2705328.2046 | 1237038.7562
107 | 2705331.2364 | 1237038.0435
108 | 2705375.4951 | 1237009.6979
109 | 2705375.5895 | 1237009.5994
110 | 2705392.8594 | 1236991.5794
111 | 2705393.3482 | 1236991.0694
112 | 2705403.8848 | 1237009.2865
113 | 2705404.2003 | 1237009.8319
114 | 2705407.4678 | 1237015.472
115 | 2705420.2874 | 1237025.7073
116 | 2705395.5241 | 1237022.7677
117 | 2705416.3603 | 1237035.3772
118 | 2705390.5605 | 1237027.0253
119 | 2705410.5966 | 1237038.7231
120 | 2705404.615 | 1237044.9058
121 | 2705401.9491 | 1237051.3683
122 | 2705449.0549 | 1237034.0372
123 | 2705442.8412 | 1237037.6173
124 | 2705442.8277 | 1237045.5337
125 | 2705434.0744 | 1237050.439
126 | 2705135.6415 | 1237028.2646

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97097 | -0.56065 | 0.00082501 | 0.00020677
1 | 0.97099 | -0.56036 | 0 | 0
2 | 0.9711 | -0.55819 | 0.0015411 | 0.00038624
3 | 0.97044 | -0.57129 | 0 | 0
4 | 0.98028 | -0.37738 | 0.00044351 | 0.00011115
5 | 0.98649 | -0.25706 | 0 | 0
6 | 0.97953 | -0.39206 | 0 | 0
7 | 0.97148 | -0.55058 | 0.001485 | 0.00037217
8 | 0.9702 | -0.57591 | 0.0024611 | 0.00061682
9 | 1 | 0 | -0.39285 | -0.10047
10 | 0.98505 | -0.28504 | 0 | 0
11 | 0.97364 | -0.50797 | 0.0014456 | 0.0003623
12 | 0.97019 | -0.57623 | 0.0012077 | 0.00030268
13 | 0.9742 | -0.49691 | 0 | 0
14 | 0.99514 | -0.093612 | 0.00171 | 0.00042857
15 | 0.9952 | -0.092538 | 0.0030019 | 0.00075236
16 | 0.99527 | -0.091071 | 0.00085783 | 0.00021499
17 | 0.99707 | -0.056295 | 0.0022535 | 0.00056478
18 | 0.99764 | -0.045396 | 0.0011558 | 0.00028967
19 | 0.99703 | -0.057104 | 0.0017655 | 0.00044247
20 | 0.97377 | -0.50557 | 0.00083291 | 0.00020875
21 | 0.97383 | -0.50434 | 0 | 0
22 | 0.97386 | -0.50375 | 0.003334 | 0.00083557
23 | 0.97387 | -0.50354 | 0.00058588 | 0.00014683
24 | 0.98302 | -0.32436 | 0 | 0
25 | 0.98144 | -0.35523 | 0.0389 | 0.0097493
26 | 0.97991 | -0.38511 | 0 | 0
27 | 0.98295 | -0.32581 | 0.0019068 | 0.00047789
28 | 0.97388 | -0.50342 | 0.00080782 | 0.00020246
29 | 0.97771 | -0.42806 | 0 | 0
30 | 0.97968 | -0.38954 | 0.001108 | 0.00027768
31 | 0.97909 | -0.40135 | 0.052841 | 0.013243
32 | 0.98036 | -0.37646 | 0.0023803 | 0.00059656
33 | 0.99986 | -0.0026402 | 0 | 0
34 | 0.99476 | -0.10076 | 0.091777 | 0.023001
35 | 0.9812 | -0.36006 | 0.024859 | 0.0062303
36 | 0.97389 | -0.50331 | 0.00053191 | 0.00013331
37 | 0.97396 | -0.50184 | 0.001065 | 0.0002669
38 | 0.97416 | -0.49792 | 0.00083645 | 0.00020963
39 | 0.97417 | -0.49777 | 0.00045732 | 0.00011461
40 | 0.97417 | -0.49767 | 0.00058102 | 0.00014562
41 | 0.97429 | -0.49536 | 0.0055839 | 0.0013995
42 | 0.97436 | -0.49402 | 0.0023067 | 0.00057813
43 | 0.97508 | -0.47975 | 0.0023786 | 0.00059614
44 | 0.97673 | -0.44725 | 0 | 0
45 | 0.97965 | -0.39004 | 0.0064423 | 0.0016146
46 | 0.97709 | -0.4399 | 0.0019439 | 0.00048718
47 | 0.9771 | -0.43977 | 0 | 0
48 | 0.975 | -0.48099 | 0 | 0
49 | 0.97514 | -0.47833 | 0.0017029 | 0.00042678
50 | 0.97713 | -0.43915 | 0.0017539 | 0.00043957
51 | 0.97519 | -0.47723 | 0.0018083 | 0.00045321
52 | 0.97403 | -0.50012 | 0 | 0
53 | 0.97384 | -0.50397 | 0 | 0
54 | 0.9788 | -0.40647 | 0 | 0
55 | 0.97937 | -0.39522 | 0.00070169 | 0.00017586
56 | 0.9783 | -0.4162 | 0.0005148 | 0.00012902
57 | 0.97716 | -0.43849 | 0.00164 | 0.00041102
58 | 0.97523 | -0.47658 | 0.0017048 | 0.00042725
59 | 0.97351 | -0.51041 | 0.002246 | 0.0005629
60 | 0.97571 | -0.46706 | 0.0016348 | 0.00040973
61 | 0.97572 | -0.46685 | 0.0016357 | 0.00040994
62 | 0.97805 | -0.42107 | 0.00050715 | 0.0001271
63 | 0.9772 | -0.4378 | 0.0016401 | 0.00041105
64 | 0.97529 | -0.47525 | 0.0024057 | 0.00060292
65 | 0.97507 | -0.47959 | 0.0070098 | 0.0017568
66 | 0.97577 | -0.46596 | 0 | 0
67 | 0.97494 | -0.48218 | 0.0019365 | 0.00048532
68 | 0.97574 | -0.46645 | 0.0028002 | 0.00070179
69 | 0.97595 | -0.46231 | 0.001749 | 0.00043833
70 | 0.97471 | -0.4868 | 0.0032488 | 0.00081422
71 | 0.97635 | -0.45442 | 0 | 0
72 | 0.97466 | -0.48783 | 0.0068559 | 0.0017182
73 | 0.97606 | -0.4602 | 0.001745 | 0.00043734
74 | 0.97656 | -0.45037 | 0.0017441 | 0.00043711
75 | 0.97502 | -0.48073 | 0.0071237 | 0.0017854
76 | 0.97495 | -0.48193 | 0.0013806 | 0.000346
77 | 0.97508 | -0.47955 | 0.0014357 | 0.00035982
78 | 0.97492 | -0.48254 | 0.0013842 | 0.00034691
79 | 0.97516 | -0.47781 | 0.0014384 | 0.0003605
80 | 0.9749 | -0.483 | 0.0013819 | 0.00034633
81 | 0.97526 | -0.47592 | 0.0014367 | 0.00036007
82 | 0.97488 | -0.48331 | 0.0013842 | 0.00034691
83 | 0.97536 | -0.47387 | 0.0014367 | 0.00036007
84 | 0.97488 | -0.48346 | 0.0013819 | 0.00034633
85 | 0.97572 | -0.46677 | 0 | 0
86 | 0.97605 | -0.4604 | 0.001635 | 0.00040978
87 | 0.97619 | -0.45763 | 0.0016327 | 0.00040918
88 | 0.9753 | -0.47512 | 0 | 0
89 | 0.97559 | -0.46936 | 0.0014316 | 0.00035878
90 | 0.97486 | -0.48372 | 0.0013565 | 0.00033997
91 | 0.97634 | -0.45465 | 0.001635 | 0.00040978
92 | 0.9756 | -0.46917 | 0.0014332 | 0.00035919
93 | 0.97478 | -0.48528 | 0.0013552 | 0.00033964
94 | 0.97376 | -0.50543 | 0.0014372 | 0.00036021
95 | 0.97396 | -0.50144 | 0.00144 | 0.00036089
96 | 0.97368 | -0.50698 | 0 | 0
97 | 0.97404 | -0.49995 | 0.0014404 | 0.000361
98 | 0.97364 | -0.50784 | 0.0014372 | 0.00036021
99 | 0.97362 | -0.50824 | 0 | 0
100 | 0.97412 | -0.49834 | 0.0014386 | 0.00036055
101 | 0.97361 | -0.50832 | 0.0014389 | 0.00036061
102 | 0.97335 | -0.51348 | 0.0087509 | 0.0021932
103 | 0.97421 | -0.49661 | 0.001439 | 0.00036066
104 | 0.97361 | -0.50841 | 0.0028745 | 0.00072042
105 | 0.9743 | -0.49476 | 0.0014386 | 0.00036055
106 | 0.97464 | -0.48816 | 0.0013565 | 0.00033997
107 | 0.97471 | -0.48676 | 0.0013552 | 0.00033964
108 | 0.97621 | -0.45725 | 0.0013932 | 0.00034916
109 | 0.97621 | -0.45717 | 0.0013934 | 0.00034923
110 | 0.977 | -0.44156 | 0.00044362 | 0.00011118
111 | 0.97703 | -0.44111 | 0 | 0
112 | 0.97771 | -0.42781 | 0.0015066 | 0.00037759
113 | 0.97773 | -0.42739 | 0 | 0
114 | 0.97761 | -0.42968 | 0 | 0
115 | 0.97725 | -0.43674 | 0 | 0
116 | 0.97757 | -0.43051 | 0.0015058 | 0.00037739
117 | 0.97702 | -0.44132 | 0.0016404 | 0.00041112
118 | 0.97756 | -0.43071 | 0.001744 | 0.00043708
119 | 0.97691 | -0.44338 | 0.0016406 | 0.00041117
120 | 0.97678 | -0.44598 | 0.0018292 | 0.00045843
121 | 0.97667 | -0.4481 | 0 | 0
122 | 0.97534 | -0.47443 | 0.0017238 | 0.00043202
123 | 0.97546 | -0.47204 | 0.0017253 | 0.00043241
124 | 0.97566 | -0.46813 | 0.0017037 | 0.00042699
125 | 0.97586 | -0.46416 | 0.0017849 | 0.00044733
126 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.00082501 | -0.00020677 | 0.00082503 | 0.00020654 | 1.1349e-08 | -2.2692e-07 | 0.0012643 | 0.0012643 | 0.0012643 | 0.97097 | -0.56065 | 0.97099 | -0.56036 | 0.34734
1 | -0.0044966 | -0.0011248 | 0.0044971 | 0.0011248 | 4.6465e-07 | -2.5497e-08 | 0.0068902 | 0.00689 | 0.0068902 | 0.97099 | -0.56036 | 0.9711 | -0.55819 | 1.8929
2 | 0.0036716 | 0.00091824 | -0.0036697 | -0.00091901 | 1.9083e-06 | -7.6601e-07 | 0.0056259 | 0.0056266 | 0.0056266 | 0.97099 | -0.56036 | 0.97044 | -0.57129 | 1.5458
3 | -0.0060382 | -0.001511 | 0.0060403 | 0.0015116 | 2.1858e-06 | 5.56e-07 | 0.0092515 | 0.0092512 | 0.0092515 | 0.9711 | -0.55819 | 0.97148 | -0.55058 | 2.5416
4 | 0.0036697 | 0.00091901 | -0.0036689 | -0.00091933 | 8.0817e-07 | -3.2357e-07 | 0.0056266 | 0.0056269 | 0.0056269 | 0.97044 | -0.57129 | 0.9702 | -0.57591 | 1.5459
5 | -0.13515 | -0.034097 | 0.13593 | 0.034583 | 0.00078341 | 0.00048565 | 0.20523 | 0.20522 | 0.20523 | 0.98028 | -0.37738 | 0.98649 | -0.25706 | 11.2763
6 | 0.1347 | 0.033986 | -0.13461 | -0.033928 | 9.4632e-05 | 5.8665e-05 | 0.20455 | 0.20456 | 0.20456 | 0.98028 | -0.37738 | 0.97953 | -0.39206 | 11.2393
7 | -0.28463 | -0.072212 | 0.2882 | 0.074478 | 0.0035664 | 0.0022658 | 0.42965 | 0.42965 | 0.42965 | 0.98649 | -0.25706 | 1 | 0 | 23.6072
8 | 0.1487 | 0.037629 | -0.1485 | -0.037505 | 0.00019941 | 0.00012425 | 0.22443 | 0.22443 | 0.22443 | 0.98649 | -0.25706 | 0.98505 | -0.28504 | 12.3313
9 | 0.13461 | 0.033928 | -0.13459 | -0.033915 | 2.0308e-05 | 1.259e-05 | 0.20456 | 0.20456 | 0.20456 | 0.97953 | -0.39206 | 0.97937 | -0.39522 | 11.2393
10 | -0.0075253 | -0.0018837 | 0.0075406 | 0.0018897 | 1.5287e-05 | 5.9751e-06 | 0.011526 | 0.011524 | 0.011526 | 0.97148 | -0.55058 | 0.97364 | -0.50797 | 3.1664
11 | 0.0012077 | 0.00030252 | -0.0012077 | -0.00030268 | 1.831e-08 | -1.6402e-07 | 0.0018522 | 0.0018523 | 0.0018523 | 0.9702 | -0.57591 | 0.97019 | -0.57623 | 0.50888
12 | 0.010783 | 0.0027075 | -0.010781 | -0.0027068 | 1.358e-06 | 6.8464e-07 | 0.016046 | 0.016047 | 0.016047 | 1 | 0 | 0.99986 | -0.0026402 | 4.4084
13 | 0.092219 | 0.023284 | -0.091777 | -0.023001 | 0.00044284 | 0.0002826 | 0.13728 | 0.13728 | 0.13728 | 1 | 0 | 0.99476 | -0.10076 | 37.7156
14 | 0.1485 | 0.037505 | -0.14822 | -0.037327 | 0.00027926 | 0.00017797 | 0.22443 | 0.22443 | 0.22443 | 0.98505 | -0.28504 | 0.98302 | -0.32436 | 30.8284
15 | -0.0089862 | -0.002252 | 0.008991 | 0.0022542 | 4.7352e-06 | 2.1974e-06 | 0.013734 | 0.013733 | 0.013734 | 0.97364 | -0.50797 | 0.9742 | -0.49691 | 3.773
16 | -0.011238 | -0.002814 | 0.011247 | 0.0028185 | 8.5254e-06 | 4.4947e-06 | 0.017165 | 0.017165 | 0.017165 | 0.9742 | -0.49691 | 0.975 | -0.48099 | 4.7156
17 | 0.0022474 | 0.00055976 | -0.0022471 | -0.00056051 | 3.4255e-07 | -7.4637e-07 | 0.0034315 | 0.0034319 | 0.0034319 | 0.9742 | -0.49691 | 0.97403 | -0.50012 | 0.94282
18 | -0.00171 | -0.00042857 | 0.0017101 | 0.00042816 | 8.747e-08 | -4.0759e-07 | 0.0025569 | 0.0025568 | 0.0025569 | 0.99514 | -0.093612 | 0.9952 | -0.092538 | 0.70246
19 | -0.004712 | -0.0011805 | 0.0047124 | 0.0011805 | 3.2915e-07 | -1.9136e-08 | 0.0070453 | 0.0070452 | 0.0070453 | 0.9952 | -0.092538 | 0.99527 | -0.091071 | 1.9355
20 | -0.0055702 | -0.0013955 | 0.0055794 | 0.0013968 | 9.2305e-06 | 1.2857e-06 | 0.0083277 | 0.0083261 | 0.0083277 | 0.99527 | -0.091071 | 0.99707 | -0.056295 | 2.2878
21 | -0.0095985 | -0.0024037 | 0.0096035 | 0.0024061 | 4.983e-06 | 2.3439e-06 | 0.014324 | 0.014324 | 0.014324 | 0.99707 | -0.056295 | 0.99764 | -0.045396 | 3.9351
22 | 0.0017656 | 0.00044218 | -0.0017655 | -0.00044247 | 6.7984e-08 | -2.9707e-07 | 0.0026348 | 0.0026349 | 0.0026349 | 0.99707 | -0.056295 | 0.99703 | -0.057104 | 0.72387
23 | -0.010759 | -0.0026957 | 0.010781 | 0.0027068 | 2.195e-05 | 1.1073e-05 | 0.016048 | 0.016047 | 0.016048 | 0.99764 | -0.045396 | 0.99986 | -0.0026402 | 4.4087
24 | -0.00083291 | -0.00020875 | 0.00083296 | 0.00020779 | 4.8442e-08 | -9.6134e-07 | 0.0012728 | 0.0012724 | 0.0012728 | 0.97377 | -0.50557 | 0.97383 | -0.50434 | 0.34966
25 | -0.00083296 | -0.00020779 | 0.00083298 | 0.00020732 | 2.3518e-08 | -4.6696e-07 | 0.0012724 | 0.0012722 | 0.0012724 | 0.97383 | -0.50434 | 0.97386 | -0.50375 | 0.34956
26 | -0.0041669 | -0.0010429 | 0.004167 | 0.0010429 | 4.1123e-08 | -7.3468e-09 | 0.0063664 | 0.0063663 | 0.0063664 | 0.97386 | -0.50375 | 0.97387 | -0.50354 | 1.749
27 | -0.0047529 | -0.0011897 | 0.0047529 | 0.0011897 | 2.6569e-08 | 2.8521e-10 | 0.0072615 | 0.0072615 | 0.0072615 | 0.97387 | -0.50354 | 0.97388 | -0.50342 | 1.9949
28 | 0.11928 | 0.030011 | -0.11911 | -0.029899 | 0.00017562 | 0.00011221 | 0.1806 | 0.1806 | 0.1806 | 0.98302 | -0.32436 | 0.98144 | -0.35523 | 49.615
29 | 0.027035 | 0.0068387 | -0.026957 | -0.00679 | 7.8549e-05 | 4.8692e-05 | 0.040946 | 0.040946 | 0.040946 | 0.98302 | -0.32436 | 0.97991 | -0.38511 | 11.249
30 | 0.0019069 | 0.00047744 | -0.0019068 | -0.00047789 | 1.315e-07 | -4.4939e-07 | 0.0028864 | 0.0028866 | 0.0028866 | 0.98302 | -0.32436 | 0.98295 | -0.32581 | 0.79302
31 | 0.080205 | 0.020149 | -0.080187 | -0.020137 | 1.8482e-05 | 1.1786e-05 | 0.12162 | 0.12162 | 0.12162 | 0.98144 | -0.35523 | 0.9812 | -0.36006 | 33.4122
32 | 0.019405 | 0.0048971 | -0.019365 | -0.0048731 | 3.9836e-05 | 2.3959e-05 | 0.029478 | 0.029479 | 0.029479 | 0.97991 | -0.38511 | 0.97771 | -0.42806 | 8.0986
33 | 0.007552 | 0.0018929 | -0.0075504 | -0.0018923 | 1.5935e-06 | 6.1293e-07 | 0.011468 | 0.011468 | 0.011468 | 0.97991 | -0.38511 | 0.97968 | -0.38954 | 3.1506
34 | -0.0055607 | -0.0013922 | 0.0055607 | 0.0013922 | 3.0851e-08 | 5.5623e-09 | 0.0084958 | 0.0084958 | 0.0084958 | 0.97388 | -0.50342 | 0.97389 | -0.50331 | 2.334
35 | 0.019365 | 0.0048731 | -0.019347 | -0.0048624 | 1.7738e-05 | 1.0671e-05 | 0.029479 | 0.029479 | 0.029479 | 0.97771 | -0.42806 | 0.97673 | -0.44725 | 8.0987
36 | 0.0064424 | 0.0016146 | -0.0064423 | -0.0016146 | 1.5415e-07 | 4.4603e-08 | 0.0097853 | 0.0097853 | 0.0097853 | 0.97968 | -0.38954 | 0.97965 | -0.39004 | 2.6883
37 | -0.052841 | -0.013243 | 0.052904 | 0.013283 | 6.275e-05 | 3.9833e-05 | 0.080308 | 0.080308 | 0.080308 | 0.97909 | -0.40135 | 0.98036 | -0.37646 | 22.0627
38 | -0.055284 | -0.01388 | 0.055328 | 0.013907 | 4.329e-05 | 2.7499e-05 | 0.083921 | 0.083921 | 0.083921 | 0.98036 | -0.37646 | 0.9812 | -0.36006 | 23.0552
39 | -0.0060926 | -0.0015255 | 0.0060931 | 0.0015256 | 4.2397e-07 | 1.0897e-07 | 0.0093085 | 0.0093085 | 0.0093085 | 0.97389 | -0.50331 | 0.97396 | -0.50184 | 2.5573
40 | -0.007158 | -0.0017925 | 0.0071594 | 0.001793 | 1.337e-06 | 4.8455e-07 | 0.010935 | 0.010935 | 0.010935 | 0.97396 | -0.50184 | 0.97416 | -0.49792 | 3.0043
41 | -0.0079958 | -0.0020026 | 0.0079959 | 0.0020026 | 5.6645e-08 | 2.3644e-08 | 0.012213 | 0.012213 | 0.012213 | 0.97416 | -0.49792 | 0.97417 | -0.49777 | 3.3552
42 | -0.0084532 | -0.0021173 | 0.0084532 | 0.0021173 | 4.3163e-08 | 1.9028e-08 | 0.012912 | 0.012912 | 0.012912 | 0.97417 | -0.49777 | 0.97417 | -0.49767 | 3.5471
43 | -0.0090342 | -0.0022629 | 0.0090352 | 0.0022634 | 9.9149e-07 | 4.6165e-07 | 0.013799 | 0.013799 | 0.013799 | 0.97417 | -0.49767 | 0.97429 | -0.49536 | 3.7909
44 | -0.014619 | -0.0036628 | 0.01462 | 0.0036634 | 9.3187e-07 | 5.3432e-07 | 0.022327 | 0.022327 | 0.022327 | 0.97429 | -0.49536 | 0.97436 | -0.49402 | 6.1339
45 | -0.016927 | -0.0042415 | 0.016938 | 0.0042483 | 1.1514e-05 | 6.7965e-06 | 0.02585 | 0.02585 | 0.02585 | 0.97436 | -0.49402 | 0.97508 | -0.47975 | 7.1017
46 | -0.019317 | -0.0048444 | 0.019347 | 0.0048624 | 2.9972e-05 | 1.8033e-05 | 0.02948 | 0.029479 | 0.02948 | 0.97508 | -0.47975 | 0.97673 | -0.44725 | 8.0988
47 | -0.0019439 | -0.00048718 | 0.0019439 | 0.00048714 | 1.1623e-08 | -3.6861e-08 | 0.0029603 | 0.0029603 | 0.0029603 | 0.97709 | -0.4399 | 0.9771 | -0.43977 | 0.81328
48 | -0.0019439 | -0.00048714 | 0.0019439 | 0.00048696 | 5.7287e-08 | -1.8169e-07 | 0.0029603 | 0.0029602 | 0.0029603 | 0.9771 | -0.43977 | 0.97713 | -0.43915 | 0.81327
49 | -0.011247 | -0.0028185 | 0.011248 | 0.0028192 | 1.4215e-06 | 7.4927e-07 | 0.017165 | 0.017165 | 0.017165 | 0.975 | -0.48099 | 0.97514 | -0.47833 | 4.7155
50 | -0.012951 | -0.003246 | 0.012952 | 0.0032464 | 6.8088e-07 | 3.7777e-07 | 0.019763 | 0.019763 | 0.019763 | 0.97514 | -0.47833 | 0.97519 | -0.47723 | 5.4294
51 | -0.0036979 | -0.00092654 | 0.003698 | 0.00092649 | 1.1702e-07 | -4.8379e-08 | 0.0056312 | 0.0056311 | 0.0056312 | 0.97713 | -0.43915 | 0.97716 | -0.43849 | 1.547
52 | -0.01476 | -0.0036996 | 0.014761 | 0.0036998 | 4.556e-07 | 2.617e-07 | 0.022522 | 0.022522 | 0.022522 | 0.97519 | -0.47723 | 0.97523 | -0.47658 | 6.1874
53 | 0.0022471 | 0.00056051 | -0.0022467 | -0.0005614 | 4.1069e-07 | -8.9417e-07 | 0.0034319 | 0.0034323 | 0.0034323 | 0.97403 | -0.50012 | 0.97384 | -0.50397 | 0.94294
54 | 0.0022467 | 0.0005614 | -0.002246 | -0.0005629 | 6.8816e-07 | -1.4966e-06 | 0.0034323 | 0.003433 | 0.003433 | 0.97384 | -0.50397 | 0.97351 | -0.51041 | 0.94313
55 | -0.13382 | -0.033694 | 0.13389 | 0.033739 | 7.2047e-05 | 4.4651e-05 | 0.20349 | 0.20349 | 0.20349 | 0.9788 | -0.40647 | 0.97937 | -0.39522 | 11.1808
56 | 0.13382 | 0.033694 | -0.13375 | -0.033656 | 6.218e-05 | 3.8537e-05 | 0.20349 | 0.20349 | 0.20349 | 0.9788 | -0.40647 | 0.9783 | -0.4162 | 11.1808
57 | 0.13324 | 0.033527 | -0.13321 | -0.033508 | 3.1032e-05 | 1.9228e-05 | 0.20271 | 0.20271 | 0.20271 | 0.9783 | -0.4162 | 0.97805 | -0.42107 | 11.1378
58 | -0.005338 | -0.0013375 | 0.0053381 | 0.0013375 | 1.7522e-07 | 2.3549e-08 | 0.0081285 | 0.0081285 | 0.0081285 | 0.97716 | -0.43849 | 0.9772 | -0.4378 | 2.2331
59 | -0.016465 | -0.0041271 | 0.016467 | 0.0041281 | 1.6883e-06 | 9.9153e-07 | 0.025123 | 0.025123 | 0.025123 | 0.97523 | -0.47658 | 0.97534 | -0.47443 | 6.902
60 | -0.0016348 | -0.00040973 | 0.0016348 | 0.00040965 | 1.6343e-08 | -7.7109e-08 | 0.0024932 | 0.0024932 | 0.0024932 | 0.97571 | -0.46706 | 0.97572 | -0.46685 | 0.68495
61 | -0.0032705 | -0.00081959 | 0.0032706 | 0.00081955 | 6.3023e-08 | -4.4046e-08 | 0.0049877 | 0.0049876 | 0.0049877 | 0.97572 | -0.46685 | 0.97574 | -0.46645 | 1.3702
62 | 0.1327 | 0.033381 | -0.13266 | -0.033356 | 4.0042e-05 | 2.4805e-05 | 0.20194 | 0.20194 | 0.20194 | 0.97805 | -0.42107 | 0.97773 | -0.42739 | 11.0954
63 | -0.0069782 | -0.0017486 | 0.0069786 | 0.0017487 | 3.5124e-07 | 1.2086e-07 | 0.010626 | 0.010626 | 0.010626 | 0.9772 | -0.4378 | 0.97725 | -0.43674 | 2.9192
64 | 0.019059 | 0.004779 | -0.019055 | -0.0047766 | 3.9424e-06 | 2.368e-06 | 0.029079 | 0.029079 | 0.029079 | 0.97529 | -0.47525 | 0.97507 | -0.47959 | 7.9888
65 | -0.021465 | -0.0053819 | 0.021474 | 0.0053877 | 9.511e-06 | 5.7918e-06 | 0.03275 | 0.03275 | 0.03275 | 0.97529 | -0.47525 | 0.97577 | -0.46596 | 8.9972
66 | 0.012045 | 0.0030198 | -0.012044 | -0.003019 | 1.4832e-06 | 8.0326e-07 | 0.018382 | 0.018382 | 0.018382 | 0.97507 | -0.47959 | 0.97494 | -0.48218 | 5.05
67 | 0.0060709 | 0.0015214 | -0.0060707 | -0.0015213 | 1.4297e-07 | 3.5939e-08 | 0.0092579 | 0.0092579 | 0.0092579 | 0.97577 | -0.46596 | 0.97574 | -0.46645 | 2.5434
68 | -0.027545 | -0.0069091 | 0.02755 | 0.0069121 | 4.7892e-06 | 2.9747e-06 | 0.042007 | 0.042007 | 0.042007 | 0.97577 | -0.46596 | 0.97595 | -0.46231 | 11.5405
69 | 0.010107 | 0.0025337 | -0.010105 | -0.0025326 | 2.2264e-06 | 1.1138e-06 | 0.015426 | 0.015427 | 0.015427 | 0.97494 | -0.48218 | 0.97471 | -0.4868 | 4.2381
70 | -0.029299 | -0.0073504 | 0.02931 | 0.0073573 | 1.1031e-05 | 6.8754e-06 | 0.044674 | 0.044674 | 0.044674 | 0.97595 | -0.46231 | 0.97635 | -0.45442 | 12.2731
71 | 0.0068562 | 0.0017184 | -0.0068559 | -0.0017182 | 3.3723e-07 | 1.1352e-07 | 0.010467 | 0.010467 | 0.010467 | 0.97471 | -0.4868 | 0.97466 | -0.48783 | 2.8755
72 | 0.025171 | 0.0063171 | -0.025164 | -0.0063128 | 6.9377e-06 | 4.283e-06 | 0.038365 | 0.038365 | 0.038365 | 0.97635 | -0.45442 | 0.97606 | -0.4602 | 10.5399
73 | -0.054481 | -0.013674 | 0.054491 | 0.013681 | 1.0505e-05 | 6.5198e-06 | 0.083039 | 0.083039 | 0.083039 | 0.97635 | -0.45442 | 0.97656 | -0.45037 | 11.4065
74 | 0.023419 | 0.0058755 | -0.023415 | -0.0058728 | 4.4232e-06 | 2.7153e-06 | 0.035705 | 0.035705 | 0.035705 | 0.97606 | -0.4602 | 0.97586 | -0.46416 | 9.8091
75 | -0.056235 | -0.014118 | 0.056242 | 0.014121 | 6.1098e-06 | 3.2162e-06 | 0.085697 | 0.085696 | 0.085697 | 0.97656 | -0.45037 | 0.97667 | -0.4481 | 4.7086
76 | 0.0069133 | 0.0017325 | -0.0069129 | -0.0017324 | 3.9544e-07 | 1.3494e-07 | 0.010551 | 0.010551 | 0.010551 | 0.97502 | -0.48073 | 0.97495 | -0.48193 | 2.8986
77 | -0.014037 | -0.0035178 | 0.014038 | 0.0035183 | 7.885e-07 | 4.4749e-07 | 0.021422 | 0.021422 | 0.021422 | 0.97502 | -0.48073 | 0.97508 | -0.47955 | 5.8853
78 | 0.0055324 | 0.0013864 | -0.0055322 | -0.0013863 | 1.617e-07 | 2.8068e-08 | 0.0084437 | 0.0084437 | 0.0084437 | 0.97495 | -0.48193 | 0.97492 | -0.48254 | 2.3197
79 | -0.015473 | -0.0038781 | 0.015475 | 0.0038789 | 1.2773e-06 | 7.4128e-07 | 0.023613 | 0.023613 | 0.023613 | 0.97508 | -0.47955 | 0.97516 | -0.47781 | 6.4872
80 | 0.004148 | 0.0010394 | -0.0041479 | -0.0010394 | 9.0906e-08 | -1.7234e-08 | 0.006331 | 0.0063311 | 0.0063311 | 0.97492 | -0.48254 | 0.9749 | -0.483 | 1.7393
81 | -0.016913 | -0.0042394 | 0.016915 | 0.0042403 | 1.5256e-06 | 9.0018e-07 | 0.025808 | 0.025808 | 0.025808 | 0.97516 | -0.47781 | 0.97526 | -0.47592 | 7.0902
82 | 0.0027661 | 0.00069311 | -0.002766 | -0.00069316 | 4.0426e-08 | -4.9538e-08 | 0.0042219 | 0.0042219 | 0.0042219 | 0.9749 | -0.483 | 0.97488 | -0.48331 | 1.1599
83 | -0.018351 | -0.0046003 | 0.018353 | 0.0046014 | 1.7953e-06 | 1.0728e-06 | 0.028 | 0.028 | 0.028 | 0.97526 | -0.47592 | 0.97536 | -0.47387 | 7.6924
84 | 0.0013819 | 0.00034626 | -0.0013819 | -0.00034633 | 1.009e-08 | -6.8952e-08 | 0.0021092 | 0.0021092 | 0.0021092 | 0.97488 | -0.48331 | 0.97488 | -0.48346 | 0.57946
85 | -0.01979 | -0.0049615 | 0.019797 | 0.0049655 | 6.6928e-06 | 4.039e-06 | 0.030192 | 0.030192 | 0.030192 | 0.97536 | -0.47387 | 0.97572 | -0.46677 | 8.2945
86 | -0.019797 | -0.0049655 | 0.019803 | 0.0049692 | 6.0188e-06 | 3.6321e-06 | 0.030192 | 0.030192 | 0.030192 | 0.97572 | -0.46677 | 0.97605 | -0.4604 | 8.2945
87 | -0.021438 | -0.0053789 | 0.02144 | 0.0053807 | 2.8315e-06 | 1.7238e-06 | 0.032685 | 0.032685 | 0.032685 | 0.97605 | -0.4604 | 0.97619 | -0.45763 | 8.9793
88 | -0.023073 | -0.0057898 | 0.023076 | 0.0057918 | 3.2791e-06 | 2.0103e-06 | 0.035173 | 0.035173 | 0.035173 | 0.97619 | -0.45763 | 0.97634 | -0.45465 | 9.663
89 | -0.028597 | -0.0071801 | 0.028604 | 0.007185 | 7.8561e-06 | 4.8906e-06 | 0.043635 | 0.043635 | 0.043635 | 0.9753 | -0.47512 | 0.97559 | -0.46936 | 11.9876
90 | 0.028597 | 0.0071801 | -0.028585 | -0.0071728 | 1.1732e-05 | 7.3037e-06 | 0.043635 | 0.043635 | 0.043635 | 0.9753 | -0.47512 | 0.97486 | -0.48372 | 11.9876
91 | -0.030036 | -0.0075437 | 0.030036 | 0.0075439 | 2.8203e-07 | 1.7602e-07 | 0.045818 | 0.045818 | 0.045818 | 0.97559 | -0.46936 | 0.9756 | -0.46917 | 12.5874
92 | 0.027228 | 0.0068328 | -0.027226 | -0.0068315 | 2.0176e-06 | 1.2525e-06 | 0.041564 | 0.041564 | 0.041564 | 0.97486 | -0.48372 | 0.97478 | -0.48528 | 11.4188
93 | -0.024711 | -0.0062016 | 0.024719 | 0.0062064 | 7.7238e-06 | 4.7616e-06 | 0.037665 | 0.037665 | 0.037665 | 0.97634 | -0.45465 | 0.97667 | -0.4481 | 10.3476
94 | -0.031469 | -0.0079031 | 0.031487 | 0.0079143 | 1.7903e-05 | 1.1199e-05 | 0.048004 | 0.048004 | 0.048004 | 0.9756 | -0.46917 | 0.97621 | -0.45725 | 13.1879
95 | 0.025871 | 0.0064919 | -0.025869 | -0.0064908 | 1.8239e-06 | 1.1284e-06 | 0.039496 | 0.039496 | 0.039496 | 0.97478 | -0.48528 | 0.97471 | -0.48676 | 10.8504
96 | -0.015943 | -0.0039965 | 0.015946 | 0.0039983 | 3.037e-06 | 1.7739e-06 | 0.024363 | 0.024363 | 0.024363 | 0.97376 | -0.50543 | 0.97396 | -0.50144 | 6.6931
97 | 0.014506 | 0.0036363 | -0.014505 | -0.0036357 | 1.0721e-06 | 6.1376e-07 | 0.022166 | 0.022167 | 0.022167 | 0.97376 | -0.50543 | 0.97368 | -0.50698 | 6.0897
98 | -0.017386 | -0.0043592 | 0.017387 | 0.0043599 | 1.2299e-06 | 7.2929e-07 | 0.026563 | 0.026563 | 0.026563 | 0.97396 | -0.50144 | 0.97404 | -0.49995 | 7.2975
99 | 0.0057509 | 0.0014413 | -0.0057507 | -0.0014412 | 2.3395e-07 | 4.9277e-08 | 0.0087888 | 0.0087888 | 0.0087888 | 0.97368 | -0.50698 | 0.97364 | -0.50784 | 2.4145
100 | 0.0087536 | 0.0021944 | -0.008753 | -0.0021942 | 5.2253e-07 | 2.3759e-07 | 0.013378 | 0.013378 | 0.013378 | 0.97368 | -0.50698 | 0.97362 | -0.50824 | 3.6752
101 | -0.018827 | -0.0047209 | 0.018829 | 0.0047217 | 1.4421e-06 | 8.651e-07 | 0.028763 | 0.028763 | 0.028763 | 0.97404 | -0.49995 | 0.97412 | -0.49834 | 7.902
102 | 0.0043135 | 0.001081 | -0.0043134 | -0.001081 | 9.8647e-08 | -1.2145e-08 | 0.0065923 | 0.0065923 | 0.0065923 | 0.97364 | -0.50784 | 0.97361 | -0.50832 | 1.8111
103 | 0.008753 | 0.0021942 | -0.0087509 | -0.0021932 | 2.1871e-06 | 9.9456e-07 | 0.013378 | 0.013378 | 0.013378 | 0.97362 | -0.50824 | 0.97335 | -0.51348 | 3.6753
104 | -0.020268 | -0.0050823 | 0.020269 | 0.0050833 | 1.6709e-06 | 1.0115e-06 | 0.030961 | 0.030961 | 0.030961 | 0.97412 | -0.49834 | 0.97421 | -0.49661 | 8.5057
105 | 0.0028745 | 0.0007204 | -0.0028745 | -0.00072042 | 1.1862e-08 | -1.279e-08 | 0.0043932 | 0.0043932 | 0.0043932 | 0.97361 | -0.50832 | 0.97361 | -0.50841 | 1.2069
106 | -0.021708 | -0.005444 | 0.02171 | 0.0054451 | 1.9166e-06 | 1.1687e-06 | 0.033159 | 0.033159 | 0.033159 | 0.97421 | -0.49661 | 0.9743 | -0.49476 | 9.1095
107 | -0.023149 | -0.0058057 | 0.023156 | 0.0058102 | 7.2927e-06 | 4.4735e-06 | 0.035356 | 0.035356 | 0.035356 | 0.9743 | -0.49476 | 0.97464 | -0.48816 | 9.7131
108 | -0.024513 | -0.0061501 | 0.024514 | 0.0061511 | 1.6359e-06 | 1.0082e-06 | 0.037427 | 0.037427 | 0.037427 | 0.97464 | -0.48816 | 0.97471 | -0.48676 | 10.2821
109 | -0.032881 | -0.0082635 | 0.032881 | 0.0082635 | 1.2855e-07 | 8.0564e-08 | 0.050128 | 0.050128 | 0.050128 | 0.97621 | -0.45725 | 0.97621 | -0.45717 | 13.7713
110 | -0.034274 | -0.0086128 | 0.0343 | 0.0086288 | 2.5554e-05 | 1.6042e-05 | 0.052252 | 0.052251 | 0.052252 | 0.97621 | -0.45717 | 0.977 | -0.44156 | 14.3548
111 | -0.034743 | -0.00874 | 0.034744 | 0.0087405 | 7.4214e-07 | 4.6612e-07 | 0.052927 | 0.052927 | 0.052927 | 0.977 | -0.44156 | 0.97703 | -0.44111 | 14.5404
112 | -0.034744 | -0.0087405 | 0.034766 | 0.0087543 | 2.2107e-05 | 1.3885e-05 | 0.052927 | 0.052927 | 0.052927 | 0.97703 | -0.44111 | 0.97771 | -0.42781 | 14.5404
113 | -0.036273 | -0.0091319 | 0.036273 | 0.0091324 | 7.2047e-07 | 4.532e-07 | 0.05522 | 0.05522 | 0.05522 | 0.97771 | -0.42781 | 0.97773 | -0.42739 | 15.1703
114 | 0.096387 | 0.024223 | -0.096376 | -0.024217 | 1.0516e-05 | 6.3221e-06 | 0.14672 | 0.14672 | 0.14672 | 0.97773 | -0.42739 | 0.97761 | -0.42968 | 8.0613
115 | 0.093126 | 0.023403 | -0.093095 | -0.023384 | 3.1401e-05 | 1.8791e-05 | 0.14177 | 0.14177 | 0.14177 | 0.97761 | -0.42968 | 0.97725 | -0.43674 | 7.7896
116 | 0.00325 | 0.00081431 | -0.0032498 | -0.00081441 | 1.2843e-07 | -9.3283e-08 | 0.0049467 | 0.0049467 | 0.0049467 | 0.97761 | -0.42968 | 0.97757 | -0.43051 | 1.359
117 | 0.086116 | 0.021635 | -0.086098 | -0.021624 | 1.8831e-05 | 1.1137e-05 | 0.13114 | 0.13114 | 0.13114 | 0.97725 | -0.43674 | 0.97702 | -0.44132 | 7.2058
118 | 0.001744 | 0.00043701 | -0.001744 | -0.00043708 | 1.7294e-08 | -7.0977e-08 | 0.0026546 | 0.0026547 | 0.0026547 | 0.97757 | -0.43051 | 0.97756 | -0.43071 | 0.7293
119 | 0.084457 | 0.021213 | -0.084449 | -0.021208 | 8.2722e-06 | 4.877e-06 | 0.12865 | 0.12865 | 0.12865 | 0.97702 | -0.44132 | 0.97691 | -0.44338 | 7.0685
120 | 0.082808 | 0.020797 | -0.082798 | -0.020791 | 1.0267e-05 | 6.0325e-06 | 0.12615 | 0.12615 | 0.12615 | 0.97691 | -0.44338 | 0.97678 | -0.44598 | 6.9312
121 | 0.080969 | 0.020332 | -0.080961 | -0.020328 | 8.1895e-06 | 4.7923e-06 | 0.12336 | 0.12336 | 0.12336 | 0.97678 | -0.44598 | 0.97667 | -0.4481 | 6.7781
122 | -0.018191 | -0.0045601 | 0.018193 | 0.0045613 | 2.0713e-06 | 1.2361e-06 | 0.027753 | 0.027753 | 0.027753 | 0.97534 | -0.47443 | 0.97546 | -0.47204 | 7.6245
123 | -0.019918 | -0.0049937 | 0.019922 | 0.004996 | 3.7115e-06 | 2.2415e-06 | 0.030385 | 0.030385 | 0.030385 | 0.97546 | -0.47204 | 0.97566 | -0.46813 | 8.3475
124 | -0.021626 | -0.005423 | 0.02163 | 0.0054255 | 4.0936e-06 | 2.4945e-06 | 0.032983 | 0.032983 | 0.032983 | 0.97566 | -0.46813 | 0.97586 | -0.46416 | 9.0614

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.39285 | 0.10047

## res_load
| p_mw | q_mvar
0 | 0.00082501 | 0.00020677
1 | 0.0015411 | 0.00038624
2 | 0.00044351 | 0.00011115
3 | 0.001485 | 0.00037217
4 | 0.0024611 | 0.00061682
5 | 0.0014456 | 0.0003623
6 | 0.0012077 | 0.00030268
7 | 0.00171 | 0.00042857
8 | 0.0030019 | 0.00075236
9 | 0.00085783 | 0.00021499
10 | 0.0022535 | 0.00056478
11 | 0.0011558 | 0.00028967
12 | 0.0017655 | 0.00044247
13 | 0.00083291 | 0.00020875
14 | 0.003334 | 0.00083557
15 | 0.00058588 | 0.00014683
16 | 0.0389 | 0.0097493
17 | 0.0019068 | 0.00047789
18 | 0.00080782 | 0.00020246
19 | 0.001108 | 0.00027768
20 | 0.052841 | 0.013243
21 | 0.0023803 | 0.00059656
22 | 0.091777 | 0.023001
23 | 0.024859 | 0.0062303
24 | 0.00053191 | 0.00013331
25 | 0.001065 | 0.0002669
26 | 0.00083645 | 0.00020963
27 | 0.00045732 | 0.00011461
28 | 0.00058102 | 0.00014562
29 | 0.0055839 | 0.0013995
30 | 0.0023067 | 0.00057813
31 | 0.0023786 | 0.00059614
32 | 0.0064423 | 0.0016146
33 | 0.0019439 | 0.00048718
34 | 0.0017029 | 0.00042678
35 | 0.0017539 | 0.00043957
36 | 0.0018083 | 0.00045321
37 | 0.00070169 | 0.00017586
38 | 0.0005148 | 0.00012902
39 | 0.00164 | 0.00041102
40 | 0.0017048 | 0.00042725
41 | 0.002246 | 0.0005629
42 | 0.0016348 | 0.00040973
43 | 0.0016357 | 0.00040994
44 | 0.00050715 | 0.0001271
45 | 0.0016401 | 0.00041105
46 | 0.0024057 | 0.00060292
47 | 0.0070098 | 0.0017568
48 | 0.0019365 | 0.00048532
49 | 0.0028002 | 0.00070179
50 | 0.001749 | 0.00043833
51 | 0.0032488 | 0.00081422
52 | 0.0068559 | 0.0017182
53 | 0.001745 | 0.00043734
54 | 0.0017441 | 0.00043711
55 | 0.0071237 | 0.0017854
56 | 0.0013806 | 0.000346
57 | 0.0014357 | 0.00035982
58 | 0.0013842 | 0.00034691
59 | 0.0014384 | 0.0003605
60 | 0.0013819 | 0.00034633
61 | 0.0014367 | 0.00036007
62 | 0.0013842 | 0.00034691
63 | 0.0014367 | 0.00036007
64 | 0.0013819 | 0.00034633
65 | 0.001635 | 0.00040978
66 | 0.0016327 | 0.00040918
67 | 0.0014316 | 0.00035878
68 | 0.0013565 | 0.00033997
69 | 0.001635 | 0.00040978
70 | 0.0014332 | 0.00035919
71 | 0.0013552 | 0.00033964
72 | 0.0014372 | 0.00036021
73 | 0.00144 | 0.00036089
74 | 0.0014404 | 0.000361
75 | 0.0014372 | 0.00036021
76 | 0.0014386 | 0.00036055
77 | 0.0014389 | 0.00036061
78 | 0.0087509 | 0.0021932
79 | 0.001439 | 0.00036066
80 | 0.0028745 | 0.00072042
81 | 0.0014386 | 0.00036055
82 | 0.0013565 | 0.00033997
83 | 0.0013552 | 0.00033964
84 | 0.0013932 | 0.00034916
85 | 0.0013934 | 0.00034923
86 | 0.00044362 | 0.00011118
87 | 0.0015066 | 0.00037759
88 | 0.0015058 | 0.00037739
89 | 0.0016404 | 0.00041112
90 | 0.001744 | 0.00043708
91 | 0.0016406 | 0.00041117
92 | 0.0018292 | 0.00045843
93 | 0.0017238 | 0.00043202
94 | 0.0017253 | 0.00043241
95 | 0.0017037 | 0.00042699
96 | 0.0017849 | 0.00044733

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1