## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_113-2_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_113-2_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_113-2_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_113-2_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_113-2_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_113-2_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_113-2_0_4_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_113-2_0_4_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_113-2_0_4_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_113-2_0_4_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_113-2_0_4_node_10 | 0.4 | n |  | TRUE
11 | bus_LV_113-2_0_4_node_72 | 0.4 | n |  | TRUE
12 | bus_LV_113-2_0_4_node_69 | 0.4 | n |  | TRUE
13 | bus_LV_113-2_0_4_node_90 | 0.4 | n |  | TRUE
14 | bus_LV_113-2_0_4_node_91 | 0.4 | n |  | TRUE
15 | bus_LV_113-2_0_4_node_67 | 0.4 | n |  | TRUE
16 | bus_LV_113-2_0_4_node_70 | 0.4 | n |  | TRUE
17 | bus_LV_113-2_0_4_node_74 | 0.4 | n |  | TRUE
18 | bus_LV_113-2_0_4_node_117 | 0.4 | n |  | TRUE
19 | bus_LV_113-2_0_4_node_96 | 0.4 | n |  | TRUE
20 | bus_LV_113-2_0_4_node_89 | 0.4 | n |  | TRUE
21 | bus_LV_113-2_0_4_node_65 | 0.4 | n |  | TRUE
22 | bus_LV_113-2_0_4_node_71 | 0.4 | n |  | TRUE
23 | bus_LV_113-2_0_4_node_11 | 0.4 | n |  | TRUE
24 | bus_LV_113-2_0_4_node_12 | 0.4 | n |  | TRUE
25 | bus_LV_113-2_0_4_node_13 | 0.4 | n |  | TRUE
26 | bus_LV_113-2_0_4_node_15 | 0.4 | n |  | TRUE
27 | bus_LV_113-2_0_4_node_88 | 0.4 | n |  | TRUE
28 | bus_LV_113-2_0_4_node_87 | 0.4 | n |  | TRUE
29 | bus_LV_113-2_0_4_node_16 | 0.4 | n |  | TRUE
30 | bus_LV_113-2_0_4_node_17 | 0.4 | n |  | TRUE
31 | bus_LV_113-2_0_4_node_93 | 0.4 | n |  | TRUE
32 | bus_LV_113-2_0_4_node_68 | 0.4 | n |  | TRUE
33 | bus_LV_113-2_0_4_node_66 | 0.4 | n |  | TRUE
34 | bus_LV_113-2_0_4_node_119 | 0.4 | n |  | TRUE
35 | bus_LV_113-2_0_4_node_18 | 0.4 | n |  | TRUE
36 | bus_LV_113-2_0_4_node_19 | 0.4 | n |  | TRUE
37 | bus_LV_113-2_0_4_node_20 | 0.4 | n |  | TRUE
38 | bus_LV_113-2_0_4_node_124 | 0.4 | n |  | TRUE
39 | bus_LV_113-2_0_4_node_21 | 0.4 | n |  | TRUE
40 | bus_LV_113-2_0_4_node_22 | 0.4 | n |  | TRUE
41 | bus_LV_113-2_0_4_node_23 | 0.4 | n |  | TRUE
42 | bus_LV_113-2_0_4_node_123 | 0.4 | n |  | TRUE
43 | bus_LV_113-2_0_4_node_24 | 0.4 | n |  | TRUE
44 | bus_LV_113-2_0_4_node_85 | 0.4 | n |  | TRUE
45 | bus_LV_113-2_0_4_node_84 | 0.4 | n |  | TRUE
46 | bus_LV_113-2_0_4_node_27 | 0.4 | n |  | TRUE
47 | bus_LV_113-2_0_4_node_28 | 0.4 | n |  | TRUE
48 | bus_LV_113-2_0_4_node_29 | 0.4 | n |  | TRUE
49 | bus_LV_113-2_0_4_node_30 | 0.4 | n |  | TRUE
50 | bus_LV_113-2_0_4_node_31 | 0.4 | n |  | TRUE
51 | bus_LV_113-2_0_4_node_32 | 0.4 | n |  | TRUE
52 | bus_LV_113-2_0_4_node_33 | 0.4 | n |  | TRUE
53 | bus_LV_113-2_0_4_node_35 | 0.4 | n |  | TRUE
54 | bus_LV_113-2_0_4_node_34 | 0.4 | n |  | TRUE
55 | bus_LV_113-2_0_4_node_49 | 0.4 | n |  | TRUE
56 | bus_LV_113-2_0_4_node_59 | 0.4 | n |  | TRUE
57 | bus_LV_113-2_0_4_node_48 | 0.4 | n |  | TRUE
58 | bus_LV_113-2_0_4_node_101 | 0.4 | n |  | TRUE
59 | bus_LV_113-2_0_4_node_55 | 0.4 | n |  | TRUE
60 | bus_LV_113-2_0_4_node_43 | 0.4 | n |  | TRUE
61 | bus_LV_113-2_0_4_node_36 | 0.4 | n |  | TRUE
62 | bus_LV_113-2_0_4_node_37 | 0.4 | n |  | TRUE
63 | bus_LV_113-2_0_4_node_40 | 0.4 | n |  | TRUE
64 | bus_LV_113-2_0_4_node_38 | 0.4 | n |  | TRUE
65 | bus_LV_113-2_0_4_node_39 | 0.4 | n |  | TRUE
66 | bus_LV_113-2_0_4_node_41 | 0.4 | n |  | TRUE
67 | bus_LV_113-2_0_4_node_44 | 0.4 | n |  | TRUE
68 | bus_LV_113-2_0_4_node_42 | 0.4 | n |  | TRUE
69 | bus_LV_113-2_0_4_node_45 | 0.4 | n |  | TRUE
70 | bus_LV_113-2_0_4_node_46 | 0.4 | n |  | TRUE
71 | bus_LV_113-2_0_4_node_47 | 0.4 | n |  | TRUE
72 | bus_LV_113-2_0_4_node_51 | 0.4 | n |  | TRUE
73 | bus_LV_113-2_0_4_node_75 | 0.4 | n |  | TRUE
74 | bus_LV_113-2_0_4_node_98 | 0.4 | n |  | TRUE
75 | bus_LV_113-2_0_4_node_100 | 0.4 | n |  | TRUE
76 | bus_LV_113-2_0_4_node_97 | 0.4 | n |  | TRUE
77 | bus_LV_113-2_0_4_node_52 | 0.4 | n |  | TRUE
78 | bus_LV_113-2_0_4_node_53 | 0.4 | n |  | TRUE
79 | bus_LV_113-2_0_4_node_54 | 0.4 | n |  | TRUE
80 | bus_LV_113-2_0_4_node_57 | 0.4 | n |  | TRUE
81 | bus_LV_113-2_0_4_node_58 | 0.4 | n |  | TRUE
82 | bus_LV_113-2_0_4_node_60 | 0.4 | n |  | TRUE
83 | bus_LV_113-2_0_4_node_61 | 0.4 | n |  | TRUE
84 | bus_LV_113-2_0_4_node_114 | 0.4 | n |  | TRUE
85 | bus_LV_113-2_0_4_node_94 | 0.4 | n |  | TRUE
86 | bus_LV_113-2_0_4_node_112 | 0.4 | n |  | TRUE
87 | bus_LV_113-2_0_4_node_95 | 0.4 | n |  | TRUE
88 | bus_LV_113-2_0_4_node_62 | 0.4 | n |  | TRUE
89 | bus_LV_113-2_0_4_node_63 | 0.4 | n |  | TRUE
90 | bus_LV_113-2_0_4_node_64 | 0.4 | n |  | TRUE
91 | bus_LV_113-2_0_4_node_120 | 0.4 | n |  | TRUE
92 | bus_LV_113-2_0_4_node_92 | 0.4 | n |  | TRUE
93 | bus_LV_113-2_0_4_node_73 | 0.4 | n |  | TRUE
94 | bus_LV_113-2_0_4_node_86 | 0.4 | n |  | TRUE
95 | bus_LV_113-2_0_4_node_76 | 0.4 | n |  | TRUE
96 | bus_LV_113-2_0_4_node_78 | 0.4 | n |  | TRUE
97 | bus_LV_113-2_0_4_node_77 | 0.4 | n |  | TRUE
98 | bus_LV_113-2_0_4_node_79 | 0.4 | n |  | TRUE
99 | bus_LV_113-2_0_4_node_80 | 0.4 | n |  | TRUE
100 | bus_LV_113-2_0_4_node_81 | 0.4 | n |  | TRUE
101 | bus_LV_113-2_0_4_node_82 | 0.4 | n |  | TRUE
102 | bus_LV_113-2_0_4_node_83 | 0.4 | n |  | TRUE
103 | bus_LV_113-2_0_4_node_99 | 0.4 | n |  | TRUE
104 | bus_LV_113-2_0_4_node_107 | 0.4 | n |  | TRUE
105 | bus_LV_113-2_0_4_node_116 | 0.4 | n |  | TRUE
106 | bus_LV_113-2_0_4_node_105 | 0.4 | n |  | TRUE
107 | bus_LV_113-2_0_4_node_115 | 0.4 | n |  | TRUE
108 | bus_LV_113-2_0_4_node_118 | 0.4 | n |  | TRUE
109 | bus_LV_113-2_0_4_node_109 | 0.4 | n |  | TRUE
110 | bus_LV_113-2_0_4_node_110 | 0.4 | n |  | TRUE
111 | bus_LV_113-2_0_4_node_113 | 0.4 | n |  | TRUE
112 | bus_LV_113-2_0_4_node_102 | 0.4 | n |  | TRUE
113 | bus_LV_113-2_0_4_node_103 | 0.4 | n |  | TRUE
114 | bus_LV_113-2_0_4_node_104 | 0.4 | n |  | TRUE
115 | bus_LV_113-2_0_4_node_106 | 0.4 | n |  | TRUE
116 | bus_LV_113-2_0_4_node_108 | 0.4 | n |  | TRUE
117 | bus_LV_113-2_0_4_node_111 | 0.4 | n |  | TRUE
118 | bus_MV_9_2_node_136 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_113-2_0_4_load_0 | 0 | 0.0043437 | 0.0010886 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_113-2_0_4_load_1 | 1 | 0.0080078 | 0.0020069 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_113-2_0_4_load_5 | 5 | 0.0013574 | 0.0003402 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_113-2_0_4_load_6 | 6 | 0.011478 | 0.0028766 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_113-2_0_4_load_9 | 9 | 0.0097051 | 0.0024323 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_113-2_0_4_load_10 | 10 | 0.0012854 | 0.00032216 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_113-2_0_4_load_72 | 11 | 0.019098 | 0.0047863 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_113-2_0_4_load_69 | 12 | 0.00059788 | 0.00014984 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_113-2_0_4_load_90 | 13 | 0.02525 | 0.0063283 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_113-2_0_4_load_91 | 14 | 0.014429 | 0.0036162 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_113-2_0_4_load_117 | 18 | 0.020805 | 0.0052141 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_113-2_0_4_load_96 | 19 | 0.042419 | 0.010631 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_113-2_0_4_load_89 | 20 | 0.0098254 | 0.0024625 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_113-2_0_4_load_65 | 21 | 0.017096 | 0.0042848 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_113-2_0_4_load_71 | 22 | 0.0013157 | 0.00032976 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_113-2_0_4_load_11 | 23 | 0.00030096 | 7.5429e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_113-2_0_4_load_12 | 24 | 0.00038997 | 9.7735e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_113-2_0_4_load_13 | 25 | 0.00014926 | 3.7408e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_113-2_0_4_load_88 | 27 | 0.0051838 | 0.0012992 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_113-2_0_4_load_87 | 28 | 0.002681 | 0.00067191 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_113-2_0_4_load_16 | 29 | 0.00012385 | 3.104e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_113-2_0_4_load_17 | 30 | 0.00026004 | 6.5171e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_113-2_0_4_load_93 | 31 | 0.0012688 | 0.000318 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_113-2_0_4_load_68 | 32 | 0.008325 | 0.0020864 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_113-2_0_4_load_66 | 33 | 0.0026324 | 0.00065975 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_113-2_0_4_load_119 | 34 | 0.00017048 | 4.2726e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_113-2_0_4_load_18 | 35 | 0.0010788 | 0.00027038 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_113-2_0_4_load_19 | 36 | 0.00042523 | 0.00010657 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_113-2_0_4_load_20 | 37 | 0.00070354 | 0.00017632 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_113-2_0_4_load_124 | 38 | 0.0064544 | 0.0016176 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_113-2_0_4_load_21 | 39 | 0.00069414 | 0.00017397 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_113-2_0_4_load_22 | 40 | 0.00081615 | 0.00020455 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_113-2_0_4_load_24 | 43 | 0.0008116 | 0.00020341 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_113-2_0_4_load_84 | 45 | 0.0035468 | 0.00088891 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_113-2_0_4_load_27 | 46 | 0.001865 | 0.00046741 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_113-2_0_4_load_28 | 47 | 0.0020915 | 0.00052418 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_113-2_0_4_load_29 | 48 | 0.0010346 | 0.0002593 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_113-2_0_4_load_32 | 51 | 0.0027048 | 0.00067788 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_113-2_0_4_load_35 | 53 | 0.0027117 | 0.00067962 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_113-2_0_4_load_49 | 55 | 0.014143 | 0.0035446 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_113-2_0_4_load_59 | 56 | 0.0013804 | 0.00034596 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_113-2_0_4_load_48 | 57 | 0.0017262 | 0.00043263 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_113-2_0_4_load_101 | 58 | 0.011078 | 0.0027765 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_113-2_0_4_load_43 | 60 | 0.0016945 | 0.00042468 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_113-2_0_4_load_36 | 61 | 0.0020358 | 0.00051021 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_113-2_0_4_load_38 | 64 | 0.0057892 | 0.0014509 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_113-2_0_4_load_44 | 67 | 0.00054384 | 0.0001363 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_113-2_0_4_load_42 | 68 | 0.0033835 | 0.000848 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_113-2_0_4_load_46 | 70 | 0.0061496 | 0.0015412 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_113-2_0_4_load_47 | 71 | 0.0012807 | 0.00032097 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_113-2_0_4_load_75 | 73 | 0.007836 | 0.0019639 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_113-2_0_4_load_98 | 74 | 0.0066088 | 0.0016563 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_113-2_0_4_load_100 | 75 | 0.0013252 | 0.00033214 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_113-2_0_4_load_97 | 76 | 0.01163 | 0.0029148 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_113-2_0_4_load_52 | 77 | 0.0017676 | 0.000443 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_113-2_0_4_load_53 | 78 | 0.00023578 | 5.9092e-05 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_113-2_0_4_load_54 | 79 | 0.00040014 | 0.00010028 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_113-2_0_4_load_58 | 81 | 0.013923 | 0.0034895 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_113-2_0_4_load_60 | 82 | 0.0010678 | 0.00026762 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_113-2_0_4_load_61 | 83 | 0.054127 | 0.013565 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_113-2_0_4_load_114 | 84 | 0.00050692 | 0.00012705 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_113-2_0_4_load_94 | 85 | 0.0048517 | 0.0012159 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_113-2_0_4_load_95 | 87 | 0.00033802 | 8.4716e-05 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_113-2_0_4_load_62 | 88 | 0.0034542 | 0.00086571 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_113-2_0_4_load_63 | 89 | 0.015827 | 0.0039667 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_113-2_0_4_load_64 | 90 | 0.0022962 | 0.00057548 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_113-2_0_4_load_92 | 92 | 0.0093667 | 0.0023475 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_113-2_0_4_load_86 | 94 | 0.0042106 | 0.0010553 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_113-2_0_4_load_76 | 95 | 0.00024998 | 6.2651e-05 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_113-2_0_4_load_78 | 96 | 0.00026633 | 6.6748e-05 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_113-2_0_4_load_77 | 97 | 0.0010749 | 0.0002694 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_113-2_0_4_load_79 | 98 | 0.00010117 | 2.5356e-05 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_113-2_0_4_load_81 | 100 | 0.0010992 | 0.00027549 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_113-2_0_4_load_82 | 101 | 0.010702 | 0.0026823 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_113-2_0_4_load_107 | 104 | 0.00010662 | 2.6721e-05 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_113-2_0_4_load_116 | 105 | 0.0002691 | 6.7443e-05 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_113-2_0_4_load_105 | 106 | 0.01611 | 0.0040376 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_113-2_0_4_load_115 | 107 | 0.00037994 | 9.5222e-05 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_113-2_0_4_load_118 | 108 | 0.010398 | 0.0026059 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_113-2_0_4_load_109 | 109 | 0.00010989 | 2.7541e-05 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_113-2_0_4_load_110 | 110 | 0.006283 | 0.0015747 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_113-2_0_4_load_113 | 111 | 0.001816 | 0.00045514 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_113-2_0_4_load_102 | 112 | 0.0026025 | 0.00065224 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_113-2_0_4_load_103 | 113 | 0.0092954 | 0.0023297 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_113-2_0_4_load_104 | 114 | 0.014824 | 0.0037154 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_113-2_0_4_load_106 | 115 | 0.010819 | 0.0027115 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_113-2_0_4_load_108 | 116 | 0.038142 | 0.0095593 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_113-2_0_4_load_111 | 117 | 0.00011107 | 2.7837e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 116 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_113-2_0_4_line_0 |  | 0 | 1 | 0.031956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
1 | LV_113-2_0_4_line_1 |  | 0 | 2 | 0.046563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
2 | LV_113-2_0_4_line_2 |  | 1 | 3 | 0.023333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
3 | LV_113-2_0_4_line_3 |  | 2 | 4 | 0.016256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
4 | LV_113-2_0_4_line_4 |  | 2 | 5 | 0.014084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_113-2_0_4_line_5 |  | 3 | 6 | 0.010366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_113-2_0_4_line_6 |  | 3 | 7 | 0.039974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
7 | LV_113-2_0_4_line_7 |  | 4 | 8 | 0.065443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_113-2_0_4_line_8 |  | 4 | 9 | 0.01778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_113-2_0_4_line_9 |  | 5 | 10 | 0.040219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_113-2_0_4_line_10 |  | 7 | 11 | 0.023431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_113-2_0_4_line_11 |  | 7 | 12 | 0.039063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_113-2_0_4_line_12 |  | 8 | 13 | 0.062149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
13 | LV_113-2_0_4_line_13 |  | 8 | 14 | 0.028639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_113-2_0_4_line_14 |  | 9 | 15 | 0.03139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
15 | LV_113-2_0_4_line_15 |  | 10 | 16 | 0.033686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_113-2_0_4_line_16 |  | 11 | 17 | 0.031084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_113-2_0_4_line_17 |  | 13 | 18 | 0.028912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_113-2_0_4_line_18 |  | 14 | 19 | 0.0025107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_113-2_0_4_line_19 |  | 15 | 20 | 0.01962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_113-2_0_4_line_20 |  | 15 | 21 | 0.025307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_113-2_0_4_line_21 |  | 16 | 22 | 0.0073212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_113-2_0_4_line_22 |  | 17 | 38 | 0.25254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_113-2_0_4_line_23 |  | 18 | 101 | 0.038052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_113-2_0_4_line_24 |  | 19 | 76 | 0.046083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_113-2_0_4_line_25 |  | 20 | 92 | 0.010317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_113-2_0_4_line_26 |  | 21 | 89 | 0.02636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
27 | LV_113-2_0_4_line_27 |  | 22 | 93 | 0.031284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_113-2_0_4_line_28 |  | 23 | 24 | 0.023414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_113-2_0_4_line_29 |  | 23 | 25 | 0.00018104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_113-2_0_4_line_30 |  | 25 | 26 | 0.0035081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_113-2_0_4_line_31 |  | 26 | 29 | 0.048055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_113-2_0_4_line_32 |  | 27 | 28 | 0.030197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_113-2_0_4_line_33 |  | 28 | 44 | 0.049661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_113-2_0_4_line_34 |  | 29 | 30 | 0.017881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_113-2_0_4_line_35 |  | 30 | 31 | 0.016847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_113-2_0_4_line_36 |  | 31 | 34 | 0.03568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_113-2_0_4_line_37 |  | 32 | 33 | 0.0067123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_113-2_0_4_line_38 |  | 33 | 91 | 0.17987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_113-2_0_4_line_39 |  | 33 | 90 | 0.10422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
40 | LV_113-2_0_4_line_40 |  | 34 | 91 | 0.095033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_113-2_0_4_line_41 |  | 35 | 36 | 0.033194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_113-2_0_4_line_42 |  | 36 | 37 | 0.03921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_113-2_0_4_line_43 |  | 37 | 39 | 0.0038932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_113-2_0_4_line_44 |  | 38 | 42 | 0.044557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_113-2_0_4_line_45 |  | 39 | 40 | 0.0097747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_113-2_0_4_line_46 |  | 40 | 41 | 0.045428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_113-2_0_4_line_47 |  | 41 | 42 | 0.1242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
48 | LV_113-2_0_4_line_48 |  | 43 | 44 | 0.14378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_113-2_0_4_line_49 |  | 44 | 45 | 0.028955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_113-2_0_4_line_50 |  | 45 | 93 | 0.010239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_113-2_0_4_line_51 |  | 46 | 47 | 0.0026029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_113-2_0_4_line_52 |  | 46 | 48 | 0.056018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_113-2_0_4_line_53 |  | 47 | 49 | 0.0091883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_113-2_0_4_line_54 |  | 48 | 50 | 0.02806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_113-2_0_4_line_55 |  | 49 | 51 | 0.0096748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_113-2_0_4_line_56 |  | 50 | 52 | 0.021082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_113-2_0_4_line_57 |  | 51 | 53 | 0.063117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_113-2_0_4_line_58 |  | 52 | 54 | 0.021744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
59 | LV_113-2_0_4_line_59 |  | 52 | 55 | 0.051018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_113-2_0_4_line_60 |  | 53 | 57 | 0.031398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_113-2_0_4_line_61 |  | 54 | 56 | 0.021903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
62 | LV_113-2_0_4_line_62 |  | 55 | 58 | 0.12399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_113-2_0_4_line_63 |  | 56 | 59 | 0.03323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
64 | LV_113-2_0_4_line_64 |  | 57 | 60 | 0.030998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_113-2_0_4_line_65 |  | 59 | 80 | 0.020441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_113-2_0_4_line_66 |  | 59 | 81 | 0.028377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
67 | LV_113-2_0_4_line_67 |  | 59 | 78 | 0.022461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_113-2_0_4_line_68 |  | 60 | 65 | 0.019299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_113-2_0_4_line_69 |  | 61 | 62 | 0.044591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_113-2_0_4_line_70 |  | 61 | 63 | 0.20485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_113-2_0_4_line_71 |  | 62 | 64 | 0.071711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_113-2_0_4_line_72 |  | 62 | 65 | 0.050084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_113-2_0_4_line_73 |  | 63 | 66 | 0.082848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_113-2_0_4_line_74 |  | 64 | 68 | 0.010169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_113-2_0_4_line_75 |  | 66 | 67 | 0.0022511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_113-2_0_4_line_76 |  | 68 | 69 | 0.0054355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_113-2_0_4_line_77 |  | 69 | 70 | 0.01204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_113-2_0_4_line_78 |  | 70 | 71 | 0.026656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_113-2_0_4_line_79 |  | 72 | 73 | 0.056191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_113-2_0_4_line_80 |  | 72 | 74 | 0.034862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_113-2_0_4_line_81 |  | 72 | 75 | 0.021497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_113-2_0_4_line_82 |  | 74 | 76 | 0.0044147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_113-2_0_4_line_83 |  | 77 | 78 | 0.0090792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_113-2_0_4_line_84 |  | 77 | 79 | 0.015928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_113-2_0_4_line_85 |  | 80 | 82 | 0.073004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_113-2_0_4_line_86 |  | 81 | 83 | 0.048827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
87 | LV_113-2_0_4_line_87 |  | 82 | 84 | 0.047259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_113-2_0_4_line_88 |  | 83 | 85 | 0.017339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
89 | LV_113-2_0_4_line_89 |  | 84 | 86 | 0.023739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_113-2_0_4_line_90 |  | 85 | 87 | 0.0018825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
91 | LV_113-2_0_4_line_91 |  | 86 | 111 | 0.0068167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_113-2_0_4_line_92 |  | 86 | 103 | 0.007318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_113-2_0_4_line_93 |  | 87 | 109 | 0.016744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
94 | LV_113-2_0_4_line_94 |  | 88 | 89 | 0.0038598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
95 | LV_113-2_0_4_line_95 |  | 88 | 90 | 0.021925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
96 | LV_113-2_0_4_line_96 |  | 92 | 108 | 0.0052996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_113-2_0_4_line_97 |  | 93 | 94 | 0.069536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_113-2_0_4_line_98 |  | 95 | 96 | 0.022134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_113-2_0_4_line_99 |  | 96 | 99 | 0.02314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_113-2_0_4_line_100 |  | 97 | 98 | 0.001959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_113-2_0_4_line_101 |  | 98 | 100 | 0.012667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_113-2_0_4_line_102 |  | 99 | 101 | 0.0037768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
103 | LV_113-2_0_4_line_103 |  | 99 | 102 | 0.024021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
104 | LV_113-2_0_4_line_104 |  | 100 | 103 | 0.069205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_113-2_0_4_line_105 |  | 102 | 104 | 0.038106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
106 | LV_113-2_0_4_line_106 |  | 102 | 105 | 0.0060271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
107 | LV_113-2_0_4_line_107 |  | 104 | 106 | 0.0093058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
108 | LV_113-2_0_4_line_108 |  | 105 | 107 | 0.028929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
109 | LV_113-2_0_4_line_109 |  | 106 | 113 | 0.021988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
110 | LV_113-2_0_4_line_110 |  | 107 | 117 | 0.0036774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
111 | LV_113-2_0_4_line_111 |  | 109 | 110 | 0.00055814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
112 | LV_113-2_0_4_line_112 |  | 110 | 117 | 0.025075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
113 | LV_113-2_0_4_line_113 |  | 112 | 113 | 0.022032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
114 | LV_113-2_0_4_line_114 |  | 112 | 114 | 0.012832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
115 | LV_113-2_0_4_line_115 |  | 114 | 115 | 0.0097693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
116 | LV_113-2_0_4_line_116 |  | 115 | 116 | 0.011703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_113-2_0_4_trafo_108 | 0.63 MVA 20/0.4 kV | 118 | 116 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16
0 | 2707254.2577 | 1236810.8135 | 2707265.8612 | 1236799.2607 | 2707276.0309 | 1236787.4547
1 | 2707221.2623 | 1236843.6676 | 2707225.2852 | 1236839.6594 | 2707254.2577 | 1236810.8135
2 | 2707293.9701 | 1236800.8918 | 2707276.6605 | 1236786.7238 | 2707276.0309 | 1236787.4547
3 | 2707221.2623 | 1236843.6676 | 2707218.988 | 1236838.4336 | 2707214.7885 | 1236828.7504
4 | 2707221.2623 | 1236843.6676 | 2707225.0682 | 1236852.5098 | 2707226.8954 | 1236856.5759
5 | 2707293.9701 | 1236800.8918 | 2707300.2645 | 1236792.6436
6 | 2707293.9701 | 1236800.8918 | 2707301.6208 | 1236809.3032 | 2707305.3306 | 1236811.3162 | 2707323.7483 | 1236827.3946
7 | 2707183.2633 | 1236771.5595 | 2707201.6216 | 1236801.425 | 2707206.9337 | 1236809.8496 | 2707214.7885 | 1236828.7504
8 | 2707214.7885 | 1236828.7504 | 2707200.2424 | 1236838.974
9 | 2707226.8954 | 1236856.5759 | 2707227.8693 | 1236858.743 | 2707234.7054 | 1236874.5452 | 2707238.4979 | 1236884.9662 | 2707241.326 | 1236894.0731
10 | 2707323.7483 | 1236827.3946 | 2707330.9067 | 1236819.4956 | 2707339.4779 | 1236810.0285
11 | 2707323.7483 | 1236827.3946 | 2707326.274 | 1236829.5975 | 2707303.4069 | 1236857.0278
12 | 2707183.2633 | 1236771.5595 | 2707177.9027 | 1236764.98 | 2707167.4353 | 1236751.603 | 2707143.5811 | 1236723.743
13 | 2707183.2633 | 1236771.5595 | 2707205.2941 | 1236753.2613
14 | 2707174.5607 | 1236857.0241 | 2707200.2424 | 1236838.974
15 | 2707249.8839 | 1236926.6484 | 2707246.1762 | 1236911.5365 | 2707242.3457 | 1236897.3564 | 2707241.326 | 1236894.0731
16 | 2707359.8354 | 1236789.1839 | 2707353.0254 | 1236799.9914 | 2707347.6518 | 1236800.0054 | 2707340.6137 | 1236808.7739 | 2707339.4779 | 1236810.0285
17 | 2707143.5811 | 1236723.743 | 2707141.4416 | 1236721.2441 | 2707122.3236 | 1236704.1848
18 | 2707207.2255 | 1236751.6572 | 2707205.2941 | 1236753.2613
19 | 2707174.5607 | 1236857.0241 | 2707169.4955 | 1236859.657 | 2707164.7265 | 1236857.6249 | 2707162.5225 | 1236853.5264 | 2707162.2326 | 1236849.4625 | 2707162.2326 | 1236849.4625
20 | 2707174.5607 | 1236857.0241 | 2707154.0148 | 1236871.7996
21 | 2707249.8839 | 1236926.6484 | 2707251.278 | 1236933.8356
22 | 2707359.8354 | 1236789.1839 | 2707606.6308 | 1236842.7462
23 | 2707093.9313 | 1236678.8498 | 2707122.3236 | 1236704.1848
24 | 2707207.2255 | 1236751.6572 | 2707208.8798 | 1236750.2831 | 2707239.0656 | 1236718.3628
25 | 2707162.2326 | 1236849.4625 | 2707163.5216 | 1236844.7154 | 2707166.957 | 1236840.552
26 | 2707135.5791 | 1236890.0687 | 2707135.5791 | 1236890.0687 | 2707137.1574 | 1236887.7398 | 2707138.7215 | 1236884.9436 | 2707139.4872 | 1236883.6119 | 2707140.3638 | 1236882.4268 | 2707141.4749 | 1236881.246 | 2707142.9748 | 1236879.9053 | 2707144.6647 | 1236878.5236 | 2707154.0148 | 1236871.7996
27 | 2707256.1962 | 1236964.7251 | 2707252.6393 | 1236940.8536 | 2707251.278 | 1236933.8356
28 | 2706949.2182 | 1237278.0921 | 2706951.3936 | 1237278.3051 | 2706957.3515 | 1237279.4354 | 2706962.6105 | 1237280.72 | 2706971.8502 | 1237283.8351
29 | 2706949.0381 | 1237278.0745 | 2706949.2182 | 1237278.0921
30 | 2706945.5466 | 1237277.7327 | 2706949.0381 | 1237278.0745
31 | 2706945.5466 | 1237277.7327 | 2706945.7664 | 1237273.9337 | 2706945.7013 | 1237270.8301 | 2706945.4181 | 1237268.0674 | 2706945.0383 | 1237265.6253 | 2706944.1937 | 1237262.5188 | 2706942.2449 | 1237256.8571 | 2706940.8235 | 1237252.5838 | 2706940.1029 | 1237248.9013 | 2706939.9064 | 1237244.6834 | 2706940.259 | 1237241.0758 | 2706941.0173 | 1237237.2087 | 2706942.6299 | 1237231.7113 | 2706942.9447 | 1237230.85
32 | 2707209.6868 | 1237009.8093 | 2707199.1183 | 1237015.0448 | 2707181.2726 | 1237019.5372
33 | 2707258.7742 | 1237003.8241 | 2707238.3843 | 1237004.3564 | 2707232.8519 | 1237004.7902 | 2707227.9952 | 1237005.5253 | 2707209.6868 | 1237009.8093
34 | 2706949.8591 | 1237214.3725 | 2706947.2389 | 1237219.9296 | 2706944.8826 | 1237225.5471 | 2706942.9447 | 1237230.85
35 | 2706958.3173 | 1237199.8024 | 2706954.4916 | 1237206.3275 | 2706949.8591 | 1237214.3725 | 2706949.8591 | 1237214.3725
36 | 2706958.3173 | 1237199.8024 | 2706992.6257 | 1237190.004
37 | 2707006.7786 | 1236924.9407 | 2707008.0026 | 1236924.6292 | 2707009.2826 | 1236924.5744 | 2707010.4749 | 1236924.7627 | 2707011.7754 | 1236925.2532 | 2707013.1343 | 1236926.0417
38 | 2707013.1343 | 1236926.0417 | 2707007.8463 | 1237105.833
39 | 2707112.6697 | 1236900.2057 | 2707092.3445 | 1236904.667 | 2707085.0033 | 1236906.3582 | 2707079.1384 | 1236908.0204 | 2707072.3924 | 1236910.2784 | 2707045.0143 | 1236920.6152 | 2707037.4876 | 1236923.3594 | 2707028.9301 | 1236926.1963 | 2707024.5483 | 1236927.4517 | 2707021.9744 | 1236927.9168 | 2707019.778 | 1236928.0106 | 2707017.7614 | 1236927.7852 | 2707015.9457 | 1236927.3299 | 2707014.0896 | 1236926.5959 | 2707013.1343 | 1236926.0417
40 | 2707007.8463 | 1237105.833 | 2707013.2078 | 1237121.5862 | 2707015.3823 | 1237128.9977 | 2707016.281 | 1237133.7176 | 2707016.8532 | 1237138.4982 | 2707016.8998 | 1237143.4696 | 2707016.2817 | 1237148.3734 | 2707014.7733 | 1237155.6407 | 2707011.0618 | 1237169.2621 | 2707009.3163 | 1237174.5681 | 2707007.6742 | 1237178.764 | 2707006.3764 | 1237181.4872 | 2707005.2106 | 1237183.1897 | 2707003.7249 | 1237184.5862 | 2707002.1158 | 1237185.6914 | 2706999.8918 | 1237186.8968 | 2706992.6257 | 1237190.004
41 | 2707826.8252 | 1236785.958 | 2707811.2919 | 1236764.1628 | 2707806.5264 | 1236759.8454
42 | 2707775.8524 | 1236735.6811 | 2707788.1208 | 1236743.1705 | 2707806.5264 | 1236759.8454
43 | 2707772.5294 | 1236733.6525 | 2707775.8524 | 1236735.6811
44 | 2707639.1807 | 1236815.6482 | 2707626.9149 | 1236818.4504 | 2707616.5041 | 1236827.0573 | 2707606.6308 | 1236842.7462
45 | 2707772.5294 | 1236733.6525 | 2707764.1865 | 1236728.5594
46 | 2707720.1656 | 1236721.4878 | 2707726.9618 | 1236721.0774 | 2707744.8975 | 1236721.97 | 2707757.8204 | 1236724.6732 | 2707764.1865 | 1236728.5594
47 | 2707720.1656 | 1236721.4878 | 2707639.1807 | 1236815.6482
48 | 2707258.7742 | 1237003.8241 | 2707348.7409 | 1237115.9804
49 | 2707258.7742 | 1237003.8241 | 2707258.082 | 1236988.9446 | 2707257.2211 | 1236974.9114
50 | 2707256.1962 | 1236964.7251 | 2707257.1232 | 1236973.3152 | 2707257.2211 | 1236974.9114
51 | 2707097.9848 | 1236418.5977 | 2707100.4484 | 1236417.7576
52 | 2707097.9848 | 1236418.5977 | 2707065.4474 | 1236429.6935 | 2707049.6184 | 1236444.451
53 | 2707109.1449 | 1236414.7919 | 2707100.4484 | 1236417.7576
54 | 2707025.8113 | 1236456.9448 | 2707031.7579 | 1236456.6517 | 2707039.074 | 1236454.2817 | 2707049.6184 | 1236444.451
55 | 2707109.1449 | 1236414.7919 | 2707117.5256 | 1236409.9582
56 | 2707025.8113 | 1236456.9448 | 2707019.5223 | 1236477.0692
57 | 2707172.1998 | 1236378.4235 | 2707117.5256 | 1236409.9582
58 | 2707001.9688 | 1236464.1653 | 2707019.5223 | 1236477.0692
59 | 2707019.5223 | 1236477.0692 | 2707031.2794 | 1236485.7099 | 2707055.2203 | 1236493.5918 | 2707065.9728 | 1236496.8034
60 | 2707172.1998 | 1236378.4235 | 2707199.3979 | 1236362.7364
61 | 2707001.9688 | 1236464.1653 | 2706997.5202 | 1236474.1485 | 2706993.05 | 1236484.1701
62 | 2707139.0181 | 1236568.1847 | 2707138.466 | 1236566.5822 | 2707138.2339 | 1236563.0864 | 2707139.4032 | 1236554.4897 | 2707142.3054 | 1236544.6567 | 2707143.2666 | 1236537.9466 | 2707138.9204 | 1236528.4053 | 2707128.4029 | 1236515.6725 | 2707117.1206 | 1236507.9965 | 2707084.2631 | 1236502.2664 | 2707065.9728 | 1236496.8034
63 | 2706979.6865 | 1236514.5918 | 2706986.6952 | 1236499.0394 | 2706991.0448 | 1236488.6652 | 2706993.05 | 1236484.1701
64 | 2707199.3979 | 1236362.7364 | 2707207.8308 | 1236357.8725 | 2707226.745 | 1236348.1591
65 | 2706979.6865 | 1236514.5918 | 2706971.1024 | 1236533.1515
66 | 2706979.6865 | 1236514.5918 | 2706989.9031 | 1236521.3588 | 2706992.4952 | 1236523.6739 | 2706995.3007 | 1236528.0056 | 2706997.915 | 1236534.9691 | 2706997.932 | 1236535.0145
67 | 2706979.6865 | 1236514.5918 | 2706973.3414 | 1236510.1185 | 2706959.0683 | 1236506.6108
68 | 2707243.9125 | 1236339.3428 | 2707226.745 | 1236348.1591
69 | 2707280.1234 | 1236371.0544 | 2707320.8199 | 1236358.5131 | 2707322.7811 | 1236358.0906
70 | 2707322.7811 | 1236358.0906 | 2707527.6223 | 1236360.454
71 | 2707280.1234 | 1236371.0544 | 2707291.4298 | 1236377.8193 | 2707298.52 | 1236386.2872 | 2707302.4397 | 1236395.9655 | 2707311.0387 | 1236432.0026
72 | 2707243.9125 | 1236339.3428 | 2707250.3097 | 1236350.1444 | 2707258.7809 | 1236361.3504 | 2707269.1324 | 1236367.3531 | 2707280.1234 | 1236371.0544
73 | 2707539.7889 | 1236285.8833 | 2707537.1421 | 1236295.3649 | 2707527.121 | 1236303.7233 | 2707528.6877 | 1236324.2008 | 2707534.9615 | 1236338.025 | 2707533.1722 | 1236352.4038 | 2707527.6223 | 1236360.454
74 | 2707313.399 | 1236441.8943 | 2707311.0387 | 1236432.0026
75 | 2707539.7889 | 1236285.8833 | 2707540.832 | 1236283.8885
76 | 2707314.6606 | 1236447.1813 | 2707313.399 | 1236441.8943
77 | 2707314.6606 | 1236447.1813 | 2707316.9024 | 1236459.0104
78 | 2707324.6574 | 1236484.4343 | 2707318.5092 | 1236467.4887 | 2707316.9024 | 1236459.0104
79 | 2707270.8997 | 1236695.5049 | 2707281.7099 | 1236693.6765 | 2707290.2563 | 1236696.5108 | 2707298.3049 | 1236705.9412 | 2707308.6335 | 1236727.411
80 | 2707270.8997 | 1236695.5049 | 2707242.1198 | 1236715.1797
81 | 2707270.8997 | 1236695.5049 | 2707257.0465 | 1236679.0664
82 | 2707239.0656 | 1236718.3628 | 2707241.9952 | 1236715.2649 | 2707242.1198 | 1236715.1797
83 | 2706950.2515 | 1236504.444 | 2706959.0683 | 1236506.6108
84 | 2706950.2515 | 1236504.444 | 2706934.7837 | 1236500.6427
85 | 2706971.1024 | 1236533.1515 | 2706940.8405 | 1236596.3443 | 2706939.566 | 1236598.9924
86 | 2706997.932 | 1236535.0145 | 2707010.7926 | 1236569.1941 | 2707015.5515 | 1236580.5453
87 | 2706919.0714 | 1236641.5763 | 2706939.566 | 1236598.9924
88 | 2707015.5515 | 1236580.5453 | 2707019.3043 | 1236589.4964 | 2707022.188 | 1236596.5632
89 | 2706907.637 | 1236662.3754 | 2706917.9838 | 1236643.8362 | 2706919.0714 | 1236641.5763
90 | 2707022.8993 | 1236598.3061 | 2707022.188 | 1236596.5632
91 | 2706907.637 | 1236662.3754 | 2706904.1854 | 1236668.2536
92 | 2706914.1611 | 1236665.7287 | 2706907.637 | 1236662.3754
93 | 2707022.8993 | 1236598.3061 | 2707026.248 | 1236606.5124 | 2707030.1488 | 1236613.3596
94 | 2707133.0248 | 1236892.9519 | 2707134.0076 | 1236892.0196 | 2707135.5791 | 1236890.0687
95 | 2707133.0248 | 1236892.9519 | 2707132.1442 | 1236893.7874 | 2707129.8598 | 1236895.403 | 2707127.4315 | 1236896.6046 | 2707124.8965 | 1236897.4261 | 2707120.8526 | 1236898.4095 | 2707112.6697 | 1236900.2057
96 | 2707171.6849 | 1236838.1576 | 2707166.957 | 1236840.552
97 | 2707256.1962 | 1236964.7251 | 2707270.8416 | 1236955.0154 | 2707281.111 | 1236948.329 | 2707306.3633 | 1236917.6832
98 | 2707060.5345 | 1236709.7219 | 2707075.4842 | 1236693.3995
99 | 2707091.1132 | 1236676.3353 | 2707075.4842 | 1236693.3995
100 | 2706989.3452 | 1236702.5825 | 2706987.8323 | 1236701.338
101 | 2706976.4034 | 1236695.875 | 2706987.8323 | 1236701.338 | 2706987.8323 | 1236701.338
102 | 2707091.1132 | 1236676.3353 | 2707093.9313 | 1236678.8498
103 | 2707091.1132 | 1236676.3353 | 2707073.0004 | 1236660.4965
104 | 2706914.1611 | 1236665.7287 | 2706943.9906 | 1236679.0092 | 2706963.0779 | 1236689.5054 | 2706976.4034 | 1236695.875
105 | 2707073.0004 | 1236660.4965 | 2707100.2712 | 1236633.8817
106 | 2707073.0004 | 1236660.4965 | 2707068.4647 | 1236656.5275
107 | 2707100.2712 | 1236633.8817 | 2707100.9119 | 1236633.2564 | 2707107.8559 | 1236630.9465 | 2707108.911 | 1236631.2298
108 | 2707046.9704 | 1236637.1835 | 2707051.0058 | 1236641.252 | 2707060.5577 | 1236649.6083 | 2707068.4647 | 1236656.5275
109 | 2707126.6546 | 1236643.1347 | 2707122.932 | 1236638.9134 | 2707115.9376 | 1236633.1161 | 2707108.911 | 1236631.2298
110 | 2707044.3808 | 1236634.5726 | 2707046.9704 | 1236637.1835
111 | 2707030.4251 | 1236613.8446 | 2707030.1488 | 1236613.3596
112 | 2707044.3808 | 1236634.5726 | 2707041.6623 | 1236631.8319 | 2707032.8726 | 1236618.1408 | 2707030.4251 | 1236613.8446
113 | 2707141.2266 | 1236659.6593 | 2707126.6546 | 1236643.1347
114 | 2707141.2266 | 1236659.6593 | 2707149.7138 | 1236669.2836
115 | 2707156.1753 | 1236676.6109 | 2707149.7138 | 1236669.2836
116 | 2707163.9156 | 1236685.3884 | 2707156.1753 | 1236676.6109

## bus_geodata
| x | y | coords
0 | 2707254.2577 | 1236810.8135
1 | 2707276.0309 | 1236787.4547
2 | 2707221.2623 | 1236843.6676
3 | 2707293.9701 | 1236800.8918
4 | 2707214.7885 | 1236828.7504
5 | 2707226.8954 | 1236856.5759
6 | 2707300.2645 | 1236792.6436
7 | 2707323.7483 | 1236827.3946
8 | 2707183.2633 | 1236771.5595
9 | 2707200.2424 | 1236838.974
10 | 2707241.326 | 1236894.0731
11 | 2707339.4779 | 1236810.0285
12 | 2707303.4069 | 1236857.0278
13 | 2707143.5811 | 1236723.7429
14 | 2707205.2941 | 1236753.2613
15 | 2707174.5607 | 1236857.0241
16 | 2707249.8839 | 1236926.6484
17 | 2707359.8354 | 1236789.1839
18 | 2707122.3236 | 1236704.1848
19 | 2707207.2255 | 1236751.6572
20 | 2707162.2326 | 1236849.4625
21 | 2707154.0148 | 1236871.7996
22 | 2707251.278 | 1236933.8356
23 | 2706949.2182 | 1237278.0921
24 | 2706971.8502 | 1237283.8351
25 | 2706949.0381 | 1237278.0745
26 | 2706945.5466 | 1237277.7327
27 | 2707181.2726 | 1237019.5372
28 | 2707209.6868 | 1237009.8093
29 | 2706942.9447 | 1237230.85
30 | 2706949.8591 | 1237214.3725
31 | 2706958.3173 | 1237199.8024
32 | 2707006.7786 | 1236924.9407
33 | 2707013.1343 | 1236926.0417
34 | 2706992.6257 | 1237190.004
35 | 2707826.8252 | 1236785.958
36 | 2707806.5264 | 1236759.8454
37 | 2707775.8524 | 1236735.6811
38 | 2707606.6308 | 1236842.7462
39 | 2707772.5294 | 1236733.6525
40 | 2707764.1865 | 1236728.5594
41 | 2707720.1656 | 1236721.4878
42 | 2707639.1807 | 1236815.6482
43 | 2707348.7409 | 1237115.9804
44 | 2707258.7742 | 1237003.8241
45 | 2707257.2211 | 1236974.9114
46 | 2707097.9848 | 1236418.5977
47 | 2707100.4484 | 1236417.7576
48 | 2707049.6184 | 1236444.451
49 | 2707109.1449 | 1236414.7919
50 | 2707025.8113 | 1236456.9448
51 | 2707117.5256 | 1236409.9582
52 | 2707019.5223 | 1236477.0692
53 | 2707172.1998 | 1236378.4235
54 | 2707001.9688 | 1236464.1653
55 | 2707065.9728 | 1236496.8034
56 | 2706993.05 | 1236484.1701
57 | 2707199.3979 | 1236362.7364
58 | 2707139.0181 | 1236568.1847
59 | 2706979.6865 | 1236514.5918
60 | 2707226.745 | 1236348.1591
61 | 2707322.7811 | 1236358.0906
62 | 2707280.1234 | 1236371.0544
63 | 2707527.6223 | 1236360.454
64 | 2707311.0387 | 1236432.0026
65 | 2707243.9125 | 1236339.3428
66 | 2707539.7889 | 1236285.8833
67 | 2707540.832 | 1236283.8885
68 | 2707313.399 | 1236441.8943
69 | 2707314.6606 | 1236447.1813
70 | 2707316.9024 | 1236459.0104
71 | 2707324.6574 | 1236484.4343
72 | 2707270.8997 | 1236695.5049
73 | 2707308.6335 | 1236727.411
74 | 2707242.1198 | 1236715.1797
75 | 2707257.0465 | 1236679.0664
76 | 2707239.0656 | 1236718.3628
77 | 2706950.2515 | 1236504.444
78 | 2706959.0683 | 1236506.6108
79 | 2706934.7837 | 1236500.6427
80 | 2706971.1024 | 1236533.1515
81 | 2706997.932 | 1236535.0145
82 | 2706939.566 | 1236598.9924
83 | 2707015.5515 | 1236580.5453
84 | 2706919.0714 | 1236641.5763
85 | 2707022.188 | 1236596.5632
86 | 2706907.637 | 1236662.3754
87 | 2707022.8993 | 1236598.3061
88 | 2707133.0248 | 1236892.9519
89 | 2707135.5791 | 1236890.0687
90 | 2707112.6697 | 1236900.2057
91 | 2707007.8463 | 1237105.833
92 | 2707166.957 | 1236840.552
93 | 2707256.1962 | 1236964.7251
94 | 2707306.3633 | 1236917.6832
95 | 2707060.5345 | 1236709.7219
96 | 2707075.4842 | 1236693.3995
97 | 2706989.3452 | 1236702.5826
98 | 2706987.8323 | 1236701.338
99 | 2707091.1132 | 1236676.3353
100 | 2706976.4034 | 1236695.875
101 | 2707093.9313 | 1236678.8498
102 | 2707073.0004 | 1236660.4965
103 | 2706914.1611 | 1236665.7287
104 | 2707100.2712 | 1236633.8817
105 | 2707068.4647 | 1236656.5275
106 | 2707108.911 | 1236631.2298
107 | 2707046.9704 | 1236637.1835
108 | 2707171.6849 | 1236838.1576
109 | 2707030.1488 | 1236613.3596
110 | 2707030.4251 | 1236613.8446
111 | 2706904.1854 | 1236668.2536
112 | 2707141.2266 | 1236659.6593
113 | 2707126.6546 | 1236643.1347
114 | 2707149.7138 | 1236669.2836
115 | 2707156.1753 | 1236676.6109
116 | 2707163.9157 | 1236685.3884
117 | 2707044.3808 | 1236634.5726
118 | 2707073.0004 | 1236660.4965

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97266 | -0.52627 | 0.0043437 | 0.0010886
1 | 0.9723 | -0.53355 | 0.0080078 | 0.0020069
2 | 0.97325 | -0.51475 | 0 | 0
3 | 0.97207 | -0.538 | 0 | 0
4 | 0.97353 | -0.5092 | 0 | 0
5 | 0.97298 | -0.52004 | 0.0013574 | 0.0003402
6 | 0.97196 | -0.5402 | 0.011478 | 0.0028766
7 | 0.97179 | -0.54352 | 0 | 0
8 | 0.97606 | -0.45944 | 0 | 0
9 | 0.97315 | -0.5167 | 0.0097051 | 0.0024323
10 | 0.97226 | -0.53415 | 0.0012854 | 0.00032216
11 | 0.97163 | -0.54669 | 0.019098 | 0.0047863
12 | 0.97177 | -0.54395 | 0.00059788 | 0.00014984
13 | 0.97968 | -0.38862 | 0.02525 | 0.0063283
14 | 0.97381 | -0.50369 | 0.014429 | 0.0036162
15 | 0.97255 | -0.52853 | 0 | 0
16 | 0.97171 | -0.54519 | 0 | 0
17 | 0.97156 | -0.54816 | 0 | 0
18 | 0.98154 | -0.35255 | 0.020805 | 0.0052141
19 | 0.97365 | -0.50691 | 0.042419 | 0.010631
20 | 0.97201 | -0.53924 | 0.0098254 | 0.0024625
21 | 0.97224 | -0.53464 | 0.017096 | 0.0042848
22 | 0.97158 | -0.54759 | 0.0013157 | 0.00032976
23 | 0.97042 | -0.57074 | 0.00030096 | 7.5429e-05
24 | 0.97041 | -0.5709 | 0.00038997 | 9.7735e-05
25 | 0.97042 | -0.57073 | 0.00014926 | 3.7408e-05
26 | 0.97042 | -0.57068 | 0 | 0
27 | 0.97024 | -0.57419 | 0.0051838 | 0.0012992
28 | 0.97039 | -0.57129 | 0.002681 | 0.00067191
29 | 0.97046 | -0.56993 | 0.00012385 | 3.104e-05
30 | 0.97048 | -0.56961 | 0.00026004 | 6.5171e-05
31 | 0.9705 | -0.56923 | 0.0012688 | 0.000318
32 | 0.97121 | -0.55503 | 0.008325 | 0.0020864
33 | 0.97126 | -0.554 | 0.0026324 | 0.00065975
34 | 0.97058 | -0.56758 | 0.00017048 | 4.2726e-05
35 | 0.97043 | -0.57068 | 0.0010788 | 0.00027038
36 | 0.97046 | -0.57002 | 0.00042523 | 0.00010657
37 | 0.97051 | -0.56893 | 0.00070354 | 0.00017632
38 | 0.97096 | -0.56007 | 0.0064544 | 0.0016176
39 | 0.97052 | -0.56877 | 0.00069414 | 0.00017397
40 | 0.97055 | -0.56824 | 0.00081615 | 0.00020455
41 | 0.97071 | -0.56511 | 0 | 0
42 | 0.97092 | -0.56083 | 0 | 0
43 | 0.97064 | -0.56623 | 0.0008116 | 0.00020341
44 | 0.97075 | -0.56406 | 0 | 0
45 | 0.97099 | -0.55941 | 0.0035468 | 0.00088891
46 | 0.9769 | -0.44353 | 0.001865 | 0.00046741
47 | 0.97683 | -0.44496 | 0.0020915 | 0.00052418
48 | 0.97857 | -0.41085 | 0.0010346 | 0.0002593
49 | 0.97659 | -0.44967 | 0 | 0
50 | 0.97944 | -0.39399 | 0 | 0
51 | 0.97634 | -0.45463 | 0.0027048 | 0.00067788
52 | 0.98009 | -0.38134 | 0 | 0
53 | 0.97485 | -0.48391 | 0.0027117 | 0.00067962
54 | 0.98067 | -0.36986 | 0 | 0
55 | 0.97889 | -0.40472 | 0.014143 | 0.0035446
56 | 0.98097 | -0.36408 | 0.0013804 | 0.00034596
57 | 0.97418 | -0.49694 | 0.0017262 | 0.00043263
58 | 0.97762 | -0.42975 | 0.011078 | 0.0027765
59 | 0.98143 | -0.3551 | 0 | 0
60 | 0.97358 | -0.50885 | 0.0016945 | 0.00042468
61 | 0.97223 | -0.5355 | 0.0020358 | 0.00051021
62 | 0.97234 | -0.53337 | 0 | 0
63 | 0.97213 | -0.53758 | 0 | 0
64 | 0.97123 | -0.55535 | 0.0057892 | 0.0014509
65 | 0.97323 | -0.51566 | 0 | 0
66 | 0.97209 | -0.53841 | 0 | 0
67 | 0.97208 | -0.53843 | 0.00054384 | 0.0001363
68 | 0.97112 | -0.55738 | 0.0033835 | 0.000848
69 | 0.97109 | -0.55813 | 0 | 0
70 | 0.971 | -0.55978 | 0.0061496 | 0.0015412
71 | 0.97097 | -0.56041 | 0.0012807 | 0.00032097
72 | 0.97211 | -0.53733 | 0 | 0
73 | 0.9717 | -0.54546 | 0.007836 | 0.0019639
74 | 0.9724 | -0.53144 | 0.0066088 | 0.0016563
75 | 0.97208 | -0.53786 | 0.0013252 | 0.00033214
76 | 0.97247 | -0.53016 | 0.01163 | 0.0029148
77 | 0.98136 | -0.35644 | 0.0017676 | 0.000443
78 | 0.98138 | -0.35608 | 0.00023578 | 5.9092e-05
79 | 0.98136 | -0.35655 | 0.00040014 | 0.00010028
80 | 0.98132 | -0.3572 | 0 | 0
81 | 0.98188 | -0.34641 | 0.013923 | 0.0034895
82 | 0.98094 | -0.3647 | 0.0010678 | 0.00026762
83 | 0.9828 | -0.32841 | 0.054127 | 0.013565
84 | 0.98074 | -0.36864 | 0.00050692 | 0.00012705
85 | 0.98335 | -0.31779 | 0.0048517 | 0.0012159
86 | 0.98065 | -0.3704 | 0 | 0
87 | 0.98341 | -0.3166 | 0.00033802 | 8.4716e-05
88 | 0.97201 | -0.53926 | 0.0034542 | 0.00086571
89 | 0.97202 | -0.53892 | 0.015827 | 0.0039667
90 | 0.97193 | -0.54087 | 0.0022962 | 0.00057548
91 | 0.97082 | -0.56289 | 0 | 0
92 | 0.97182 | -0.543 | 0.0093667 | 0.0023475
93 | 0.9711 | -0.5571 | 0 | 0
94 | 0.97083 | -0.56251 | 0.0042106 | 0.0010553
95 | 0.98441 | -0.29682 | 0.00024998 | 6.2651e-05
96 | 0.98442 | -0.29672 | 0.00026633 | 6.6748e-05
97 | 0.98047 | -0.37387 | 0.0010749 | 0.0002694
98 | 0.98048 | -0.37383 | 0.00010117 | 2.5356e-05
99 | 0.98443 | -0.29651 | 0 | 0
100 | 0.98049 | -0.37356 | 0.0010992 | 0.00027549
101 | 0.98416 | -0.30172 | 0.010702 | 0.0026823
102 | 0.98615 | -0.26337 | 0 | 0
103 | 0.98064 | -0.37071 | 0 | 0
104 | 0.99018 | -0.18591 | 0.00010662 | 2.6721e-05
105 | 0.98594 | -0.26737 | 0.0002691 | 6.7443e-05
106 | 0.99117 | -0.16708 | 0.01611 | 0.0040376
107 | 0.98495 | -0.28656 | 0.00037994 | 9.5222e-05
108 | 0.97177 | -0.54402 | 0.010398 | 0.0026059
109 | 0.98395 | -0.30597 | 0.00010989 | 2.7541e-05
110 | 0.98397 | -0.30562 | 0.006283 | 0.0015747
111 | 0.98064 | -0.37063 | 0.001816 | 0.00045514
112 | 0.99604 | -0.074527 | 0.0026025 | 0.00065224
113 | 0.99358 | -0.12119 | 0.0092954 | 0.0023297
114 | 0.99748 | -0.047308 | 0.014824 | 0.0037154
115 | 0.99862 | -0.026007 | 0.010819 | 0.0027115
116 | 1 | 0 | -0.52125 | -0.13424
117 | 0.98483 | -0.289 | 0.00011107 | 2.7837e-05
118 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.049401 | 0.012372 | -0.049384 | -0.012363 | 1.711e-05 | 9.3644e-06 | 0.075572 | 0.075572 | 0.075572 | 0.97266 | -0.52627 | 0.9723 | -0.53355 | 5.1904
1 | -0.053744 | -0.013461 | 0.053774 | 0.013477 | 2.9507e-05 | 1.6571e-05 | 0.082217 | 0.082216 | 0.082217 | 0.97266 | -0.52627 | 0.97325 | -0.51475 | 5.6468
2 | 0.041376 | 0.010356 | -0.041367 | -0.010351 | 8.7698e-06 | 4.4554e-06 | 0.063317 | 0.063317 | 0.063317 | 0.9723 | -0.53355 | 0.97207 | -0.538 | 4.3487
3 | -0.074211 | -0.018611 | 0.074231 | 0.018623 | 1.9621e-05 | 1.1749e-05 | 0.11347 | 0.11347 | 0.11347 | 0.97325 | -0.51475 | 0.97353 | -0.5092 | 7.793
4 | 0.020437 | 0.0051337 | -0.020432 | -0.0051306 | 5.1581e-06 | 3.1262e-06 | 0.031251 | 0.031251 | 0.031251 | 0.97325 | -0.51475 | 0.97298 | -0.52004 | 8.5854
5 | 0.011479 | 0.0028772 | -0.011478 | -0.0028766 | 1.2002e-06 | 6.3965e-07 | 0.017571 | 0.017572 | 0.017572 | 0.97207 | -0.538 | 0.97196 | -0.5402 | 4.8273
6 | 0.029888 | 0.0074741 | -0.02988 | -0.007471 | 7.8426e-06 | 3.0376e-06 | 0.045746 | 0.045747 | 0.045747 | 0.97207 | -0.538 | 0.97179 | -0.54352 | 3.1419
7 | -0.16595 | -0.041648 | 0.16635 | 0.041897 | 0.00039481 | 0.00024942 | 0.25368 | 0.25367 | 0.25368 | 0.97353 | -0.5092 | 0.97606 | -0.45944 | 17.4228
8 | 0.091723 | 0.023025 | -0.09169 | -0.023005 | 3.2768e-05 | 2.0088e-05 | 0.14021 | 0.14021 | 0.14021 | 0.97353 | -0.5092 | 0.97315 | -0.5167 | 9.6298
9 | 0.019074 | 0.0047904 | -0.019062 | -0.0047827 | 1.2838e-05 | 7.7169e-06 | 0.029175 | 0.029175 | 0.029175 | 0.97298 | -0.52004 | 0.97226 | -0.53415 | 8.0151
10 | 0.029282 | 0.0073217 | -0.029278 | -0.00732 | 4.4149e-06 | 1.6646e-06 | 0.044831 | 0.044832 | 0.044832 | 0.97179 | -0.54352 | 0.97163 | -0.54669 | 3.0791
11 | 0.00059789 | 0.00014937 | -0.00059788 | -0.00014984 | 1.2275e-08 | -4.7611e-07 | 0.00091532 | 0.0009155 | 0.0009155 | 0.97179 | -0.54352 | 0.97177 | -0.54395 | 0.25151
12 | -0.25082 | -0.063154 | 0.25167 | 0.063696 | 0.0008524 | 0.00054241 | 0.38249 | 0.38249 | 0.38249 | 0.97606 | -0.45944 | 0.97968 | -0.38862 | 26.2697
13 | 0.084474 | 0.021257 | -0.084295 | -0.021143 | 0.0001782 | 0.00011369 | 0.12881 | 0.12881 | 0.12881 | 0.97606 | -0.45944 | 0.97381 | -0.50369 | 35.388
14 | 0.081985 | 0.020573 | -0.081939 | -0.020545 | 4.6255e-05 | 2.8044e-05 | 0.12537 | 0.12537 | 0.12537 | 0.97315 | -0.5167 | 0.97255 | -0.52853 | 8.6106
15 | 0.017776 | 0.0044605 | -0.017767 | -0.004455 | 9.3514e-06 | 5.5674e-06 | 0.027208 | 0.027208 | 0.027208 | 0.97226 | -0.53415 | 0.97171 | -0.54519 | 7.4747
16 | 0.01018 | 0.0025336 | -0.01018 | -0.0025347 | 7.0778e-07 | -1.0869e-06 | 0.015584 | 0.015585 | 0.015585 | 0.97163 | -0.54669 | 0.97156 | -0.54816 | 1.0704
17 | -0.27692 | -0.070025 | 0.2774 | 0.07033 | 0.00048005 | 0.00030577 | 0.42084 | 0.42084 | 0.42084 | 0.97968 | -0.38862 | 0.98154 | -0.35255 | 28.9037
18 | 0.069867 | 0.017527 | -0.069856 | -0.01752 | 1.0732e-05 | 6.8373e-06 | 0.10676 | 0.10676 | 0.10676 | 0.97381 | -0.50369 | 0.97365 | -0.50691 | 29.331
19 | 0.029609 | 0.0074277 | -0.029594 | -0.0074183 | 1.5102e-05 | 9.4216e-06 | 0.045305 | 0.045305 | 0.045305 | 0.97255 | -0.52853 | 0.97201 | -0.53924 | 12.4463
20 | 0.05233 | 0.013117 | -0.052315 | -0.013108 | 1.5209e-05 | 8.4783e-06 | 0.080066 | 0.080067 | 0.080067 | 0.97255 | -0.52853 | 0.97224 | -0.53464 | 5.4991
21 | 0.017767 | 0.004455 | -0.017765 | -0.0044538 | 2.0324e-06 | 1.21e-06 | 0.027208 | 0.027208 | 0.027208 | 0.97171 | -0.54519 | 0.97158 | -0.54759 | 7.4747
22 | 0.01018 | 0.0025347 | -0.010174 | -0.0025436 | 5.7522e-06 | -8.8204e-06 | 0.015585 | 0.015589 | 0.015589 | 0.97156 | -0.54816 | 0.97096 | -0.56007 | 1.0707
23 | -0.29821 | -0.075544 | 0.29894 | 0.07601 | 0.00073005 | 0.0004653 | 0.45238 | 0.45238 | 0.45238 | 0.98154 | -0.35255 | 0.98416 | -0.30172 | 31.0699
24 | 0.027437 | 0.0068888 | -0.027407 | -0.00687 | 3.0393e-05 | 1.8879e-05 | 0.041937 | 0.041937 | 0.041937 | 0.97365 | -0.50691 | 0.97247 | -0.53016 | 11.5212
25 | 0.019768 | 0.0049558 | -0.019765 | -0.0049537 | 3.5433e-06 | 2.1399e-06 | 0.030263 | 0.030263 | 0.030263 | 0.97201 | -0.53924 | 0.97182 | -0.543 | 8.3141
26 | 0.035218 | 0.0088237 | -0.035211 | -0.0088204 | 7.1797e-06 | 3.2877e-06 | 0.0539 | 0.053901 | 0.053901 | 0.97224 | -0.53464 | 0.97202 | -0.53892 | 3.702
27 | 0.016449 | 0.004124 | -0.016442 | -0.0041196 | 7.4458e-06 | 4.3781e-06 | 0.025193 | 0.025193 | 0.025193 | 0.97158 | -0.54759 | 0.9711 | -0.5571 | 6.9212
28 | 0.00038997 | 9.7448e-05 | -0.00038997 | -9.7735e-05 | 3.139e-09 | -2.8726e-07 | 0.00059787 | 0.00059797 | 0.00059797 | 0.97042 | -0.57074 | 0.97041 | -0.5709 | 0.16428
29 | -0.00069093 | -0.00017288 | 0.00069093 | 0.00017287 | 7.5977e-11 | -2.1874e-09 | 0.0010594 | 0.0010594 | 0.0010594 | 0.97042 | -0.57074 | 0.97042 | -0.57073 | 0.29103
30 | -0.00084019 | -0.00021028 | 0.00084019 | 0.00021024 | 2.1832e-09 | -4.1945e-08 | 0.0012882 | 0.0012882 | 0.0012882 | 0.97042 | -0.57073 | 0.97042 | -0.57068 | 0.35391
31 | -0.00084019 | -0.00021024 | 0.00084022 | 0.00020967 | 2.99e-08 | -5.746e-07 | 0.0012882 | 0.001288 | 0.0012882 | 0.97042 | -0.57068 | 0.97046 | -0.56993 | 0.3539
32 | -0.0051838 | -0.0012992 | 0.0051846 | 0.0012993 | 7.1572e-07 | 8.5073e-08 | 0.0079502 | 0.0079501 | 0.0079502 | 0.97024 | -0.57419 | 0.97039 | -0.57129 | 2.1841
33 | -0.0078655 | -0.0019712 | 0.0078682 | 0.0019723 | 2.7091e-06 | 1.1201e-06 | 0.012061 | 0.012061 | 0.012061 | 0.97039 | -0.57129 | 0.97075 | -0.56406 | 3.3135
34 | -0.00096408 | -0.00024071 | 0.00096409 | 0.00024049 | 1.4645e-08 | -2.1157e-07 | 0.0014779 | 0.0014778 | 0.0014779 | 0.97046 | -0.56993 | 0.97048 | -0.56961 | 0.40602
35 | -0.0012241 | -0.00030567 | 0.0012242 | 0.00030547 | 2.2246e-08 | -1.9393e-07 | 0.0018765 | 0.0018765 | 0.0018765 | 0.97048 | -0.56961 | 0.9705 | -0.56923 | 0.51553
36 | -0.002493 | -0.00062347 | 0.0024932 | 0.00062315 | 1.9543e-07 | -3.1585e-07 | 0.0038219 | 0.0038217 | 0.0038219 | 0.9705 | -0.56923 | 0.97058 | -0.56758 | 1.05
37 | -0.008325 | -0.0020864 | 0.0083254 | 0.0020866 | 4.095e-07 | 1.7901e-07 | 0.012755 | 0.012755 | 0.012755 | 0.97121 | -0.55503 | 0.97126 | -0.554 | 3.5041
38 | 0.0026654 | 0.00066358 | -0.0026642 | -0.00066508 | 1.1241e-06 | -1.5057e-06 | 0.0040819 | 0.0040827 | 0.0040827 | 0.97126 | -0.554 | 0.97082 | -0.56289 | 1.1216
39 | -0.013623 | -0.0034099 | 0.013632 | 0.0034128 | 8.5105e-06 | 2.8653e-06 | 0.02087 | 0.020869 | 0.02087 | 0.97126 | -0.554 | 0.97193 | -0.54087 | 2.8667
40 | -0.0026636 | -0.00066588 | 0.0026642 | 0.00066508 | 5.9407e-07 | -7.9457e-07 | 0.0040831 | 0.0040827 | 0.0040831 | 0.97058 | -0.56758 | 0.97082 | -0.56289 | 1.1217
41 | -0.0010788 | -0.00027038 | 0.0010789 | 0.00026999 | 3.406e-08 | -3.8832e-07 | 0.0016542 | 0.0016541 | 0.0016542 | 0.97043 | -0.57068 | 0.97046 | -0.57002 | 0.45446
42 | -0.0015041 | -0.00037656 | 0.0015042 | 0.00037613 | 7.8189e-08 | -4.3445e-07 | 0.0023061 | 0.0023059 | 0.0023061 | 0.97046 | -0.57002 | 0.97051 | -0.56893 | 0.63354
43 | -0.0022077 | -0.00055245 | 0.0022077 | 0.00055242 | 1.6725e-08 | -3.7405e-08 | 0.0033846 | 0.0033846 | 0.0033846 | 0.97051 | -0.56893 | 0.97052 | -0.56877 | 0.92984
44 | 0.0037195 | 0.00092594 | -0.0037194 | -0.00092806 | 1.3564e-07 | -2.1175e-06 | 0.005698 | 0.0056988 | 0.0056988 | 0.97096 | -0.56007 | 0.97092 | -0.56083 | 0.3914
45 | -0.0029019 | -0.00072638 | 0.0029019 | 0.00072631 | 7.2548e-08 | -7.4361e-08 | 0.0044489 | 0.0044488 | 0.0044489 | 0.97052 | -0.56877 | 0.97055 | -0.56824 | 1.2222
46 | -0.0037181 | -0.00093085 | 0.0037186 | 0.00093065 | 5.5348e-07 | -2.0725e-07 | 0.0057001 | 0.0056999 | 0.0057001 | 0.97055 | -0.56824 | 0.97071 | -0.56511 | 1.566
47 | -0.0037186 | -0.00093065 | 0.0037194 | 0.00092806 | 7.5641e-07 | -2.5872e-06 | 0.0056999 | 0.0056988 | 0.0056999 | 0.97071 | -0.56511 | 0.97092 | -0.56083 | 0.78295
48 | -0.0008116 | -0.00020341 | 0.00081169 | 0.00020168 | 8.3425e-08 | -1.724e-06 | 0.0012442 | 0.0012436 | 0.0012442 | 0.97064 | -0.56623 | 0.97075 | -0.56406 | 0.34181
49 | -0.0086799 | -0.002174 | 0.0086819 | 0.0021749 | 1.922e-06 | 8.7201e-07 | 0.013305 | 0.013304 | 0.013305 | 0.97075 | -0.56406 | 0.97099 | -0.55941 | 3.6551
50 | -0.012229 | -0.0030638 | 0.01223 | 0.0030645 | 1.3484e-06 | 7.3632e-07 | 0.01874 | 0.01874 | 0.01874 | 0.97099 | -0.55941 | 0.9711 | -0.5571 | 5.1483
51 | 0.03023 | 0.0076142 | -0.030228 | -0.007613 | 2.0708e-06 | 1.2928e-06 | 0.04606 | 0.04606 | 0.04606 | 0.9769 | -0.44353 | 0.97683 | -0.44496 | 12.6539
52 | -0.032095 | -0.0080817 | 0.032145 | 0.0081131 | 5.0234e-05 | 3.1447e-05 | 0.048901 | 0.048901 | 0.048901 | 0.9769 | -0.44353 | 0.97857 | -0.41085 | 13.4343
53 | 0.028137 | 0.0070888 | -0.02813 | -0.0070848 | 6.3337e-06 | 3.9386e-06 | 0.042874 | 0.042874 | 0.042874 | 0.97683 | -0.44496 | 0.97659 | -0.44967 | 11.7786
54 | -0.03318 | -0.0083724 | 0.033207 | 0.0083892 | 2.6808e-05 | 1.6804e-05 | 0.050474 | 0.050474 | 0.050474 | 0.97857 | -0.41085 | 0.97944 | -0.39399 | 13.8665
55 | 0.02813 | 0.0070848 | -0.028124 | -0.0070807 | 6.6691e-06 | 4.1472e-06 | 0.042874 | 0.042874 | 0.042874 | 0.97659 | -0.44967 | 0.97634 | -0.45463 | 11.7786
56 | -0.033207 | -0.0083892 | 0.033227 | 0.0084018 | 2.0141e-05 | 1.2625e-05 | 0.050474 | 0.050474 | 0.050474 | 0.97944 | -0.39399 | 0.98009 | -0.38134 | 13.8664
57 | 0.025419 | 0.0064028 | -0.025383 | -0.0063808 | 3.5544e-05 | 2.196e-05 | 0.038752 | 0.038752 | 0.038752 | 0.97634 | -0.45463 | 0.97485 | -0.48391 | 10.6462
58 | -0.05849 | -0.014747 | 0.058522 | 0.014767 | 3.2173e-05 | 2.0043e-05 | 0.088834 | 0.088834 | 0.088834 | 0.98009 | -0.38134 | 0.98067 | -0.36986 | 12.2025
59 | 0.025263 | 0.0063454 | -0.025235 | -0.006328 | 2.8152e-05 | 1.7375e-05 | 0.03836 | 0.03836 | 0.03836 | 0.98009 | -0.38134 | 0.97889 | -0.40472 | 10.5386
60 | 0.022672 | 0.0057012 | -0.022657 | -0.0056926 | 1.4106e-05 | 8.6368e-06 | 0.034613 | 0.034613 | 0.034613 | 0.97485 | -0.48391 | 0.97418 | -0.49694 | 9.5091
61 | -0.058522 | -0.014767 | 0.058538 | 0.014776 | 1.6204e-05 | 9.2649e-06 | 0.088834 | 0.088833 | 0.088834 | 0.98067 | -0.36986 | 0.98097 | -0.36408 | 6.1012
62 | 0.011092 | 0.0027834 | -0.011078 | -0.0027765 | 1.322e-05 | 6.9042e-06 | 0.016862 | 0.016862 | 0.016862 | 0.97889 | -0.40472 | 0.97762 | -0.42975 | 4.6324
63 | -0.059919 | -0.015122 | 0.059944 | 0.015137 | 2.5756e-05 | 1.4805e-05 | 0.090927 | 0.090927 | 0.090927 | 0.98097 | -0.36408 | 0.98143 | -0.3551 | 6.245
64 | 0.020931 | 0.0052599 | -0.020919 | -0.0052527 | 1.1886e-05 | 7.2211e-06 | 0.031976 | 0.031977 | 0.031977 | 0.97418 | -0.49694 | 0.97358 | -0.50885 | 8.7848
65 | 0.0056703 | 0.0014194 | -0.0056697 | -0.0014193 | 5.6648e-07 | 1.0427e-07 | 0.0085965 | 0.0085966 | 0.0085966 | 0.98143 | -0.3551 | 0.98132 | -0.3572 | 2.3617
66 | -0.068018 | -0.017159 | 0.068047 | 0.017175 | 2.8315e-05 | 1.6687e-05 | 0.10317 | 0.10317 | 0.10317 | 0.98143 | -0.3551 | 0.98188 | -0.34641 | 7.0857
67 | 0.0024036 | 0.00060187 | -0.0024035 | -0.00060208 | 1.1186e-07 | -2.1223e-07 | 0.0036441 | 0.0036442 | 0.0036442 | 0.98143 | -0.3551 | 0.98138 | -0.35608 | 1.0012
68 | 0.019225 | 0.0048281 | -0.019219 | -0.0048243 | 6.2499e-06 | 3.76e-06 | 0.029387 | 0.029387 | 0.029387 | 0.97358 | -0.50885 | 0.97323 | -0.51566 | 8.0733
69 | -0.0025797 | -0.00064297 | 0.00258 | 0.00064258 | 2.6049e-07 | -3.8631e-07 | 0.003947 | 0.0039468 | 0.003947 | 0.97223 | -0.5355 | 0.97234 | -0.53337 | 1.0843
70 | 0.00054391 | 0.00013275 | -0.00054386 | -0.00013526 | 5.3132e-08 | -2.5061e-06 | 0.0008312 | 0.0008321 | 0.0008321 | 0.97223 | -0.5355 | 0.97213 | -0.53758 | 0.2286
71 | 0.016622 | 0.004172 | -0.016605 | -0.0041617 | 1.7405e-05 | 1.0251e-05 | 0.02544 | 0.025441 | 0.025441 | 0.97234 | -0.53337 | 0.97123 | -0.55535 | 6.9892
72 | -0.019202 | -0.0048145 | 0.019219 | 0.0048243 | 1.622e-05 | 9.7588e-06 | 0.029387 | 0.029387 | 0.029387 | 0.97234 | -0.53337 | 0.97323 | -0.51566 | 8.0734
73 | 0.00054386 | 0.00013526 | -0.00054384 | -0.00013627 | 2.1521e-08 | -1.0133e-06 | 0.0008321 | 0.00083247 | 0.00083247 | 0.97213 | -0.53758 | 0.97209 | -0.53841 | 0.2287
74 | 0.010816 | 0.0027108 | -0.010815 | -0.0027102 | 1.0472e-06 | 5.4436e-07 | 0.016571 | 0.016571 | 0.016571 | 0.97123 | -0.55535 | 0.97112 | -0.55738 | 4.5525
75 | 0.00054384 | 0.00013627 | -0.00054384 | -0.0001363 | 5.8501e-10 | -2.7532e-08 | 0.00083247 | 0.00083248 | 0.00083248 | 0.97209 | -0.53841 | 0.97208 | -0.53843 | 0.2287
76 | 0.0074312 | 0.0018622 | -0.007431 | -0.0018621 | 2.6427e-07 | 1.0189e-07 | 0.011387 | 0.011387 | 0.011387 | 0.97112 | -0.55738 | 0.97109 | -0.55813 | 3.1282
77 | 0.007431 | 0.0018621 | -0.0074304 | -0.0018619 | 5.8537e-07 | 2.257e-07 | 0.011387 | 0.011387 | 0.011387 | 0.97109 | -0.55813 | 0.971 | -0.55978 | 3.1282
78 | 0.0012807 | 0.00032067 | -0.0012807 | -0.00032097 | 3.8503e-08 | -3.0506e-07 | 0.0019626 | 0.0019627 | 0.0019627 | 0.971 | -0.55978 | 0.97097 | -0.56041 | 0.5392
79 | 0.0078391 | 0.0019651 | -0.007836 | -0.0019639 | 3.0341e-06 | 1.2455e-06 | 0.012 | 0.012 | 0.012 | 0.97211 | -0.53733 | 0.9717 | -0.54546 | 3.2966
80 | -0.0091643 | -0.002297 | 0.0091669 | 0.0022982 | 2.5726e-06 | 1.2141e-06 | 0.014028 | 0.014028 | 0.014028 | 0.97211 | -0.53733 | 0.9724 | -0.53144 | 3.8539
81 | 0.0013253 | 0.00033189 | -0.0013252 | -0.00033214 | 3.3174e-08 | -2.4528e-07 | 0.0020285 | 0.0020286 | 0.0020286 | 0.97211 | -0.53733 | 0.97208 | -0.53786 | 0.55731
82 | -0.015776 | -0.0039546 | 0.015777 | 0.0039551 | 9.648e-07 | 5.6271e-07 | 0.024141 | 0.024141 | 0.024141 | 0.9724 | -0.53144 | 0.97247 | -0.53016 | 6.6321
83 | -0.0021677 | -0.00054308 | 0.0021678 | 0.00054299 | 3.678e-08 | -9.1177e-08 | 0.0032868 | 0.0032867 | 0.0032868 | 0.98136 | -0.35644 | 0.98138 | -0.35608 | 0.90296
84 | 0.00040014 | 0.00010008 | -0.00040014 | -0.00010028 | 2.1985e-09 | -1.9984e-07 | 0.00060665 | 0.00060673 | 0.00060673 | 0.98136 | -0.35644 | 0.98136 | -0.35655 | 0.16668
85 | 0.0056697 | 0.0014193 | -0.0056677 | -0.0014189 | 2.0232e-06 | 3.7291e-07 | 0.0085966 | 0.0085969 | 0.0085969 | 0.98132 | -0.3572 | 0.98094 | -0.3647 | 2.3618
86 | -0.08197 | -0.020665 | 0.082041 | 0.020708 | 7.0688e-05 | 4.2768e-05 | 0.12427 | 0.12427 | 0.12427 | 0.98188 | -0.34641 | 0.9828 | -0.32841 | 8.5348
87 | 0.0045999 | 0.0011513 | -0.004599 | -0.0011514 | 8.6275e-07 | -4.4316e-08 | 0.0069771 | 0.0069774 | 0.0069774 | 0.98094 | -0.3647 | 0.98074 | -0.36864 | 1.9169
88 | -0.13617 | -0.034273 | 0.13624 | 0.034316 | 6.9125e-05 | 4.3361e-05 | 0.20622 | 0.20622 | 0.20622 | 0.9828 | -0.32841 | 0.98335 | -0.31779 | 14.1633
89 | 0.0040921 | 0.0010243 | -0.0040918 | -0.0010244 | 3.4311e-07 | -7.9938e-08 | 0.0062082 | 0.0062083 | 0.0062083 | 0.98074 | -0.36864 | 0.98065 | -0.3704 | 1.7056
90 | -0.14109 | -0.035532 | 0.1411 | 0.035537 | 8.0488e-06 | 5.0557e-06 | 0.21356 | 0.21356 | 0.21356 | 0.98335 | -0.31779 | 0.98341 | -0.3166 | 14.6675
91 | 0.0018161 | 0.00045507 | -0.001816 | -0.00045514 | 1.9411e-08 | -7.3579e-08 | 0.0027556 | 0.0027557 | 0.0027557 | 0.98065 | -0.3704 | 0.98064 | -0.37063 | 0.75705
92 | 0.0022757 | 0.00056933 | -0.0022757 | -0.0005694 | 3.2715e-08 | -7.1388e-08 | 0.0034527 | 0.0034527 | 0.0034527 | 0.98065 | -0.3704 | 0.98064 | -0.37071 | 0.94856
93 | -0.14143 | -0.035622 | 0.14151 | 0.035667 | 7.1934e-05 | 4.5187e-05 | 0.21407 | 0.21407 | 0.21407 | 0.98341 | -0.3166 | 0.98395 | -0.30597 | 14.7026
94 | -0.019383 | -0.0048537 | 0.019384 | 0.0048537 | 3.1858e-07 | 1.252e-08 | 0.029672 | 0.029672 | 0.029672 | 0.97201 | -0.53926 | 0.97202 | -0.53892 | 2.0379
95 | 0.015929 | 0.003988 | -0.015928 | -0.0039883 | 1.2222e-06 | -3.0479e-07 | 0.024384 | 0.024384 | 0.024384 | 0.97201 | -0.53926 | 0.97193 | -0.54087 | 1.6747
96 | 0.010398 | 0.0026062 | -0.010398 | -0.0026059 | 5.0377e-07 | 2.5676e-07 | 0.015921 | 0.015921 | 0.015921 | 0.97182 | -0.543 | 0.97177 | -0.54402 | 4.374
97 | 0.0042117 | 0.0010551 | -0.0042106 | -0.0010553 | 1.086e-06 | -1.6502e-07 | 0.0064533 | 0.0064536 | 0.0064536 | 0.9711 | -0.5571 | 0.97083 | -0.56251 | 1.773
98 | -0.00024998 | -6.2651e-05 | 0.00024998 | 6.2371e-05 | 1.1848e-09 | -2.8064e-07 | 0.00037787 | 0.00037777 | 0.00037787 | 0.98441 | -0.29682 | 0.98442 | -0.29672 | 0.10381
99 | -0.00051631 | -0.00012912 | 0.00051631 | 0.00012883 | 5.2832e-09 | -2.9081e-07 | 0.00078034 | 0.00078023 | 0.00078034 | 0.98442 | -0.29672 | 0.98443 | -0.29651 | 0.21438
100 | -0.0010749 | -0.0002694 | 0.0010749 | 0.00026938 | 1.955e-09 | -2.3455e-08 | 0.0016314 | 0.0016314 | 0.0016314 | 0.98047 | -0.37387 | 0.98048 | -0.37383 | 0.44818
101 | -0.0011761 | -0.00029474 | 0.0011761 | 0.00029459 | 1.5133e-08 | -1.5008e-07 | 0.0017849 | 0.0017848 | 0.0017849 | 0.98048 | -0.37383 | 0.98049 | -0.37356 | 0.49036
102 | 0.30972 | 0.078742 | -0.30964 | -0.078692 | 7.7736e-05 | 4.9559e-05 | 0.46856 | 0.46856 | 0.46856 | 0.98443 | -0.29651 | 0.98416 | -0.30172 | 32.1812
103 | -0.31024 | -0.07887 | 0.31073 | 0.079187 | 0.00049606 | 0.00031625 | 0.46934 | 0.46934 | 0.46934 | 0.98443 | -0.29651 | 0.98615 | -0.26337 | 32.2348
104 | -0.0022753 | -0.00057008 | 0.0022757 | 0.0005694 | 3.0941e-07 | -6.7494e-07 | 0.0034531 | 0.0034527 | 0.0034531 | 0.98049 | -0.37356 | 0.98064 | -0.37071 | 0.94864
105 | -0.45969 | -0.11684 | 0.46142 | 0.11794 | 0.0017217 | 0.0010999 | 0.69422 | 0.69422 | 0.69422 | 0.98615 | -0.26337 | 0.99018 | -0.18591 | 47.6801
106 | 0.14896 | 0.03765 | -0.14893 | -0.037632 | 2.8576e-05 | 1.7981e-05 | 0.22488 | 0.22488 | 0.22488 | 0.98615 | -0.26337 | 0.98594 | -0.26737 | 15.4454
107 | -0.46152 | -0.11796 | 0.46194 | 0.11823 | 0.00042065 | 0.00026874 | 0.69438 | 0.69438 | 0.69438 | 0.99018 | -0.18591 | 0.99117 | -0.16708 | 47.691
108 | 0.14866 | 0.037565 | -0.14853 | -0.037479 | 0.00013666 | 8.5989e-05 | 0.22448 | 0.22448 | 0.22448 | 0.98594 | -0.26737 | 0.98495 | -0.28656 | 15.4175
109 | -0.47805 | -0.12227 | 0.47912 | 0.12295 | 0.0010644 | 0.00068007 | 0.71857 | 0.71857 | 0.71857 | 0.99117 | -0.16708 | 0.99358 | -0.12119 | 49.3521
110 | 0.14815 | 0.037384 | -0.14813 | -0.037373 | 1.7284e-05 | 1.0874e-05 | 0.2239 | 0.2239 | 0.2239 | 0.98495 | -0.28656 | 0.98483 | -0.289 | 15.3781
111 | -0.14162 | -0.035695 | 0.14162 | 0.035696 | 2.4016e-06 | 1.5087e-06 | 0.21424 | 0.21424 | 0.21424 | 0.98395 | -0.30597 | 0.98397 | -0.30562 | 14.714
112 | -0.1479 | -0.037271 | 0.14802 | 0.037345 | 0.00011767 | 7.4036e-05 | 0.22374 | 0.22374 | 0.22374 | 0.98397 | -0.30562 | 0.98483 | -0.289 | 15.3666
113 | 0.48952 | 0.12599 | -0.48841 | -0.12528 | 0.0011082 | 0.00070811 | 0.73249 | 0.73249 | 0.73249 | 0.99604 | -0.074527 | 0.99358 | -0.12119 | 50.3082
114 | -0.49212 | -0.12664 | 0.49278 | 0.12706 | 0.00065233 | 0.00041682 | 0.73637 | 0.73637 | 0.73637 | 0.99604 | -0.074527 | 0.99748 | -0.047308 | 50.5752
115 | -0.5076 | -0.13077 | 0.50813 | 0.13111 | 0.00052691 | 0.00033671 | 0.75849 | 0.75849 | 0.75849 | 0.99748 | -0.047308 | 0.99862 | -0.026007 | 52.094
116 | -0.51895 | -0.13382 | 0.5196 | 0.13424 | 0.00065831 | 0.00042071 | 0.77461 | 0.77461 | 0.77461 | 0.99862 | -0.026007 | 1 | 0 | 53.2012

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.5594 | 0.1438

## res_load
| p_mw | q_mvar
0 | 0.0043437 | 0.0010886
1 | 0.0080078 | 0.0020069
2 | 0.0013574 | 0.0003402
3 | 0.011478 | 0.0028766
4 | 0.0097051 | 0.0024323
5 | 0.0012854 | 0.00032216
6 | 0.019098 | 0.0047863
7 | 0.00059788 | 0.00014984
8 | 0.02525 | 0.0063283
9 | 0.014429 | 0.0036162
10 | 0.020805 | 0.0052141
11 | 0.042419 | 0.010631
12 | 0.0098254 | 0.0024625
13 | 0.017096 | 0.0042848
14 | 0.0013157 | 0.00032976
15 | 0.00030096 | 7.5429e-05
16 | 0.00038997 | 9.7735e-05
17 | 0.00014926 | 3.7408e-05
18 | 0.0051838 | 0.0012992
19 | 0.002681 | 0.00067191
20 | 0.00012385 | 3.104e-05
21 | 0.00026004 | 6.5171e-05
22 | 0.0012688 | 0.000318
23 | 0.008325 | 0.0020864
24 | 0.0026324 | 0.00065975
25 | 0.00017048 | 4.2726e-05
26 | 0.0010788 | 0.00027038
27 | 0.00042523 | 0.00010657
28 | 0.00070354 | 0.00017632
29 | 0.0064544 | 0.0016176
30 | 0.00069414 | 0.00017397
31 | 0.00081615 | 0.00020455
32 | 0.0008116 | 0.00020341
33 | 0.0035468 | 0.00088891
34 | 0.001865 | 0.00046741
35 | 0.0020915 | 0.00052418
36 | 0.0010346 | 0.0002593
37 | 0.0027048 | 0.00067788
38 | 0.0027117 | 0.00067962
39 | 0.014143 | 0.0035446
40 | 0.0013804 | 0.00034596
41 | 0.0017262 | 0.00043263
42 | 0.011078 | 0.0027765
43 | 0.0016945 | 0.00042468
44 | 0.0020358 | 0.00051021
45 | 0.0057892 | 0.0014509
46 | 0.00054384 | 0.0001363
47 | 0.0033835 | 0.000848
48 | 0.0061496 | 0.0015412
49 | 0.0012807 | 0.00032097
50 | 0.007836 | 0.0019639
51 | 0.0066088 | 0.0016563
52 | 0.0013252 | 0.00033214
53 | 0.01163 | 0.0029148
54 | 0.0017676 | 0.000443
55 | 0.00023578 | 5.9092e-05
56 | 0.00040014 | 0.00010028
57 | 0.013923 | 0.0034895
58 | 0.0010678 | 0.00026762
59 | 0.054127 | 0.013565
60 | 0.00050692 | 0.00012705
61 | 0.0048517 | 0.0012159
62 | 0.00033802 | 8.4716e-05
63 | 0.0034542 | 0.00086571
64 | 0.015827 | 0.0039667
65 | 0.0022962 | 0.00057548
66 | 0.0093667 | 0.0023475
67 | 0.0042106 | 0.0010553
68 | 0.00024998 | 6.2651e-05
69 | 0.00026633 | 6.6748e-05
70 | 0.0010749 | 0.0002694
71 | 0.00010117 | 2.5356e-05
72 | 0.0010992 | 0.00027549
73 | 0.010702 | 0.0026823
74 | 0.00010662 | 2.6721e-05
75 | 0.0002691 | 6.7443e-05
76 | 0.01611 | 0.0040376
77 | 0.00037994 | 9.5222e-05
78 | 0.010398 | 0.0026059
79 | 0.00010989 | 2.7541e-05
80 | 0.006283 | 0.0015747
81 | 0.001816 | 0.00045514
82 | 0.0026025 | 0.00065224
83 | 0.0092954 | 0.0023297
84 | 0.014824 | 0.0037154
85 | 0.010819 | 0.0027115
86 | 0.038142 | 0.0095593
87 | 0.00011107 | 2.7837e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1