## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_118-10_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_118-10_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_118-10_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_118-10_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_118-10_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_118-10_0_4_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_118-10_0_4_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_118-10_0_4_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_118-10_0_4_node_52 | 0.4 | n |  | TRUE
9 | bus_LV_118-10_0_4_node_12 | 0.4 | n |  | TRUE
10 | bus_LV_118-10_0_4_node_76 | 0.4 | n |  | TRUE
11 | bus_LV_118-10_0_4_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_118-10_0_4_node_57 | 0.4 | n |  | TRUE
13 | bus_LV_118-10_0_4_node_61 | 0.4 | n |  | TRUE
14 | bus_LV_118-10_0_4_node_53 | 0.4 | n |  | TRUE
15 | bus_LV_118-10_0_4_node_66 | 0.4 | n |  | TRUE
16 | bus_LV_118-10_0_4_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_118-10_0_4_node_20 | 0.4 | n |  | TRUE
18 | bus_LV_118-10_0_4_node_67 | 0.4 | n |  | TRUE
19 | bus_LV_118-10_0_4_node_14 | 0.4 | n |  | TRUE
20 | bus_LV_118-10_0_4_node_70 | 0.4 | n |  | TRUE
21 | bus_LV_118-10_0_4_node_75 | 0.4 | n |  | TRUE
22 | bus_LV_118-10_0_4_node_69 | 0.4 | n |  | TRUE
23 | bus_LV_118-10_0_4_node_51 | 0.4 | n |  | TRUE
24 | bus_LV_118-10_0_4_node_9 | 0.4 | n |  | TRUE
25 | bus_LV_118-10_0_4_node_11 | 0.4 | n |  | TRUE
26 | bus_LV_118-10_0_4_node_13 | 0.4 | n |  | TRUE
27 | bus_LV_118-10_0_4_node_49 | 0.4 | n |  | TRUE
28 | bus_LV_118-10_0_4_node_50 | 0.4 | n |  | TRUE
29 | bus_LV_118-10_0_4_node_19 | 0.4 | n |  | TRUE
30 | bus_LV_118-10_0_4_node_99 | 0.4 | n |  | TRUE
31 | bus_LV_118-10_0_4_node_23 | 0.4 | n |  | TRUE
32 | bus_LV_118-10_0_4_node_21 | 0.4 | n |  | TRUE
33 | bus_LV_118-10_0_4_node_86 | 0.4 | n |  | TRUE
34 | bus_LV_118-10_0_4_node_39 | 0.4 | n |  | TRUE
35 | bus_LV_118-10_0_4_node_68 | 0.4 | n |  | TRUE
36 | bus_LV_118-10_0_4_node_22 | 0.4 | n |  | TRUE
37 | bus_LV_118-10_0_4_node_125 | 0.4 | n |  | TRUE
38 | bus_LV_118-10_0_4_node_24 | 0.4 | n |  | TRUE
39 | bus_LV_118-10_0_4_node_28 | 0.4 | n |  | TRUE
40 | bus_LV_118-10_0_4_node_27 | 0.4 | n |  | TRUE
41 | bus_LV_118-10_0_4_node_118 | 0.4 | n |  | TRUE
42 | bus_LV_118-10_0_4_node_26 | 0.4 | n |  | TRUE
43 | bus_LV_118-10_0_4_node_106 | 0.4 | n |  | TRUE
44 | bus_LV_118-10_0_4_node_97 | 0.4 | n |  | TRUE
45 | bus_LV_118-10_0_4_node_110 | 0.4 | n |  | TRUE
46 | bus_LV_118-10_0_4_node_126 | 0.4 | n |  | TRUE
47 | bus_LV_118-10_0_4_node_29 | 0.4 | n |  | TRUE
48 | bus_LV_118-10_0_4_node_59 | 0.4 | n |  | TRUE
49 | bus_LV_118-10_0_4_node_60 | 0.4 | n |  | TRUE
50 | bus_LV_118-10_0_4_node_32 | 0.4 | n |  | TRUE
51 | bus_LV_118-10_0_4_node_62 | 0.4 | n |  | TRUE
52 | bus_LV_118-10_0_4_node_38 | 0.4 | n |  | TRUE
53 | bus_LV_118-10_0_4_node_77 | 0.4 | n |  | TRUE
54 | bus_LV_118-10_0_4_node_127 | 0.4 | n |  | TRUE
55 | bus_LV_118-10_0_4_node_46 | 0.4 | n |  | TRUE
56 | bus_LV_118-10_0_4_node_107 | 0.4 | n |  | TRUE
57 | bus_LV_118-10_0_4_node_112 | 0.4 | n |  | TRUE
58 | bus_LV_118-10_0_4_node_85 | 0.4 | n |  | TRUE
59 | bus_LV_118-10_0_4_node_115 | 0.4 | n |  | TRUE
60 | bus_LV_118-10_0_4_node_117 | 0.4 | n |  | TRUE
61 | bus_LV_118-10_0_4_node_113 | 0.4 | n |  | TRUE
62 | bus_LV_118-10_0_4_node_124 | 0.4 | n |  | TRUE
63 | bus_LV_118-10_0_4_node_111 | 0.4 | n |  | TRUE
64 | bus_LV_118-10_0_4_node_109 | 0.4 | n |  | TRUE
65 | bus_LV_118-10_0_4_node_96 | 0.4 | n |  | TRUE
66 | bus_LV_118-10_0_4_node_64 | 0.4 | n |  | TRUE
67 | bus_LV_118-10_0_4_node_72 | 0.4 | n |  | TRUE
68 | bus_LV_118-10_0_4_node_74 | 0.4 | n |  | TRUE
69 | bus_LV_118-10_0_4_node_54 | 0.4 | n |  | TRUE
70 | bus_LV_118-10_0_4_node_55 | 0.4 | n |  | TRUE
71 | bus_LV_118-10_0_4_node_71 | 0.4 | n |  | TRUE
72 | bus_LV_118-10_0_4_node_122 | 0.4 | n |  | TRUE
73 | bus_LV_118-10_0_4_node_121 | 0.4 | n |  | TRUE
74 | bus_LV_118-10_0_4_node_120 | 0.4 | n |  | TRUE
75 | bus_LV_118-10_0_4_node_95 | 0.4 | n |  | TRUE
76 | bus_LV_118-10_0_4_node_93 | 0.4 | n |  | TRUE
77 | bus_LV_118-10_0_4_node_105 | 0.4 | n |  | TRUE
78 | bus_LV_118-10_0_4_node_65 | 0.4 | n |  | TRUE
79 | bus_LV_118-10_0_4_node_56 | 0.4 | n |  | TRUE
80 | bus_LV_118-10_0_4_node_58 | 0.4 | n |  | TRUE
81 | bus_LV_118-10_0_4_node_73 | 0.4 | n |  | TRUE
82 | bus_LV_118-10_0_4_node_63 | 0.4 | n |  | TRUE
83 | bus_LV_118-10_0_4_node_90 | 0.4 | n |  | TRUE
84 | bus_LV_118-10_0_4_node_91 | 0.4 | n |  | TRUE
85 | bus_LV_118-10_0_4_node_92 | 0.4 | n |  | TRUE
86 | bus_LV_118-10_0_4_node_94 | 0.4 | n |  | TRUE
87 | bus_LV_118-10_0_4_node_98 | 0.4 | n |  | TRUE
88 | bus_LV_118-10_0_4_node_104 | 0.4 | n |  | TRUE
89 | bus_LV_118-10_0_4_node_102 | 0.4 | n |  | TRUE
90 | bus_LV_118-10_0_4_node_114 | 0.4 | n |  | TRUE
91 | bus_LV_118-10_0_4_node_116 | 0.4 | n |  | TRUE
92 | bus_MV_9_2_node_113 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_118-10_0_4_load_0 | 0 | 0.0067505 | 0.0016918 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_118-10_0_4_load_1 | 1 | 0.00096874 | 0.00024279 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_118-10_0_4_load_3 | 3 | 0.0015899 | 0.00039846 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_118-10_0_4_load_4 | 4 | 0.0010744 | 0.00026928 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_118-10_0_4_load_7 | 6 | 0.00094029 | 0.00023566 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_118-10_0_4_load_12 | 9 | 0.0020254 | 0.00050761 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_118-10_0_4_load_76 | 10 | 0.0054574 | 0.0013678 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_118-10_0_4_load_8 | 11 | 0.00058786 | 0.00014733 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_118-10_0_4_load_61 | 13 | 0.0028738 | 0.00072025 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_118-10_0_4_load_10 | 16 | 0.0027961 | 0.00070077 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_118-10_0_4_load_67 | 18 | 0.00086014 | 0.00021557 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_118-10_0_4_load_75 | 21 | 0.0044537 | 0.0011162 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_118-10_0_4_load_51 | 23 | 0.0052822 | 0.0013238 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_118-10_0_4_load_9 | 24 | 0.0010754 | 0.00026953 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_118-10_0_4_load_11 | 25 | 0.0019105 | 0.00047882 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_118-10_0_4_load_49 | 27 | 0.0053321 | 0.0013363 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_118-10_0_4_load_50 | 28 | 0.0060645 | 0.0015199 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_118-10_0_4_load_99 | 30 | 0.00050015 | 0.00012535 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_118-10_0_4_load_86 | 33 | 0.0074008 | 0.0018548 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_118-10_0_4_load_68 | 35 | 0.081242 | 0.020361 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_118-10_0_4_load_125 | 37 | 0.0054528 | 0.0013666 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_118-10_0_4_load_118 | 41 | 0.0025814 | 0.00064697 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_118-10_0_4_load_106 | 43 | 0.0029203 | 0.0007319 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_118-10_0_4_load_97 | 44 | 0.0038632 | 0.0009682 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_118-10_0_4_load_110 | 45 | 0.00383 | 0.00095989 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_118-10_0_4_load_126 | 46 | 0.0023262 | 0.000583 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_118-10_0_4_load_59 | 48 | 0.0012924 | 0.00032389 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_118-10_0_4_load_62 | 51 | 0.0016906 | 0.00042371 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_118-10_0_4_load_77 | 53 | 0.019612 | 0.0049151 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_118-10_0_4_load_127 | 54 | 0.006832 | 0.0017123 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_118-10_0_4_load_107 | 56 | 0.0078861 | 0.0019765 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_118-10_0_4_load_112 | 57 | 0.0049197 | 0.001233 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_118-10_0_4_load_85 | 58 | 0.028685 | 0.0071891 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_118-10_0_4_load_117 | 60 | 0.004029 | 0.0010098 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_118-10_0_4_load_113 | 61 | 0.0044547 | 0.0011165 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_118-10_0_4_load_124 | 62 | 0.0064161 | 0.001608 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_118-10_0_4_load_111 | 63 | 0.0028445 | 0.0007129 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_118-10_0_4_load_109 | 64 | 0.0065547 | 0.0016428 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_118-10_0_4_load_96 | 65 | 0.0009881 | 0.00024764 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_118-10_0_4_load_64 | 66 | 0.001831 | 0.00045889 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_118-10_0_4_load_72 | 67 | 0.0017409 | 0.00043632 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_118-10_0_4_load_74 | 68 | 0.0019953 | 0.00050006 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_118-10_0_4_load_54 | 69 | 0.0023209 | 0.00058167 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_118-10_0_4_load_71 | 71 | 0.0015942 | 0.00039955 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_118-10_0_4_load_121 | 73 | 0.0065802 | 0.0016492 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_118-10_0_4_load_120 | 74 | 0.0067508 | 0.0016919 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_118-10_0_4_load_95 | 75 | 0.0015302 | 0.00038349 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_118-10_0_4_load_93 | 76 | 0.0028263 | 0.00070833 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_118-10_0_4_load_65 | 78 | 0.0015964 | 0.00040009 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_118-10_0_4_load_56 | 79 | 0.0013379 | 0.0003353 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_118-10_0_4_load_58 | 80 | 0.0018115 | 0.00045401 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_118-10_0_4_load_73 | 81 | 0.0025139 | 0.00063005 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_118-10_0_4_load_63 | 82 | 0.0013113 | 0.00032865 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_118-10_0_4_load_90 | 83 | 0.0013755 | 0.00034473 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_118-10_0_4_load_91 | 84 | 0.0017257 | 0.00043251 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_118-10_0_4_load_92 | 85 | 0.0025901 | 0.00064914 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_118-10_0_4_load_98 | 87 | 0.00028843 | 7.2287e-05 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_118-10_0_4_load_104 | 88 | 0.0010178 | 0.00025508 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_118-10_0_4_load_102 | 89 | 0.0011212 | 0.000281 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_118-10_0_4_load_114 | 90 | 0.0065947 | 0.0016528 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_118-10_0_4_load_116 | 91 | 0.0054613 | 0.0013687 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 32 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_118-10_0_4_line_0 |  | 0 | 1 | 0.024362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_118-10_0_4_line_1 |  | 0 | 2 | 0.012761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_118-10_0_4_line_2 |  | 1 | 3 | 0.037476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_118-10_0_4_line_3 |  | 2 | 4 | 0.025371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_118-10_0_4_line_4 |  | 2 | 5 | 0.004129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_118-10_0_4_line_5 |  | 4 | 6 | 0.016185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_118-10_0_4_line_6 |  | 5 | 10 | 0.013901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_118-10_0_4_line_7 |  | 6 | 11 | 0.019243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_118-10_0_4_line_8 |  | 7 | 8 | 0.006145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_118-10_0_4_line_9 |  | 7 | 9 | 0.023086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_118-10_0_4_line_10 |  | 8 | 12 | 0.006169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_118-10_0_4_line_11 |  | 8 | 13 | 0.019726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_118-10_0_4_line_12 |  | 9 | 16 | 0.016825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_118-10_0_4_line_13 |  | 10 | 14 | 0.037027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_118-10_0_4_line_14 |  | 11 | 19 | 0.011269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_118-10_0_4_line_15 |  | 12 | 15 | 0.002901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_118-10_0_4_line_16 |  | 12 | 78 | 0.041158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_118-10_0_4_line_17 |  | 12 | 70 | 0.006061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_118-10_0_4_line_18 |  | 13 | 50 | 0.038243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_118-10_0_4_line_19 |  | 14 | 15 | 0.005925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_118-10_0_4_line_20 |  | 16 | 24 | 0.013631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_118-10_0_4_line_21 |  | 17 | 18 | 0.022904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_118-10_0_4_line_22 |  | 17 | 19 | 0.005649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_118-10_0_4_line_23 |  | 18 | 36 | 0.012934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_118-10_0_4_line_24 |  | 19 | 23 | 0.021819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_118-10_0_4_line_25 |  | 20 | 21 | 0.016237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_118-10_0_4_line_26 |  | 20 | 22 | 0.001627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_118-10_0_4_line_27 |  | 22 | 36 | 0.029151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_118-10_0_4_line_28 |  | 24 | 25 | 0.00029119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_118-10_0_4_line_29 |  | 25 | 26 | 0.030333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_118-10_0_4_line_30 |  | 26 | 27 | 0.049899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_118-10_0_4_line_31 |  | 27 | 28 | 0.0066422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_118-10_0_4_line_32 |  | 29 | 30 | 0.017483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_118-10_0_4_line_33 |  | 29 | 31 | 0.016721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_118-10_0_4_line_34 |  | 29 | 32 | 0.048584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_118-10_0_4_line_35 |  | 29 | 33 | 0.029073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_118-10_0_4_line_36 |  | 30 | 42 | 0.01251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_118-10_0_4_line_37 |  | 31 | 37 | 0.01999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_118-10_0_4_line_38 |  | 32 | 34 | 0.050679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_118-10_0_4_line_39 |  | 32 | 35 | 0.052103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
40 | LV_118-10_0_4_line_40 |  | 33 | 58 | 0.11308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_118-10_0_4_line_41 |  | 34 | 54 | 0.070042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_118-10_0_4_line_42 |  | 34 | 52 | 0.035361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_118-10_0_4_line_43 |  | 35 | 36 | 0.0082507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_118-10_0_4_line_44 |  | 37 | 62 | 0.012496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_118-10_0_4_line_45 |  | 38 | 39 | 0.0048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_118-10_0_4_line_46 |  | 38 | 40 | 0.0078537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_118-10_0_4_line_47 |  | 38 | 41 | 0.0066118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_118-10_0_4_line_48 |  | 39 | 46 | 0.0079071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_118-10_0_4_line_49 |  | 40 | 45 | 0.014687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_118-10_0_4_line_50 |  | 41 | 60 | 0.026857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_118-10_0_4_line_51 |  | 42 | 43 | 0.01638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_118-10_0_4_line_52 |  | 42 | 44 | 0.017007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_118-10_0_4_line_53 |  | 43 | 64 | 0.026655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_118-10_0_4_line_54 |  | 44 | 65 | 0.05215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_118-10_0_4_line_55 |  | 45 | 64 | 0.021961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_118-10_0_4_line_56 |  | 47 | 48 | 0.012532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_118-10_0_4_line_57 |  | 47 | 49 | 0.002572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_118-10_0_4_line_58 |  | 48 | 66 | 0.00023364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_118-10_0_4_line_59 |  | 49 | 67 | 0.01451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_118-10_0_4_line_60 |  | 49 | 68 | 0.0067721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_118-10_0_4_line_61 |  | 50 | 51 | 0.012397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_118-10_0_4_line_62 |  | 52 | 53 | 0.02152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_118-10_0_4_line_63 |  | 55 | 56 | 0.0011907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_118-10_0_4_line_64 |  | 55 | 57 | 0.018913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_118-10_0_4_line_65 |  | 56 | 77 | 0.020203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_118-10_0_4_line_66 |  | 57 | 63 | 0.01712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_118-10_0_4_line_67 |  | 59 | 60 | 0.010071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_118-10_0_4_line_68 |  | 59 | 61 | 0.031016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_118-10_0_4_line_69 |  | 61 | 90 | 0.011704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_118-10_0_4_line_70 |  | 62 | 72 | 0.019742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_118-10_0_4_line_71 |  | 65 | 86 | 0.019146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_118-10_0_4_line_72 |  | 66 | 82 | 0.028037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_118-10_0_4_line_73 |  | 67 | 71 | 0.022012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_118-10_0_4_line_74 |  | 68 | 81 | 0.026391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_118-10_0_4_line_75 |  | 69 | 70 | 0.016239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_118-10_0_4_line_76 |  | 70 | 79 | 0.019161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_118-10_0_4_line_77 |  | 70 | 80 | 0.002725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_118-10_0_4_line_78 |  | 72 | 73 | 0.01877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_118-10_0_4_line_79 |  | 73 | 74 | 0.021768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_118-10_0_4_line_80 |  | 75 | 76 | 0.016209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_118-10_0_4_line_81 |  | 76 | 84 | 0.005348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_118-10_0_4_line_82 |  | 77 | 88 | 0.037166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_118-10_0_4_line_83 |  | 77 | 87 | 0.013511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_118-10_0_4_line_84 |  | 80 | 81 | 0.020794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_118-10_0_4_line_85 |  | 83 | 84 | 0.0025964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_118-10_0_4_line_86 |  | 83 | 85 | 0.012465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_118-10_0_4_line_87 |  | 85 | 86 | 0.0086401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_118-10_0_4_line_88 |  | 86 | 87 | 0.038042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_118-10_0_4_line_89 |  | 88 | 89 | 0.039454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_118-10_0_4_line_90 |  | 90 | 91 | 0.016791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_118-10_0_4_trafo_21 | 0.63 MVA 20/0.4 kV | 92 | 32 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2706462.7234 | 1234895.5964 | 2706462.6202 | 1234895.0828 | 2706463.6083 | 1234887.2612 | 2706466.4579 | 1234876.1148 | 2706467.1221 | 1234871.7152
1 | 2706467.1095 | 1234907.3282 | 2706464.2118 | 1234903.0063 | 2706462.7234 | 1234895.5964
2 | 2706467.1221 | 1234871.7152 | 2706470.3238 | 1234850.5089 | 2706472.1662 | 1234834.586
3 | 2706467.1095 | 1234907.3282 | 2706486.2448 | 1234890.6689
4 | 2706469.41 | 1234910.7609 | 2706467.1095 | 1234907.3282
5 | 2706486.2448 | 1234890.6689 | 2706494.2035 | 1234883.74 | 2706498.4107 | 1234879.9944
6 | 2706469.41 | 1234910.7609 | 2706459.0576 | 1234920.0383
7 | 2706512.7828 | 1234867.199 | 2706498.4107 | 1234879.9944
8 | 2706427.5553 | 1234941.8683 | 2706425.95 | 1234947.7996
9 | 2706427.5553 | 1234941.8683 | 2706415.8297 | 1234926.1796 | 2706414.0352 | 1234923.1747
10 | 2706425.95 | 1234947.7996 | 2706428.6898 | 1234953.3307
11 | 2706425.95 | 1234947.7996 | 2706412.2536 | 1234961.9956
12 | 2706405.4085 | 1234908.729 | 2706414.0352 | 1234923.1747
13 | 2706432.6955 | 1234945.6743 | 2706434.5095 | 1234942.0374 | 2706459.0576 | 1234920.0383
14 | 2706521.1997 | 1234859.7055 | 2706512.7828 | 1234867.199
15 | 2706430.733 | 1234951.2657 | 2706428.6898 | 1234953.3307
16 | 2706428.6898 | 1234953.3307 | 2706400.7203 | 1234983.5251
17 | 2706428.6898 | 1234953.3307 | 2706432.0131 | 1234958.4052
18 | 2706386.8884 | 1234990.3661 | 2706389.3667 | 1234986.8299 | 2706395.9816 | 1234981.0106 | 2706400.703 | 1234973.9675 | 2706412.2536 | 1234961.9956
19 | 2706430.733 | 1234951.2657 | 2706432.6955 | 1234945.6743
20 | 2706398.4196 | 1234897.0259 | 2706405.4085 | 1234908.729
21 | 2706523.652 | 1234864.7978 | 2706533.7682 | 1234885.3469
22 | 2706523.652 | 1234864.7978 | 2706521.1997 | 1234859.7055
23 | 2706539.4806 | 1234896.9506 | 2706533.7682 | 1234885.3469
24 | 2706521.1997 | 1234859.7055 | 2706511.5751 | 1234840.1238
25 | 2706511.0739 | 1234905.926 | 2706499.3473 | 1234917.1569
26 | 2706512.2344 | 1234907.0699 | 2706511.0739 | 1234905.926
27 | 2706512.2344 | 1234907.0699 | 2706522.7159 | 1234904.7449 | 2706539.4806 | 1234896.9506
28 | 2706398.2703 | 1234896.7759 | 2706398.4196 | 1234897.0259
29 | 2706382.718 | 1234870.7332 | 2706398.2703 | 1234896.7759
30 | 2706382.718 | 1234870.7332 | 2706410.7391 | 1234848.2066 | 2706422.2842 | 1234840.3842
31 | 2706427.7831 | 1234836.6585 | 2706422.2842 | 1234840.3842
32 | 2706591.7364 | 1234983.5985 | 2706599.3886 | 1234999.3181
33 | 2706588.0439 | 1234994.8854 | 2706584.3822 | 1234987.1582 | 2706587.2155 | 1234985.7858 | 2706591.7364 | 1234983.5985
34 | 2706566.2787 | 1234951.0281 | 2706576.5616 | 1234971.9952 | 2706584.3822 | 1234987.1582 | 2706587.2155 | 1234985.7858 | 2706591.7364 | 1234983.5985
35 | 2706591.7364 | 1234983.5985 | 2706578.7499 | 1234957.5871
36 | 2706604.8639 | 1235010.5658 | 2706599.3886 | 1234999.3181
37 | 2706588.0439 | 1234994.8854 | 2706571.9959 | 1235006.8043
38 | 2706551.5925 | 1234983.0671 | 2706556.9598 | 1234980.9617 | 2706559.7122 | 1234979.8769 | 2706576.5616 | 1234971.9952 | 2706566.2787 | 1234951.0281
39 | 2706566.2787 | 1234951.0281 | 2706557.0839 | 1234932.2822 | 2706543.1599 | 1234904.3355
40 | 2706537.0441 | 1234855.1082 | 2706535.1368 | 1234859.722 | 2706534.0609 | 1234863.1498 | 2706545.6655 | 1234889.3668 | 2706561.2325 | 1234921.7374 | 2706566.7075 | 1234933.4668 | 2706578.7499 | 1234957.5871
41 | 2706551.5925 | 1234983.0671 | 2706520.9841 | 1235017.7337 | 2706512.0646 | 1235022.8889 | 2706517.2448 | 1235035.4358
42 | 2706523.1246 | 1234978.5977 | 2706522.4902 | 1234981.4663 | 2706525.3942 | 1234985.4325 | 2706527.4989 | 1234985.0032 | 2706530.1813 | 1234986.975 | 2706540.6713 | 1234983.327 | 2706551.5925 | 1234983.0671
43 | 2706539.4806 | 1234896.9506 | 2706543.1599 | 1234904.3355
44 | 2706561.9644 | 1235014.2547 | 2706571.9959 | 1235006.8043
45 | 2706632.7084 | 1235085.5673 | 2706634.8951 | 1235089.8431
46 | 2706632.7084 | 1235085.5673 | 2706636.0682 | 1235083.9597 | 2706639.7944 | 1235082.1807
47 | 2706632.7084 | 1235085.5673 | 2706629.6847 | 1235079.6874
48 | 2706634.8951 | 1235089.8431 | 2706627.8598 | 1235093.4525
49 | 2706639.7944 | 1235082.1807 | 2706633.1936 | 1235069.0608
50 | 2706617.4028 | 1235055.8031 | 2706629.6847 | 1235079.6874
51 | 2706604.8639 | 1235010.5658 | 2706611.9567 | 1235025.3305
52 | 2706604.8639 | 1235010.5658 | 2706619.8119 | 1235002.4536
53 | 2706611.9567 | 1235025.3305 | 2706623.4987 | 1235049.3571
54 | 2706655.1847 | 1234965.7823 | 2706635.0306 | 1234994.1945 | 2706619.8119 | 1235002.4536
55 | 2706633.1936 | 1235069.0608 | 2706628.114 | 1235058.9645 | 2706623.4987 | 1235049.3571
56 | 2706460.2193 | 1235003.6562 | 2706449.2869 | 1235009.7824
57 | 2706462.4676 | 1235002.3955 | 2706460.2193 | 1235003.6562
58 | 2706449.2869 | 1235009.7824 | 2706449.0831 | 1235009.8966
59 | 2706462.4676 | 1235002.3955 | 2706469.8654 | 1235014.8775
60 | 2706462.4676 | 1235002.3955 | 2706458.8965 | 1234996.6415
61 | 2706386.8884 | 1234990.3661 | 2706394.4263 | 1235000.2085
62 | 2706523.1246 | 1234978.5977 | 2706509.0717 | 1234962.3002
63 | 2706681.0069 | 1235010.5656 | 2706681.7321 | 1235009.6213
64 | 2706681.0069 | 1235010.5656 | 2706671.6474 | 1235025.0309 | 2706670.9708 | 1235026.5724
65 | 2706694.0376 | 1234993.5977 | 2706681.7321 | 1235009.6213
66 | 2706665.3674 | 1235042.6806 | 2706667.1876 | 1235035.192 | 2706670.9708 | 1235026.5724
67 | 2706612.7973 | 1235046.847 | 2706617.4028 | 1235055.8031
68 | 2706612.7973 | 1235046.847 | 2706599.8449 | 1235054.8319 | 2706595.7288 | 1235070.0867
69 | 2706595.7288 | 1235070.0867 | 2706595.4169 | 1235071.2428 | 2706592.2774 | 1235070.6972 | 2706589.137 | 1235064.0847
70 | 2706557.0323 | 1235027.5431 | 2706552.297 | 1235021.4313 | 2706561.9644 | 1235014.2547
71 | 2706666.2622 | 1234950.1658 | 2706655.1847 | 1234965.7823
72 | 2706424.6248 | 1235023.6022 | 2706449.0831 | 1235009.8966
73 | 2706481.0882 | 1235033.8132 | 2706469.8654 | 1235014.8775
74 | 2706444.9798 | 1234974.2183 | 2706458.8965 | 1234996.6415
75 | 2706432.0131 | 1234958.4052 | 2706435.5055 | 1234963.7607 | 2706440.7373 | 1234972.1008
76 | 2706418.9009 | 1234972.3588 | 2706425.4769 | 1234964.4817 | 2706432.0131 | 1234958.4052
77 | 2706434.0147 | 1234956.5507 | 2706432.0131 | 1234958.4052
78 | 2706557.0323 | 1235027.5431 | 2706542.1357 | 1235038.9629
79 | 2706540.7518 | 1235056.1193 | 2706535.248 | 1235044.2431 | 2706542.1357 | 1235038.9629
80 | 2706689.4317 | 1234911.2874 | 2706689.3674 | 1234911.3953 | 2706681.1337 | 1234925.2114
81 | 2706678.3959 | 1234929.8054 | 2706681.1337 | 1234925.2114
82 | 2706694.0376 | 1234993.5977 | 2706719.5437 | 1234966.5647
83 | 2706694.0376 | 1234993.5977 | 2706686.7581 | 1234982.2149
84 | 2706434.0147 | 1234956.5507 | 2706444.9798 | 1234974.2183
85 | 2706677.0667 | 1234932.0358 | 2706678.3959 | 1234929.8054
86 | 2706677.0667 | 1234932.0358 | 2706670.6854 | 1234942.7437
87 | 2706666.2622 | 1234950.1658 | 2706670.6854 | 1234942.7437
88 | 2706666.2622 | 1234950.1658 | 2706686.7581 | 1234982.2149
89 | 2706746.6198 | 1234937.8678 | 2706719.5437 | 1234966.5647
90 | 2706589.137 | 1235064.0847 | 2706581.9337 | 1235048.9172

## bus_geodata
| x | y | coords
0 | 2706462.7234 | 1234895.5964
1 | 2706467.1221 | 1234871.7152
2 | 2706467.1095 | 1234907.3282
3 | 2706472.1662 | 1234834.586
4 | 2706486.2448 | 1234890.6689
5 | 2706469.41 | 1234910.7609
6 | 2706498.4107 | 1234879.9944
7 | 2706427.5553 | 1234941.8683
8 | 2706425.95 | 1234947.7996
9 | 2706414.0352 | 1234923.1747
10 | 2706459.0576 | 1234920.0383
11 | 2706512.7828 | 1234867.199
12 | 2706428.6898 | 1234953.3307
13 | 2706412.2536 | 1234961.9956
14 | 2706432.6955 | 1234945.6743
15 | 2706430.733 | 1234951.2657
16 | 2706405.4085 | 1234908.729
17 | 2706523.652 | 1234864.7978
18 | 2706533.7682 | 1234885.3469
19 | 2706521.1997 | 1234859.7055
20 | 2706511.0739 | 1234905.926
21 | 2706499.3473 | 1234917.1569
22 | 2706512.2344 | 1234907.0699
23 | 2706511.5751 | 1234840.1238
24 | 2706398.4196 | 1234897.0259
25 | 2706398.2703 | 1234896.7759
26 | 2706382.718 | 1234870.7332
27 | 2706422.2842 | 1234840.3842
28 | 2706427.7831 | 1234836.6585
29 | 2706591.7364 | 1234983.5985
30 | 2706599.3886 | 1234999.3181
31 | 2706588.0439 | 1234994.8854
32 | 2706566.2787 | 1234951.0281
33 | 2706578.7499 | 1234957.5871
34 | 2706551.5925 | 1234983.0671
35 | 2706543.1599 | 1234904.3355
36 | 2706539.4806 | 1234896.9506
37 | 2706571.9959 | 1235006.8043
38 | 2706632.7084 | 1235085.5673
39 | 2706634.8951 | 1235089.8431
40 | 2706639.7944 | 1235082.1807
41 | 2706629.6847 | 1235079.6874
42 | 2706604.8639 | 1235010.5658
43 | 2706611.9567 | 1235025.3305
44 | 2706619.8119 | 1235002.4536
45 | 2706633.1936 | 1235069.0608
46 | 2706627.8598 | 1235093.4525
47 | 2706460.2193 | 1235003.6562
48 | 2706449.2869 | 1235009.7824
49 | 2706462.4676 | 1235002.3955
50 | 2706386.8884 | 1234990.3661
51 | 2706394.4263 | 1235000.2085
52 | 2706523.1246 | 1234978.5977
53 | 2706509.0717 | 1234962.3002
54 | 2706517.2448 | 1235035.4358
55 | 2706681.0069 | 1235010.5656
56 | 2706681.7321 | 1235009.6213
57 | 2706670.9708 | 1235026.5724
58 | 2706537.0441 | 1234855.1082
59 | 2706612.7973 | 1235046.847
60 | 2706617.4028 | 1235055.8031
61 | 2706595.7288 | 1235070.0867
62 | 2706561.9644 | 1235014.2547
63 | 2706665.3674 | 1235042.6806
64 | 2706623.4987 | 1235049.3571
65 | 2706655.1847 | 1234965.7823
66 | 2706449.0831 | 1235009.8966
67 | 2706469.8654 | 1235014.8775
68 | 2706458.8965 | 1234996.6415
69 | 2706440.7373 | 1234972.1008
70 | 2706432.0131 | 1234958.4052
71 | 2706481.0882 | 1235033.8132
72 | 2706557.0323 | 1235027.5431
73 | 2706542.1357 | 1235038.9629
74 | 2706540.7518 | 1235056.1193
75 | 2706689.4317 | 1234911.2874
76 | 2706681.1337 | 1234925.2114
77 | 2706694.0376 | 1234993.5977
78 | 2706400.7203 | 1234983.5251
79 | 2706418.9009 | 1234972.3588
80 | 2706434.0147 | 1234956.5507
81 | 2706444.9798 | 1234974.2183
82 | 2706424.6248 | 1235023.6022
83 | 2706677.0667 | 1234932.0358
84 | 2706678.3959 | 1234929.8054
85 | 2706670.6854 | 1234942.7437
86 | 2706666.2622 | 1234950.1658
87 | 2706686.7581 | 1234982.2149
88 | 2706719.5437 | 1234966.5647
89 | 2706746.6198 | 1234937.8678
90 | 2706589.137 | 1235064.0847
91 | 2706581.9337 | 1235048.9172
92 | 2706569.8136 | 1234949.7905

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9893 | -0.20565 | 0.0067505 | 0.0016918
1 | 0.98924 | -0.20677 | 0.00096874 | 0.00024279
2 | 0.9894 | -0.20354 | 0 | 0
3 | 0.98918 | -0.20783 | 0.0015899 | 0.00039846
4 | 0.99075 | -0.17742 | 0.0010744 | 0.00026928
5 | 0.98922 | -0.20711 | 0 | 0
6 | 0.99163 | -0.16049 | 0.00094029 | 0.00023566
7 | 0.98654 | -0.25922 | 0 | 0
8 | 0.98665 | -0.25711 | 0 | 0
9 | 0.98613 | -0.26717 | 0.0020254 | 0.00050761
10 | 0.9886 | -0.21915 | 0.0054574 | 0.0013678
11 | 0.99269 | -0.14007 | 0.00058786 | 0.00014733
12 | 0.98678 | -0.25448 | 0 | 0
13 | 0.98656 | -0.25872 | 0.0028738 | 0.00072025
14 | 0.98713 | -0.24767 | 0 | 0
15 | 0.9869 | -0.25224 | 0 | 0
16 | 0.98586 | -0.27235 | 0.0027961 | 0.00070077
17 | 0.99366 | -0.12146 | 0 | 0
18 | 0.99504 | -0.094895 | 0.00086014 | 0.00021557
19 | 0.99332 | -0.12802 | 0 | 0
20 | 0.99571 | -0.082143 | 0 | 0
21 | 0.99564 | -0.083414 | 0.0044537 | 0.0011162
22 | 0.99572 | -0.082015 | 0 | 0
23 | 0.99321 | -0.13006 | 0.0052822 | 0.0013238
24 | 0.98568 | -0.27587 | 0.0010754 | 0.00026953
25 | 0.98568 | -0.27594 | 0.0019105 | 0.00047882
26 | 0.98536 | -0.28214 | 0 | 0
27 | 0.98484 | -0.29236 | 0.0053321 | 0.0013363
28 | 0.9848 | -0.29308 | 0.0060645 | 0.0015199
29 | 0.99406 | -0.11376 | 0 | 0
30 | 0.9929 | -0.13606 | 0.00050015 | 0.00012535
31 | 0.99367 | -0.1212 | 0 | 0
32 | 1 | 0 | -0.31624 | -0.079718
33 | 0.9931 | -0.13228 | 0.0074008 | 0.0018548
34 | 0.99878 | -0.02339 | 0 | 0
35 | 0.99637 | -0.069427 | 0.081242 | 0.020361
36 | 0.99583 | -0.079733 | 0 | 0
37 | 0.99321 | -0.13009 | 0.0054528 | 0.0013666
38 | 0.9895 | -0.20178 | 0 | 0
39 | 0.98949 | -0.20198 | 0 | 0
40 | 0.98969 | -0.19822 | 0 | 0
41 | 0.98936 | -0.2045 | 0.0025814 | 0.00064697
42 | 0.99208 | -0.15195 | 0 | 0
43 | 0.9915 | -0.16319 | 0.0029203 | 0.0007319
44 | 0.99156 | -0.16189 | 0.0038632 | 0.0009682
45 | 0.99003 | -0.19157 | 0.00383 | 0.00095989
46 | 0.98948 | -0.20231 | 0.0023262 | 0.000583
47 | 0.98612 | -0.26744 | 0 | 0
48 | 0.98607 | -0.26843 | 0.0012924 | 0.00032389
49 | 0.98613 | -0.26723 | 0 | 0
50 | 0.9865 | -0.25988 | 0 | 0
51 | 0.98649 | -0.26026 | 0.0016906 | 0.00042371
52 | 0.99815 | -0.035516 | 0 | 0
53 | 0.99777 | -0.042902 | 0.019612 | 0.0049151
54 | 0.99835 | -0.031756 | 0.006832 | 0.0017123
55 | 0.98853 | -0.22076 | 0 | 0
56 | 0.98854 | -0.2206 | 0.0078861 | 0.0019765
57 | 0.98839 | -0.22338 | 0.0049197 | 0.001233
58 | 0.99013 | -0.18978 | 0.028685 | 0.0071891
59 | 0.98871 | -0.2173 | 0 | 0
60 | 0.98886 | -0.21433 | 0.004029 | 0.0010098
61 | 0.98824 | -0.22643 | 0.0044547 | 0.0011165
62 | 0.99299 | -0.13445 | 0.0064161 | 0.001608
63 | 0.98835 | -0.22425 | 0.0028445 | 0.0007129
64 | 0.99062 | -0.18015 | 0.0065547 | 0.0016428
65 | 0.99017 | -0.18885 | 0.0009881 | 0.00024764
66 | 0.98606 | -0.26845 | 0.001831 | 0.00045889
67 | 0.98608 | -0.2681 | 0.0017409 | 0.00043632
68 | 0.98618 | -0.26629 | 0.0019953 | 0.00050006
69 | 0.98665 | -0.25708 | 0.0023209 | 0.00058167
70 | 0.98668 | -0.25641 | 0 | 0
71 | 0.98605 | -0.26873 | 0.0015942 | 0.00039955
72 | 0.99275 | -0.13911 | 0 | 0
73 | 0.99252 | -0.14353 | 0.0065802 | 0.0016492
74 | 0.99238 | -0.14613 | 0.0067508 | 0.0016919
75 | 0.98945 | -0.20276 | 0.0015302 | 0.00038349
76 | 0.98948 | -0.20232 | 0.0028263 | 0.00070833
77 | 0.98883 | -0.21496 | 0 | 0
78 | 0.98672 | -0.25566 | 0.0015964 | 0.00040009
79 | 0.98666 | -0.25687 | 0.0013379 | 0.0003353
80 | 0.98665 | -0.2571 | 0.0018115 | 0.00045401
81 | 0.98641 | -0.26167 | 0.0025139 | 0.00063005
82 | 0.98603 | -0.26911 | 0.0013113 | 0.00032865
83 | 0.98951 | -0.20163 | 0.0013755 | 0.00034473
84 | 0.9895 | -0.20191 | 0.0017257 | 0.00043251
85 | 0.9896 | -0.19997 | 0.0025901 | 0.00064914
86 | 0.98968 | -0.19843 | 0 | 0
87 | 0.98905 | -0.21068 | 0.00028843 | 7.2287e-05
88 | 0.98875 | -0.21638 | 0.0010178 | 0.00025508
89 | 0.98871 | -0.21717 | 0.0011212 | 0.000281
90 | 0.98811 | -0.22895 | 0.0065947 | 0.0016528
91 | 0.98802 | -0.23059 | 0.0054613 | 0.0013687
92 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0025588 | 0.00064059 | -0.0025587 | -0.00064082 | 1.3531e-07 | -2.2619e-07 | 0.0038485 | 0.0038486 | 0.0038486 | 0.9893 | -0.20565 | 0.98924 | -0.20677 | 1.0573
1 | -0.0093094 | -0.0023324 | 0.0093103 | 0.0023329 | 9.3823e-07 | 4.366e-07 | 0.014002 | 0.014002 | 0.014002 | 0.9893 | -0.20565 | 0.9894 | -0.20354 | 3.8467
2 | 0.0015899 | 0.00039803 | -0.0015899 | -0.00039846 | 8.0377e-08 | -4.2966e-07 | 0.0023914 | 0.0023916 | 0.0023916 | 0.98924 | -0.20677 | 0.98918 | -0.20783 | 0.65704
3 | -0.058027 | -0.014593 | 0.0581 | 0.014639 | 7.249e-05 | 4.6067e-05 | 0.087288 | 0.087288 | 0.087288 | 0.9894 | -0.20354 | 0.99075 | -0.17742 | 23.9802
4 | 0.048717 | 0.01226 | -0.048709 | -0.012255 | 8.3161e-06 | 5.2693e-06 | 0.073286 | 0.073286 | 0.073286 | 0.9894 | -0.20354 | 0.98922 | -0.20711 | 20.1335
5 | -0.059174 | -0.014908 | 0.059222 | 0.014939 | 4.797e-05 | 3.0492e-05 | 0.088902 | 0.088901 | 0.088902 | 0.99075 | -0.17742 | 0.99163 | -0.16049 | 24.4235
6 | 0.048709 | 0.012255 | -0.048681 | -0.012237 | 2.7998e-05 | 1.774e-05 | 0.073286 | 0.073286 | 0.073286 | 0.98922 | -0.20711 | 0.9886 | -0.21915 | 20.1335
7 | -0.060163 | -0.015174 | 0.060221 | 0.015212 | 5.8856e-05 | 3.7419e-05 | 0.090312 | 0.090312 | 0.090312 | 0.99163 | -0.16049 | 0.99269 | -0.14007 | 24.8111
8 | -0.019227 | -0.004826 | 0.019229 | 0.0048271 | 1.9384e-06 | 1.1621e-06 | 0.029003 | 0.029003 | 0.029003 | 0.98654 | -0.25922 | 0.98665 | -0.25711 | 7.9679
9 | 0.019227 | 0.004826 | -0.01922 | -0.0048216 | 7.2825e-06 | 4.3661e-06 | 0.029003 | 0.029003 | 0.029003 | 0.98654 | -0.25922 | 0.98613 | -0.26717 | 7.9679
10 | -0.023794 | -0.0059705 | 0.023797 | 0.0059723 | 2.9794e-06 | 1.828e-06 | 0.035887 | 0.035887 | 0.035887 | 0.98665 | -0.25711 | 0.98678 | -0.25448 | 9.8592
11 | 0.0045649 | 0.0011434 | -0.0045645 | -0.0011434 | 3.5059e-07 | -2.7528e-08 | 0.0068843 | 0.0068844 | 0.0068844 | 0.98665 | -0.25711 | 0.98656 | -0.25872 | 1.8913
12 | 0.017194 | 0.004314 | -0.01719 | -0.0043115 | 4.2479e-06 | 2.5041e-06 | 0.025947 | 0.025947 | 0.025947 | 0.98613 | -0.26717 | 0.98586 | -0.27235 | 7.1283
13 | 0.043223 | 0.010869 | -0.043165 | -0.010832 | 5.8795e-05 | 3.7155e-05 | 0.065072 | 0.065072 | 0.065072 | 0.9886 | -0.21915 | 0.98713 | -0.24767 | 17.8769
14 | -0.060809 | -0.015359 | 0.060844 | 0.015381 | 3.5144e-05 | 2.2347e-05 | 0.091193 | 0.091193 | 0.091193 | 0.99269 | -0.14007 | 0.99332 | -0.12802 | 25.0532
15 | -0.043151 | -0.010823 | 0.043155 | 0.010826 | 4.6064e-06 | 2.9111e-06 | 0.065072 | 0.065072 | 0.065072 | 0.98678 | -0.25448 | 0.9869 | -0.25224 | 17.8769
16 | 0.0015965 | 0.00039962 | -0.0015964 | -0.00040009 | 8.9445e-08 | -4.6851e-07 | 0.0024072 | 0.0024074 | 0.0024074 | 0.98678 | -0.25448 | 0.98672 | -0.25566 | 0.66138
17 | 0.017757 | 0.0044511 | -0.017755 | -0.0044502 | 1.6297e-06 | 9.6558e-07 | 0.026777 | 0.026777 | 0.026777 | 0.98678 | -0.25448 | 0.98668 | -0.25641 | 7.3564
18 | 0.0016907 | 0.00042314 | -0.0016906 | -0.00042357 | 9.3251e-08 | -4.2862e-07 | 0.0025499 | 0.0025501 | 0.0025501 | 0.98656 | -0.25872 | 0.9865 | -0.25988 | 0.70056
19 | 0.043165 | 0.010832 | -0.043155 | -0.010826 | 9.4082e-06 | 5.9455e-06 | 0.065072 | 0.065072 | 0.065072 | 0.98713 | -0.24767 | 0.9869 | -0.25224 | 17.8769
20 | 0.014394 | 0.0036107 | -0.014392 | -0.0036094 | 2.413e-06 | 1.3706e-06 | 0.021727 | 0.021727 | 0.021727 | 0.98586 | -0.27235 | 0.98568 | -0.27587 | 5.9689
21 | -0.066148 | -0.016718 | 0.066232 | 0.016772 | 8.4364e-05 | 5.3696e-05 | 0.099107 | 0.099107 | 0.099107 | 0.99366 | -0.12146 | 0.99504 | -0.094895 | 27.2272
22 | 0.066148 | 0.016718 | -0.066127 | -0.016705 | 2.0807e-05 | 1.3243e-05 | 0.099107 | 0.099107 | 0.099107 | 0.99366 | -0.12146 | 0.99332 | -0.12802 | 27.2272
23 | -0.067092 | -0.016988 | 0.067141 | 0.017019 | 4.8883e-05 | 3.1117e-05 | 0.10039 | 0.10039 | 0.10039 | 0.99504 | -0.094895 | 0.99583 | -0.079733 | 27.5805
24 | 0.0052827 | 0.0013239 | -0.0052822 | -0.0013238 | 5.1241e-07 | 4.5536e-08 | 0.0079136 | 0.0079137 | 0.0079137 | 0.99332 | -0.12802 | 0.99321 | -0.13006 | 2.1741
25 | 0.004454 | 0.0011162 | -0.0044537 | -0.0011162 | 2.6976e-07 | -3.8533e-08 | 0.0066561 | 0.0066562 | 0.0066562 | 0.99571 | -0.082143 | 0.99564 | -0.083414 | 1.8286
26 | -0.004454 | -0.0011162 | 0.004454 | 0.0011162 | 2.7031e-08 | -3.8628e-09 | 0.0066561 | 0.0066561 | 0.0066561 | 0.99571 | -0.082143 | 0.99572 | -0.082015 | 1.8286
27 | -0.004454 | -0.0011162 | 0.0044545 | 0.0011161 | 4.843e-07 | -6.9265e-08 | 0.0066561 | 0.0066559 | 0.0066561 | 0.99572 | -0.082015 | 0.99583 | -0.079733 | 1.8286
28 | 0.013316 | 0.0033398 | -0.013316 | -0.0033398 | 4.4132e-08 | 2.4533e-08 | 0.020103 | 0.020103 | 0.020103 | 0.98568 | -0.27587 | 0.98568 | -0.27594 | 5.5229
29 | 0.011406 | 0.002861 | -0.011402 | -0.0028592 | 3.3727e-06 | 1.772e-06 | 0.017219 | 0.017219 | 0.017219 | 0.98568 | -0.27594 | 0.98536 | -0.28214 | 4.7306
30 | 0.011402 | 0.0028592 | -0.011397 | -0.0028563 | 5.5483e-06 | 2.9157e-06 | 0.017219 | 0.01722 | 0.01722 | 0.98536 | -0.28214 | 0.98484 | -0.29236 | 4.7307
31 | 0.0060647 | 0.0015199 | -0.0060645 | -0.0015199 | 2.0914e-07 | 4.9336e-08 | 0.0091633 | 0.0091633 | 0.0091633 | 0.98484 | -0.29236 | 0.9848 | -0.29308 | 2.5174
32 | 0.072551 | 0.018301 | -0.072474 | -0.018252 | 7.7387e-05 | 4.9301e-05 | 0.10864 | 0.10864 | 0.10864 | 0.99406 | -0.11376 | 0.9929 | -0.13606 | 29.8474
33 | 0.02523 | 0.0063337 | -0.025221 | -0.0063282 | 8.9458e-06 | 5.5087e-06 | 0.037771 | 0.037771 | 0.037771 | 0.99406 | -0.11376 | 0.99367 | -0.1212 | 10.3767
34 | -0.13398 | -0.033748 | 0.13471 | 0.034217 | 0.00073324 | 0.00046864 | 0.20061 | 0.20061 | 0.20061 | 0.99406 | -0.11376 | 1 | 0 | 55.1134
35 | 0.036196 | 0.009113 | -0.036164 | -0.0090929 | 3.2024e-05 | 2.0119e-05 | 0.054197 | 0.054198 | 0.054198 | 0.99406 | -0.11376 | 0.9931 | -0.13228 | 14.8894
36 | 0.071974 | 0.018127 | -0.071919 | -0.018092 | 5.461e-05 | 3.4789e-05 | 0.10789 | 0.10789 | 0.10789 | 0.9929 | -0.13606 | 0.99208 | -0.15195 | 29.6415
37 | 0.025221 | 0.0063282 | -0.025211 | -0.0063216 | 1.0695e-05 | 6.5857e-06 | 0.037771 | 0.037771 | 0.037771 | 0.99367 | -0.1212 | 0.99321 | -0.13009 | 10.3767
38 | 0.026494 | 0.0066574 | -0.026465 | -0.0066391 | 2.9546e-05 | 1.8246e-05 | 0.03943 | 0.03943 | 0.03943 | 1 | 0 | 0.99878 | -0.02339 | 10.8324
39 | 0.15338 | 0.038844 | -0.15287 | -0.038519 | 0.00050953 | 0.00032474 | 0.22838 | 0.22838 | 0.22838 | 1 | 0 | 0.99637 | -0.069427 | 31.3707
40 | 0.028764 | 0.0072381 | -0.028685 | -0.0071891 | 7.8803e-05 | 4.8975e-05 | 0.043108 | 0.043109 | 0.043109 | 0.9931 | -0.13228 | 0.99013 | -0.18978 | 11.8431
41 | 0.0068347 | 0.0017131 | -0.006832 | -0.0017123 | 2.7234e-06 | 8.2674e-07 | 0.010183 | 0.010183 | 0.010183 | 0.99878 | -0.02339 | 0.99835 | -0.031756 | 2.7975
42 | 0.01963 | 0.0049261 | -0.019618 | -0.0049193 | 1.1343e-05 | 6.7971e-06 | 0.029247 | 0.029248 | 0.029248 | 0.99878 | -0.02339 | 0.99815 | -0.035516 | 8.035
43 | 0.071631 | 0.018158 | -0.071596 | -0.018135 | 3.5456e-05 | 2.2584e-05 | 0.10705 | 0.10705 | 0.10705 | 0.99637 | -0.069427 | 0.99583 | -0.079733 | 29.4091
44 | 0.019758 | 0.004955 | -0.019754 | -0.0049525 | 4.1061e-06 | 2.4662e-06 | 0.029602 | 0.029602 | 0.029602 | 0.99321 | -0.13009 | 0.99299 | -0.13445 | 8.1324
45 | 0.0023263 | 0.00058288 | -0.0023263 | -0.00058293 | 2.2028e-08 | -4.7559e-08 | 0.0034982 | 0.0034982 | 0.0034982 | 0.9895 | -0.20178 | 0.98949 | -0.20198 | 0.96105
46 | -0.025471 | -0.0063917 | 0.025476 | 0.0063943 | 4.3217e-06 | 2.665e-06 | 0.038307 | 0.038307 | 0.038307 | 0.9895 | -0.20178 | 0.98969 | -0.19822 | 10.5239
47 | 0.023145 | 0.0058088 | -0.023142 | -0.0058069 | 3.0042e-06 | 1.8377e-06 | 0.034809 | 0.034809 | 0.034809 | 0.9895 | -0.20178 | 0.98936 | -0.2045 | 9.5628
48 | 0.0023263 | 0.00058293 | -0.0023262 | -0.000583 | 3.6287e-08 | -7.8342e-08 | 0.0034982 | 0.0034983 | 0.0034983 | 0.98949 | -0.20198 | 0.98948 | -0.20231 | 0.96106
49 | -0.025476 | -0.0063943 | 0.025484 | 0.0063993 | 8.0819e-06 | 4.9836e-06 | 0.038307 | 0.038307 | 0.038307 | 0.98969 | -0.19822 | 0.99003 | -0.19157 | 10.5238
50 | 0.020561 | 0.00516 | -0.020551 | -0.0051541 | 9.6326e-06 | 5.8201e-06 | 0.030926 | 0.030926 | 0.030926 | 0.98936 | -0.2045 | 0.98886 | -0.21433 | 8.4962
51 | 0.038855 | 0.0097752 | -0.038834 | -0.009762 | 2.0872e-05 | 1.3146e-05 | 0.058292 | 0.058292 | 0.058292 | 0.99208 | -0.15195 | 0.9915 | -0.16319 | 16.0142
52 | 0.033064 | 0.0083166 | -0.033048 | -0.0083067 | 1.5693e-05 | 9.8237e-06 | 0.049603 | 0.049604 | 0.049604 | 0.99208 | -0.15195 | 0.99156 | -0.16189 | 13.6273
53 | 0.035914 | 0.0090301 | -0.035885 | -0.0090119 | 2.9049e-05 | 1.8248e-05 | 0.053909 | 0.053909 | 0.053909 | 0.9915 | -0.16319 | 0.99062 | -0.18015 | 14.8101
54 | 0.029185 | 0.0073385 | -0.029148 | -0.0073152 | 3.7528e-05 | 2.3346e-05 | 0.043806 | 0.043806 | 0.043806 | 0.99156 | -0.16189 | 0.99017 | -0.18885 | 12.0347
55 | -0.029314 | -0.0073592 | 0.02933 | 0.0073691 | 1.5989e-05 | 9.9505e-06 | 0.044063 | 0.044063 | 0.044063 | 0.99003 | -0.19157 | 0.99062 | -0.18015 | 12.1053
56 | 0.0044349 | 0.0011111 | -0.0044347 | -0.0011111 | 2.1046e-07 | -2.5176e-08 | 0.006692 | 0.0066921 | 0.0066921 | 0.98612 | -0.26744 | 0.98607 | -0.26843 | 1.8385
57 | -0.0044349 | -0.0011111 | 0.004435 | 0.0011111 | 4.3193e-08 | -5.1693e-09 | 0.006692 | 0.006692 | 0.006692 | 0.98612 | -0.26744 | 0.98613 | -0.26723 | 1.8385
58 | 0.0031424 | 0.00078721 | -0.0031424 | -0.00078721 | 1.9704e-09 | -1.7193e-09 | 0.0047418 | 0.0047418 | 0.0047418 | 0.98607 | -0.26843 | 0.98606 | -0.26845 | 1.3027
59 | 0.0033354 | 0.00083552 | -0.0033352 | -0.00083562 | 1.3782e-07 | -9.69e-08 | 0.0050327 | 0.0050328 | 0.0050328 | 0.98613 | -0.26723 | 0.98608 | -0.2681 | 1.3826
60 | -0.0077703 | -0.0019466 | 0.0077707 | 0.0019467 | 3.4911e-07 | 1.3703e-07 | 0.011725 | 0.011725 | 0.011725 | 0.98613 | -0.26723 | 0.98618 | -0.26629 | 3.2211
61 | 0.0016906 | 0.00042357 | -0.0016906 | -0.00042371 | 3.0232e-08 | -1.3893e-07 | 0.0025501 | 0.0025501 | 0.0025501 | 0.9865 | -0.25988 | 0.98649 | -0.26026 | 0.70058
62 | 0.019618 | 0.0049193 | -0.019612 | -0.0049151 | 6.9031e-06 | 4.1368e-06 | 0.029248 | 0.029248 | 0.029248 | 0.99815 | -0.035516 | 0.99777 | -0.042902 | 8.0351
63 | -0.0077653 | -0.0019461 | 0.0077653 | 0.0019461 | 6.1007e-08 | 2.378e-08 | 0.011689 | 0.011689 | 0.011689 | 0.98853 | -0.22076 | 0.98854 | -0.2206 | 3.2112
64 | 0.0077653 | 0.0019461 | -0.0077643 | -0.0019457 | 9.6902e-07 | 3.7775e-07 | 0.011689 | 0.011689 | 0.011689 | 0.98853 | -0.22076 | 0.98839 | -0.22338 | 3.2113
65 | -0.015651 | -0.0039226 | 0.015656 | 0.003925 | 4.2053e-06 | 2.4323e-06 | 0.02356 | 0.02356 | 0.02356 | 0.98854 | -0.2206 | 0.98883 | -0.21496 | 6.4724
66 | 0.0028446 | 0.00071275 | -0.0028445 | -0.0007129 | 1.1774e-07 | -1.4405e-07 | 0.0042825 | 0.0042826 | 0.0042826 | 0.98839 | -0.22338 | 0.98835 | -0.22425 | 1.1765
67 | -0.01652 | -0.004143 | 0.016522 | 0.0041444 | 2.3347e-06 | 1.365e-06 | 0.024864 | 0.024863 | 0.024864 | 0.98871 | -0.2173 | 0.98886 | -0.21433 | 6.8306
68 | 0.01652 | 0.004143 | -0.016513 | -0.0041388 | 7.1903e-06 | 4.2042e-06 | 0.024864 | 0.024864 | 0.024864 | 0.98871 | -0.2173 | 0.98824 | -0.22643 | 6.8307
69 | 0.012058 | 0.0030223 | -0.012056 | -0.0030216 | 1.4468e-06 | 7.7603e-07 | 0.018156 | 0.018156 | 0.018156 | 0.98824 | -0.22643 | 0.98811 | -0.22895 | 4.9879
70 | 0.013338 | 0.0033445 | -0.013335 | -0.0033429 | 2.9576e-06 | 1.6375e-06 | 0.019987 | 0.019988 | 0.019988 | 0.99299 | -0.13445 | 0.99275 | -0.13911 | 5.4911
71 | 0.02816 | 0.0070675 | -0.028147 | -0.0070596 | 1.286e-05 | 7.9843e-06 | 0.042321 | 0.042322 | 0.042322 | 0.99017 | -0.18885 | 0.98968 | -0.19843 | 11.6268
72 | 0.0013114 | 0.00032832 | -0.0013113 | -0.00032865 | 4.1171e-08 | -3.3128e-07 | 0.0019788 | 0.0019789 | 0.0019789 | 0.98606 | -0.26845 | 0.98603 | -0.26911 | 0.54366
73 | 0.0015943 | 0.0003993 | -0.0015942 | -0.00039955 | 4.7773e-08 | -2.5021e-07 | 0.0024057 | 0.0024058 | 0.0024058 | 0.98608 | -0.2681 | 0.98605 | -0.26873 | 0.66093
74 | -0.0097659 | -0.0024468 | 0.0097681 | 0.0024478 | 2.1488e-06 | 1.0384e-06 | 0.014735 | 0.014735 | 0.014735 | 0.98618 | -0.26629 | 0.98641 | -0.26167 | 4.0482
75 | -0.0023209 | -0.00058167 | 0.0023209 | 0.00058151 | 7.4606e-08 | -1.5965e-07 | 0.0035002 | 0.0035002 | 0.0035002 | 0.98665 | -0.25708 | 0.98668 | -0.25641 | 0.9616
76 | 0.0013379 | 0.00033507 | -0.0013379 | -0.0003353 | 2.925e-08 | -2.26e-07 | 0.0020176 | 0.0020177 | 0.0020177 | 0.98668 | -0.25641 | 0.98666 | -0.25687 | 0.55431
77 | 0.014097 | 0.0035336 | -0.014096 | -0.0035333 | 4.6185e-07 | 2.6078e-07 | 0.021259 | 0.021259 | 0.021259 | 0.98668 | -0.25641 | 0.98665 | -0.2571 | 5.8405
78 | 0.013335 | 0.0033429 | -0.013332 | -0.0033413 | 2.812e-06 | 1.5571e-06 | 0.019988 | 0.019988 | 0.019988 | 0.99275 | -0.13911 | 0.99252 | -0.14353 | 5.4911
79 | 0.0067516 | 0.0016922 | -0.0067508 | -0.0016919 | 8.3641e-07 | 2.5401e-07 | 0.010122 | 0.010122 | 0.010122 | 0.99252 | -0.14353 | 0.99238 | -0.14613 | 2.7809
80 | -0.0015302 | -0.00038349 | 0.0015302 | 0.00038331 | 3.2186e-08 | -1.876e-07 | 0.0023012 | 0.0023011 | 0.0023012 | 0.98945 | -0.20276 | 0.98948 | -0.20232 | 0.63219
81 | -0.0043564 | -0.0010916 | 0.0043565 | 0.0010916 | 8.6075e-08 | -1.3606e-08 | 0.0065513 | 0.0065513 | 0.0065513 | 0.98948 | -0.20232 | 0.9895 | -0.20191 | 1.7998
82 | 0.0021392 | 0.00053522 | -0.002139 | -0.0005356 | 1.4441e-07 | -3.8431e-07 | 0.0032188 | 0.003219 | 0.003219 | 0.98883 | -0.21496 | 0.98875 | -0.21638 | 0.88433
83 | -0.017795 | -0.0044602 | 0.017798 | 0.0044624 | 3.6333e-06 | 2.1519e-06 | 0.026778 | 0.026778 | 0.026778 | 0.98883 | -0.21496 | 0.98905 | -0.21068 | 7.3567
84 | 0.012285 | 0.0030793 | -0.012282 | -0.0030779 | 2.6767e-06 | 1.4476e-06 | 0.018527 | 0.018527 | 0.018527 | 0.98665 | -0.2571 | 0.98641 | -0.26167 | 5.09
85 | 0.0060823 | 0.0015241 | -0.0060823 | -0.0015241 | 8.1454e-08 | 1.8779e-08 | 0.0091465 | 0.0091465 | 0.0091465 | 0.98951 | -0.20163 | 0.9895 | -0.20191 | 2.5128
86 | -0.0074578 | -0.0018689 | 0.0074584 | 0.0018691 | 5.8792e-07 | 2.1613e-07 | 0.011215 | 0.011215 | 0.011215 | 0.98951 | -0.20163 | 0.9896 | -0.19997 | 3.081
87 | -0.010049 | -0.0025182 | 0.010049 | 0.0025186 | 7.3969e-07 | 3.6239e-07 | 0.01511 | 0.015109 | 0.01511 | 0.9896 | -0.19997 | 0.98968 | -0.19843 | 4.151
88 | 0.018097 | 0.004541 | -0.018087 | -0.0045347 | 1.0564e-05 | 6.2724e-06 | 0.027212 | 0.027212 | 0.027212 | 0.98968 | -0.19843 | 0.98905 | -0.21068 | 7.4759
89 | 0.0011213 | 0.00028052 | -0.0011212 | -0.000281 | 4.2124e-08 | -4.7905e-07 | 0.0016873 | 0.0016874 | 0.0016874 | 0.98875 | -0.21638 | 0.98871 | -0.21717 | 0.46358
90 | 0.0054617 | 0.0013688 | -0.0054613 | -0.0013687 | 4.2598e-07 | 5.7564e-08 | 0.008225 | 0.008225 | 0.008225 | 0.98811 | -0.22895 | 0.98802 | -0.23059 | 2.2596

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.31624 | 0.079718

## res_load
| p_mw | q_mvar
0 | 0.0067505 | 0.0016918
1 | 0.00096874 | 0.00024279
2 | 0.0015899 | 0.00039846
3 | 0.0010744 | 0.00026928
4 | 0.00094029 | 0.00023566
5 | 0.0020254 | 0.00050761
6 | 0.0054574 | 0.0013678
7 | 0.00058786 | 0.00014733
8 | 0.0028738 | 0.00072025
9 | 0.0027961 | 0.00070077
10 | 0.00086014 | 0.00021557
11 | 0.0044537 | 0.0011162
12 | 0.0052822 | 0.0013238
13 | 0.0010754 | 0.00026953
14 | 0.0019105 | 0.00047882
15 | 0.0053321 | 0.0013363
16 | 0.0060645 | 0.0015199
17 | 0.00050015 | 0.00012535
18 | 0.0074008 | 0.0018548
19 | 0.081242 | 0.020361
20 | 0.0054528 | 0.0013666
21 | 0.0025814 | 0.00064697
22 | 0.0029203 | 0.0007319
23 | 0.0038632 | 0.0009682
24 | 0.00383 | 0.00095989
25 | 0.0023262 | 0.000583
26 | 0.0012924 | 0.00032389
27 | 0.0016906 | 0.00042371
28 | 0.019612 | 0.0049151
29 | 0.006832 | 0.0017123
30 | 0.0078861 | 0.0019765
31 | 0.0049197 | 0.001233
32 | 0.028685 | 0.0071891
33 | 0.004029 | 0.0010098
34 | 0.0044547 | 0.0011165
35 | 0.0064161 | 0.001608
36 | 0.0028445 | 0.0007129
37 | 0.0065547 | 0.0016428
38 | 0.0009881 | 0.00024764
39 | 0.001831 | 0.00045889
40 | 0.0017409 | 0.00043632
41 | 0.0019953 | 0.00050006
42 | 0.0023209 | 0.00058167
43 | 0.0015942 | 0.00039955
44 | 0.0065802 | 0.0016492
45 | 0.0067508 | 0.0016919
46 | 0.0015302 | 0.00038349
47 | 0.0028263 | 0.00070833
48 | 0.0015964 | 0.00040009
49 | 0.0013379 | 0.0003353
50 | 0.0018115 | 0.00045401
51 | 0.0025139 | 0.00063005
52 | 0.0013113 | 0.00032865
53 | 0.0013755 | 0.00034473
54 | 0.0017257 | 0.00043251
55 | 0.0025901 | 0.00064914
56 | 0.00028843 | 7.2287e-05
57 | 0.0010178 | 0.00025508
58 | 0.0011212 | 0.000281
59 | 0.0065947 | 0.0016528
60 | 0.0054613 | 0.0013687

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1