## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_118-15_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_118-15_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_118-15_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_118-15_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_118-15_0_2_node_6 | 0.4 | n |  | TRUE
5 | bus_LV_118-15_0_2_node_24 | 0.4 | n |  | TRUE
6 | bus_LV_118-15_0_2_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_118-15_0_2_node_4 | 0.4 | n |  | TRUE
8 | bus_LV_118-15_0_2_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_118-15_0_2_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_118-15_0_2_node_25 | 0.4 | n |  | TRUE
11 | bus_LV_118-15_0_2_node_12 | 0.4 | n |  | TRUE
12 | bus_LV_118-15_0_2_node_23 | 0.4 | n |  | TRUE
13 | bus_LV_118-15_0_2_node_19 | 0.4 | n |  | TRUE
14 | bus_LV_118-15_0_2_node_14 | 0.4 | n |  | TRUE
15 | bus_LV_118-15_0_2_node_15 | 0.4 | n |  | TRUE
16 | bus_LV_118-15_0_2_node_22 | 0.4 | n |  | TRUE
17 | bus_LV_118-15_0_2_node_29 | 0.4 | n |  | TRUE
18 | bus_LV_118-15_0_2_node_28 | 0.4 | n |  | TRUE
19 | bus_LV_118-15_0_2_node_9 | 0.4 | n |  | TRUE
20 | bus_LV_118-15_0_2_node_10 | 0.4 | n |  | TRUE
21 | bus_LV_118-15_0_2_node_11 | 0.4 | n |  | TRUE
22 | bus_LV_118-15_0_2_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_118-15_0_2_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_118-15_0_2_node_26 | 0.4 | n |  | TRUE
25 | bus_LV_118-15_0_2_node_30 | 0.4 | n |  | TRUE
26 | bus_LV_118-15_0_2_node_21 | 0.4 | n |  | TRUE
27 | bus_LV_118-15_0_2_node_17 | 0.4 | n |  | TRUE
28 | bus_LV_118-15_0_2_node_27 | 0.4 | n |  | TRUE
29 | bus_LV_118-15_0_2_node_37 | 0.4 | n |  | TRUE
30 | bus_LV_118-15_0_2_node_36 | 0.4 | n |  | TRUE
31 | bus_LV_118-15_0_2_node_31 | 0.4 | n |  | TRUE
32 | bus_LV_118-15_0_2_node_18 | 0.4 | n |  | TRUE
33 | bus_LV_118-15_0_2_node_20 | 0.4 | n |  | TRUE
34 | bus_LV_118-15_0_2_node_32 | 0.4 | n |  | TRUE
35 | bus_LV_118-15_0_2_node_33 | 0.4 | n |  | TRUE
36 | bus_LV_118-15_0_2_node_34 | 0.4 | n |  | TRUE
37 | bus_LV_118-15_0_2_node_35 | 0.4 | n |  | TRUE
38 | bus_MV_9_0_node_68 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_118-15_0_2_load_0 | 0 | 0.0082793 | 0.002075 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_118-15_0_2_load_2 | 2 | 0.0014388 | 0.00036059 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_118-15_0_2_load_3 | 3 | 0.0005396 | 0.00013524 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_118-15_0_2_load_4 | 7 | 0.00084153 | 0.00021091 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_118-15_0_2_load_8 | 8 | 0.00066264 | 0.00016607 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_118-15_0_2_load_7 | 9 | 0.00056569 | 0.00014178 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_118-15_0_2_load_25 | 10 | 0.00033571 | 8.4138e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_118-15_0_2_load_23 | 12 | 0.046679 | 0.011699 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_118-15_0_2_load_22 | 16 | 0.013783 | 0.0034542 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_118-15_0_2_load_28 | 18 | 0.021226 | 0.0053198 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_118-15_0_2_load_9 | 19 | 0.004608 | 0.0011549 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_118-15_0_2_load_10 | 20 | 0.0050731 | 0.0012714 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_118-15_0_2_load_26 | 24 | 0.0047274 | 0.0011848 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_118-15_0_2_load_30 | 25 | 0.003112 | 0.00077995 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_118-15_0_2_load_21 | 26 | 0.050877 | 0.012751 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_118-15_0_2_load_17 | 27 | 0.041247 | 0.010338 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_118-15_0_2_load_37 | 29 | 0.0061582 | 0.0015434 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_118-15_0_2_load_36 | 30 | 0.017591 | 0.0044086 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_118-15_0_2_load_31 | 31 | 0.0028256 | 0.00070816 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_118-15_0_2_load_20 | 33 | 0.0027442 | 0.00068777 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_118-15_0_2_load_32 | 34 | 0.0022517 | 0.00056432 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_118-15_0_2_load_33 | 35 | 0.0022517 | 0.00056432 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_118-15_0_2_load_34 | 36 | 0.0022533 | 0.00056473 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_118-15_0_2_load_35 | 37 | 0.0017533 | 0.00043943 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 12 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_118-15_0_2_line_0 |  | 0 | 1 | 0.028063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_118-15_0_2_line_1 |  | 1 | 2 | 0.028234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_118-15_0_2_line_2 |  | 1 | 3 | 0.0019295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_118-15_0_2_line_3 |  | 3 | 4 | 0.019534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_118-15_0_2_line_4 |  | 4 | 5 | 0.11084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_118-15_0_2_line_5 |  | 4 | 6 | 0.027062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_118-15_0_2_line_6 |  | 5 | 18 | 0.01907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_118-15_0_2_line_7 |  | 6 | 8 | 0.017108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_118-15_0_2_line_8 |  | 6 | 7 | 0.024461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_118-15_0_2_line_9 |  | 8 | 10 | 0.018606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_118-15_0_2_line_10 |  | 9 | 10 | 0.0055076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_118-15_0_2_line_11 |  | 11 | 12 | 0.029885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_118-15_0_2_line_12 |  | 11 | 13 | 0.032277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_118-15_0_2_line_13 |  | 12 | 14 | 0.05284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_118-15_0_2_line_14 |  | 13 | 26 | 0.013075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_118-15_0_2_line_15 |  | 13 | 27 | 0.020665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_118-15_0_2_line_16 |  | 14 | 15 | 0.1539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_118-15_0_2_line_17 |  | 14 | 16 | 0.02916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_118-15_0_2_line_18 |  | 15 | 17 | 0.01685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_118-15_0_2_line_19 |  | 15 | 18 | 0.043192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_118-15_0_2_line_20 |  | 17 | 29 | 0.010904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_118-15_0_2_line_21 |  | 17 | 30 | 0.00364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_118-15_0_2_line_22 |  | 19 | 20 | 0.020565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_118-15_0_2_line_23 |  | 19 | 21 | 0.046139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_118-15_0_2_line_24 |  | 21 | 22 | 0.014836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_118-15_0_2_line_25 |  | 21 | 23 | 0.18077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_118-15_0_2_line_26 |  | 22 | 24 | 0.017055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_118-15_0_2_line_27 |  | 23 | 25 | 0.036103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_118-15_0_2_line_28 |  | 24 | 28 | 0.024618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_118-15_0_2_line_29 |  | 25 | 31 | 0.001298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_118-15_0_2_line_30 |  | 27 | 32 | 0.093838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_118-15_0_2_line_31 |  | 28 | 33 | 0.042745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_118-15_0_2_line_32 |  | 31 | 34 | 0.026222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_118-15_0_2_line_33 |  | 32 | 33 | 0.06616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_118-15_0_2_line_34 |  | 34 | 35 | 0.0055389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_118-15_0_2_line_35 |  | 35 | 36 | 0.0055405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_118-15_0_2_line_36 |  | 36 | 37 | 0.0016075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_118-15_0_2_trafo_23 | 0.63 MVA 20/0.4 kV | 38 | 12 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13
0 | 2706035.1856 | 1235373.8508 | 2706024.9254 | 1235379.5277 | 2706032.9615 | 1235393.7511
1 | 2706035.1856 | 1235373.8508 | 2706048.7125 | 1235398.6341
2 | 2706035.1856 | 1235373.8508 | 2706036.6695 | 1235372.6174
3 | 2706042.3976 | 1235356.166 | 2706044.4962 | 1235360.3066 | 2706042.8486 | 1235364.8251 | 2706039.7038 | 1235370.0953 | 2706036.6695 | 1235372.6174
4 | 2706008.778 | 1235388.9023 | 2706007.2202 | 1235383.3035 | 2706004.9141 | 1235380.1822 | 2706000.7451 | 1235378.3731 | 2705990.5672 | 1235380.7156 | 2705987.5375 | 1235374.8793 | 2706004.2319 | 1235365.8146 | 2706009.216 | 1235363.1015 | 2706005.823 | 1235357.2587 | 2706009.462 | 1235355.2554 | 2706025.6235 | 1235346.3703 | 2706033.3832 | 1235342.1055 | 2706042.3976 | 1235356.166
5 | 2706062.3763 | 1235337.853 | 2706042.3976 | 1235356.166
6 | 2706008.778 | 1235388.9023 | 2706002.8014 | 1235394.2108 | 2705991.8317 | 1235395.7468
7 | 2706062.3763 | 1235337.853 | 2706067.1828 | 1235348.4692 | 2706072.247 | 1235350.4945
8 | 2706062.3763 | 1235337.853 | 2706067.1828 | 1235348.4692 | 2706073.5566 | 1235351.0182 | 2706079.4713 | 1235350.4456
9 | 2706082.8228 | 1235340.0935 | 2706082.388 | 1235346.0832 | 2706079.4713 | 1235350.4456 | 2706073.5566 | 1235351.0182 | 2706072.247 | 1235350.4945
10 | 2706083.2215 | 1235334.6004 | 2706083.2215 | 1235334.6004 | 2706082.8228 | 1235340.0935
11 | 2705740.9288 | 1235487.3382 | 2705756.5945 | 1235484.993 | 2705770.2512 | 1235481.7161
12 | 2705741.0014 | 1235518.5412 | 2705739.2367 | 1235500.3181 | 2705741.6751 | 1235497.715 | 2705740.9288 | 1235487.3382
13 | 2705818.8053 | 1235461.0601 | 2705775.0147 | 1235480.5731 | 2705770.2512 | 1235481.7161
14 | 2705741.0014 | 1235518.5412 | 2705754.0452 | 1235517.1945
15 | 2705741.0014 | 1235518.5412 | 2705720.4964 | 1235521.1056
16 | 2705818.8053 | 1235461.0601 | 2705872.9106 | 1235428.5657 | 2705910.4032 | 1235409.0857 | 2705943.5695 | 1235391.9638 | 2705949.0574 | 1235401.7358
17 | 2705818.8053 | 1235461.0601 | 2705827.6924 | 1235467.8458 | 2705838.0512 | 1235466.8073 | 2705844.3022 | 1235462.5409
18 | 2705947.4787 | 1235418.5094 | 2705949.0574 | 1235401.7358
19 | 2705949.0574 | 1235401.7358 | 2705991.8317 | 1235395.7468
20 | 2705947.4787 | 1235418.5094 | 2705958.3859 | 1235417.7144
21 | 2705945.1129 | 1235421.2804 | 2705947.4787 | 1235418.5094
22 | 2705598.3989 | 1235464.0071 | 2705617.4896 | 1235471.6546
23 | 2705553.7848 | 1235452.7065 | 2705564.2715 | 1235454.2607 | 2705591.8653 | 1235461.3898 | 2705598.3989 | 1235464.0071
24 | 2705540.326 | 1235456.9485 | 2705544.3676 | 1235457.4095 | 2705547.9069 | 1235456.7497 | 2705551.1299 | 1235455.139 | 2705553.7848 | 1235452.7065
25 | 2705498.1408 | 1235320.9844 | 2705505.873 | 1235325.0581 | 2705529.9073 | 1235335.2927 | 2705569.0161 | 1235360.6957 | 2705548.6765 | 1235427.5077 | 2705548.3018 | 1235432.4047 | 2705551.2641 | 1235433.9697 | 2705553.7291 | 1235436.2485 | 2705555.526 | 1235439.0715 | 2705556.5365 | 1235442.2697 | 2705556.7218 | 1235445.0417 | 2705556.302 | 1235447.7919 | 2705555.3097 | 1235450.3874 | 2705553.7848 | 1235452.7065
26 | 2705540.326 | 1235456.9485 | 2705535.4135 | 1235473.2805
27 | 2705498.1408 | 1235320.9844 | 2705492.5487 | 1235336.6304 | 2705491.5483 | 1235350.7567 | 2705492.0169 | 1235356.0622
28 | 2705528.3226 | 1235496.8547 | 2705535.4135 | 1235473.2805
29 | 2705492.0169 | 1235356.0622 | 2705492.1311 | 1235357.3552
30 | 2705628.6784 | 1235537.9026 | 2705635.796 | 1235538.2071 | 2705645.683 | 1235537.727 | 2705655.2033 | 1235536.5843 | 2705663.674 | 1235534.8669 | 2705672.4149 | 1235532.4316 | 2705696.9967 | 1235525.0298 | 2705705.4078 | 1235523.267 | 2705714.8504 | 1235521.8117 | 2705720.4964 | 1235521.1056
31 | 2705528.3226 | 1235496.8547 | 2705566.3904 | 1235514.7557 | 2705567.0033 | 1235515.0457
32 | 2705492.1311 | 1235357.3552 | 2705492.7898 | 1235364.8117 | 2705490.9131 | 1235368.6147 | 2705476.5205 | 1235370.3371
33 | 2705628.6784 | 1235537.9026 | 2705622.0528 | 1235537.1731 | 2705616.2545 | 1235535.8913 | 2705609.9236 | 1235533.9106 | 2705596.0336 | 1235528.782 | 2705567.0033 | 1235515.0457
34 | 2705476.5205 | 1235370.3371 | 2705471.0208 | 1235370.9953
35 | 2705471.0208 | 1235370.9953 | 2705465.5196 | 1235371.6537
36 | 2705465.5196 | 1235371.6537 | 2705463.9235 | 1235371.8447

## bus_geodata
| x | y | coords
0 | 2706032.9615 | 1235393.7511
1 | 2706035.1856 | 1235373.8508
2 | 2706048.7125 | 1235398.6341
3 | 2706036.6695 | 1235372.6174
4 | 2706042.3976 | 1235356.166
5 | 2706008.778 | 1235388.9023
6 | 2706062.3763 | 1235337.853
7 | 2706079.4713 | 1235350.4456
8 | 2706072.247 | 1235350.4945
9 | 2706083.2215 | 1235334.6004
10 | 2706082.8228 | 1235340.0935
11 | 2705740.9288 | 1235487.3382
12 | 2705770.2512 | 1235481.7161
13 | 2705741.0014 | 1235518.5412
14 | 2705818.8053 | 1235461.0601
15 | 2705949.0574 | 1235401.7358
16 | 2705844.3022 | 1235462.5409
17 | 2705947.4787 | 1235418.5094
18 | 2705991.8317 | 1235395.7468
19 | 2705598.3989 | 1235464.0071
20 | 2705617.4896 | 1235471.6546
21 | 2705553.7848 | 1235452.7065
22 | 2705540.326 | 1235456.9485
23 | 2705498.1408 | 1235320.9844
24 | 2705535.4135 | 1235473.2805
25 | 2705492.0169 | 1235356.0622
26 | 2705754.0452 | 1235517.1945
27 | 2705720.4964 | 1235521.1056
28 | 2705528.3226 | 1235496.8547
29 | 2705958.3859 | 1235417.7144
30 | 2705945.1129 | 1235421.2804
31 | 2705492.1311 | 1235357.3552
32 | 2705628.6784 | 1235537.9026
33 | 2705567.0033 | 1235515.0457
34 | 2705476.5205 | 1235370.3371
35 | 2705471.0208 | 1235370.9953
36 | 2705465.5196 | 1235371.6537
37 | 2705463.9235 | 1235371.8447
38 | 2705740.9288 | 1235487.3382

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98511 | -0.28679 | 0.0082793 | 0.002075
1 | 0.98532 | -0.28262 | 0 | 0
2 | 0.98529 | -0.28335 | 0.0014388 | 0.00036059
3 | 0.98534 | -0.28228 | 0.0005396 | 0.00013524
4 | 0.98553 | -0.27868 | 0 | 0
5 | 0.98682 | -0.25351 | 0 | 0
6 | 0.98547 | -0.27985 | 0 | 0
7 | 0.98545 | -0.28022 | 0.00084153 | 0.00021091
8 | 0.98544 | -0.28033 | 0.00066264 | 0.00016607
9 | 0.98542 | -0.28069 | 0.00056569 | 0.00014178
10 | 0.98543 | -0.28063 | 0.00033571 | 8.4138e-05
11 | 0.99661 | -0.064675 | 0 | 0
12 | 1 | 0 | -0.19871 | -0.050119
13 | 0.99295 | -0.13502 | 0 | 0
14 | 0.99654 | -0.066023 | 0 | 0
15 | 0.98838 | -0.22303 | 0 | 0
16 | 0.99617 | -0.07308 | 0.013783 | 0.0034542
17 | 0.98802 | -0.23017 | 0 | 0
18 | 0.98704 | -0.24919 | 0.021226 | 0.0053198
19 | 0.98399 | -0.30852 | 0.004608 | 0.0011549
20 | 0.98389 | -0.31039 | 0.0050731 | 0.0012714
21 | 0.9844 | -0.30048 | 0 | 0
22 | 0.98473 | -0.29404 | 0 | 0
23 | 0.98199 | -0.34759 | 0 | 0
24 | 0.98511 | -0.28664 | 0.0047274 | 0.0011848
25 | 0.98151 | -0.35702 | 0.003112 | 0.00077995
26 | 0.99234 | -0.14679 | 0.050877 | 0.012751
27 | 0.99157 | -0.16168 | 0.041247 | 0.010338
28 | 0.98577 | -0.27389 | 0 | 0
29 | 0.98796 | -0.23137 | 0.0061582 | 0.0015434
30 | 0.98796 | -0.23132 | 0.017591 | 0.0044086
31 | 0.98149 | -0.35729 | 0.0028256 | 0.00070816
32 | 0.98883 | -0.21442 | 0 | 0
33 | 0.9869 | -0.25178 | 0.0027442 | 0.00068777
34 | 0.98129 | -0.36132 | 0.0022517 | 0.00056432
35 | 0.98125 | -0.36195 | 0.0022517 | 0.00056432
36 | 0.98123 | -0.36235 | 0.0022533 | 0.00056473
37 | 0.98123 | -0.3624 | 0.0017533 | 0.00043943
38 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0082793 | -0.002075 | 0.008281 | 0.0020757 | 1.6458e-06 | 6.9598e-07 | 0.012506 | 0.012506 | 0.012506 | 0.98511 | -0.28679 | 0.98532 | -0.28262 | 3.4357
1 | 0.0014388 | 0.00036026 | -0.0014388 | -0.00036059 | 4.9988e-08 | -3.2762e-07 | 0.0021728 | 0.0021729 | 0.0021729 | 0.98532 | -0.28262 | 0.98529 | -0.28335 | 0.59695
2 | -0.0097198 | -0.002436 | 0.0097199 | 0.002436 | 1.559e-07 | 7.52e-08 | 0.014679 | 0.014679 | 0.014679 | 0.98532 | -0.28262 | 0.98534 | -0.28228 | 4.0326
3 | -0.01026 | -0.0025713 | 0.010261 | 0.0025721 | 1.7584e-06 | 8.7653e-07 | 0.015493 | 0.015493 | 0.015493 | 0.98534 | -0.28228 | 0.98553 | -0.27868 | 4.2564
4 | -0.012667 | -0.003174 | 0.012682 | 0.0031823 | 1.5203e-05 | 8.3157e-06 | 0.019125 | 0.019125 | 0.019125 | 0.98553 | -0.27868 | 0.98682 | -0.25351 | 5.2542
5 | 0.0024058 | 0.00060184 | -0.0024056 | -0.0006021 | 1.3388e-07 | -2.5913e-07 | 0.003632 | 0.0036321 | 0.0036321 | 0.98553 | -0.27868 | 0.98547 | -0.27985 | 0.99784
6 | -0.012682 | -0.0031823 | 0.012685 | 0.0031837 | 2.6157e-06 | 1.4304e-06 | 0.019125 | 0.019125 | 0.019125 | 0.98682 | -0.25351 | 0.98704 | -0.24919 | 5.2541
7 | 0.0015641 | 0.00039149 | -0.0015641 | -0.00039169 | 3.5779e-08 | -1.9506e-07 | 0.0023615 | 0.0023616 | 0.0023616 | 0.98547 | -0.27985 | 0.98544 | -0.28033 | 0.6488
8 | 0.00084155 | 0.00021061 | -0.00084153 | -0.00021091 | 1.481e-08 | -3.0216e-07 | 0.0012706 | 0.0012707 | 0.0012707 | 0.98547 | -0.27985 | 0.98545 | -0.28022 | 0.3491
9 | 0.00090142 | 0.00022562 | -0.00090141 | -0.00022584 | 1.2926e-08 | -2.2876e-07 | 0.001361 | 0.0013611 | 0.0013611 | 0.98544 | -0.28033 | 0.98543 | -0.28063 | 0.37394
10 | -0.00056569 | -0.00014178 | 0.0005657 | 0.00014171 | 1.507e-09 | -6.92e-08 | 0.00085422 | 0.00085419 | 0.00085422 | 0.98542 | -0.28069 | 0.98543 | -0.28063 | 0.23467
11 | -0.12451 | -0.031504 | 0.1249 | 0.031752 | 0.00038776 | 0.00024777 | 0.18601 | 0.18601 | 0.18601 | 0.99661 | -0.064675 | 1 | 0 | 51.102
12 | 0.12451 | 0.031504 | -0.12409 | -0.031236 | 0.0004188 | 0.00026761 | 0.18601 | 0.18601 | 0.18601 | 0.99661 | -0.064675 | 0.99295 | -0.13502 | 51.1021
13 | 0.072164 | 0.018367 | -0.071935 | -0.018221 | 0.0002289 | 0.00014581 | 0.10748 | 0.10748 | 0.10748 | 1 | 0 | 0.99654 | -0.066023 | 29.5276
14 | 0.050905 | 0.012769 | -0.050877 | -0.012751 | 2.8537e-05 | 1.8094e-05 | 0.07629 | 0.07629 | 0.07629 | 0.99295 | -0.13502 | 0.99234 | -0.14679 | 20.9587
15 | 0.073188 | 0.018467 | -0.073095 | -0.018408 | 9.3293e-05 | 5.944e-05 | 0.10972 | 0.10972 | 0.10972 | 0.99295 | -0.13502 | 0.99157 | -0.16168 | 30.1435
16 | 0.058148 | 0.014765 | -0.057712 | -0.014488 | 0.00043575 | 0.00027689 | 0.086893 | 0.086894 | 0.086894 | 0.99654 | -0.066023 | 0.98838 | -0.22303 | 23.8719
17 | 0.013787 | 0.0034568 | -0.013783 | -0.0034542 | 4.6348e-06 | 2.5865e-06 | 0.020587 | 0.020588 | 0.020588 | 0.99654 | -0.066023 | 0.99617 | -0.07308 | 5.6559
18 | 0.023758 | 0.0059576 | -0.02375 | -0.0059527 | 8.0844e-06 | 4.9582e-06 | 0.035769 | 0.035769 | 0.035769 | 0.98838 | -0.22303 | 0.98802 | -0.23017 | 9.8267
19 | 0.033954 | 0.0085301 | -0.033911 | -0.0085036 | 4.2334e-05 | 2.6541e-05 | 0.051125 | 0.051125 | 0.051125 | 0.98838 | -0.22303 | 0.98704 | -0.24919 | 14.0453
20 | 0.0061586 | 0.0015435 | -0.0061582 | -0.0015434 | 3.5177e-07 | 8.5499e-08 | 0.0092752 | 0.0092752 | 0.0092752 | 0.98802 | -0.23017 | 0.98796 | -0.23137 | 2.5481
21 | 0.017592 | 0.0044092 | -0.017591 | -0.0044086 | 9.5814e-07 | 5.666e-07 | 0.026494 | 0.026494 | 0.026494 | 0.98802 | -0.23017 | 0.98796 | -0.23132 | 7.2786
22 | 0.0050735 | 0.0012715 | -0.0050731 | -0.0012714 | 4.5397e-07 | 2.9332e-08 | 0.0076723 | 0.0076724 | 0.0076724 | 0.98399 | -0.30852 | 0.98389 | -0.31039 | 2.1078
23 | -0.0096816 | -0.0024263 | 0.0096853 | 0.0024281 | 3.7087e-06 | 1.7872e-06 | 0.014641 | 0.014641 | 0.014641 | 0.98399 | -0.30852 | 0.9844 | -0.30048 | 4.0222
24 | -0.024174 | -0.0060721 | 0.024181 | 0.0060767 | 7.4307e-06 | 4.567e-06 | 0.036546 | 0.036546 | 0.036546 | 0.9844 | -0.30048 | 0.98473 | -0.29404 | 10.0402
25 | 0.014489 | 0.003644 | -0.014456 | -0.0036254 | 3.253e-05 | 1.8527e-05 | 0.021906 | 0.021906 | 0.021906 | 0.9844 | -0.30048 | 0.98199 | -0.34759 | 6.0183
26 | -0.024181 | -0.0060767 | 0.02419 | 0.0060819 | 8.542e-06 | 5.2498e-06 | 0.036546 | 0.036546 | 0.036546 | 0.98473 | -0.29404 | 0.98511 | -0.28664 | 10.0401
27 | 0.014456 | 0.0036254 | -0.01445 | -0.0036217 | 6.4972e-06 | 3.7017e-06 | 0.021906 | 0.021907 | 0.021907 | 0.98199 | -0.34759 | 0.98151 | -0.35702 | 6.0183
28 | -0.028917 | -0.0072667 | 0.028935 | 0.0072777 | 1.7619e-05 | 1.0962e-05 | 0.043687 | 0.043687 | 0.043687 | 0.98511 | -0.28664 | 0.98577 | -0.27389 | 12.0019
29 | 0.011338 | 0.0028418 | -0.011338 | -0.0028417 | 1.4381e-07 | 7.5635e-08 | 0.017189 | 0.017189 | 0.017189 | 0.98151 | -0.35702 | 0.98149 | -0.35729 | 4.7222
30 | 0.031847 | 0.0080702 | -0.031767 | -0.0080199 | 8.0482e-05 | 5.0301e-05 | 0.047823 | 0.047824 | 0.047824 | 0.99157 | -0.16168 | 0.98883 | -0.21442 | 13.1384
31 | -0.028935 | -0.0072777 | 0.028966 | 0.0072967 | 3.0592e-05 | 1.9033e-05 | 0.043687 | 0.043687 | 0.043687 | 0.98577 | -0.27389 | 0.9869 | -0.25178 | 12.0018
32 | 0.0085119 | 0.0021335 | -0.0085103 | -0.0021328 | 1.6376e-06 | 7.1672e-07 | 0.012905 | 0.012905 | 0.012905 | 0.98149 | -0.35729 | 0.98129 | -0.36132 | 3.5453
33 | 0.031767 | 0.0080199 | -0.03171 | -0.0079845 | 5.6744e-05 | 3.5469e-05 | 0.047824 | 0.047824 | 0.047824 | 0.98883 | -0.21442 | 0.9869 | -0.25178 | 13.1385
34 | 0.0062586 | 0.0015685 | -0.0062584 | -0.0015684 | 1.8708e-07 | 4.9763e-08 | 0.0094905 | 0.0094905 | 0.0094905 | 0.98129 | -0.36132 | 0.98125 | -0.36195 | 2.6073
35 | 0.0040067 | 0.0010041 | -0.0040067 | -0.0010041 | 7.6703e-08 | -2.0896e-08 | 0.006076 | 0.006076 | 0.006076 | 0.98125 | -0.36195 | 0.98123 | -0.36235 | 1.6692
36 | 0.0017533 | 0.00043941 | -0.0017533 | -0.00043943 | 4.2617e-09 | -1.7578e-08 | 0.0026589 | 0.0026589 | 0.0026589 | 0.98123 | -0.36235 | 0.98123 | -0.3624 | 0.73047

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.24539 | 0.061818

## res_load
| p_mw | q_mvar
0 | 0.0082793 | 0.002075
1 | 0.0014388 | 0.00036059
2 | 0.0005396 | 0.00013524
3 | 0.00084153 | 0.00021091
4 | 0.00066264 | 0.00016607
5 | 0.00056569 | 0.00014178
6 | 0.00033571 | 8.4138e-05
7 | 0.046679 | 0.011699
8 | 0.013783 | 0.0034542
9 | 0.021226 | 0.0053198
10 | 0.004608 | 0.0011549
11 | 0.0050731 | 0.0012714
12 | 0.0047274 | 0.0011848
13 | 0.003112 | 0.00077995
14 | 0.050877 | 0.012751
15 | 0.041247 | 0.010338
16 | 0.0061582 | 0.0015434
17 | 0.017591 | 0.0044086
18 | 0.0028256 | 0.00070816
19 | 0.0027442 | 0.00068777
20 | 0.0022517 | 0.00056432
21 | 0.0022517 | 0.00056432
22 | 0.0022533 | 0.00056473
23 | 0.0017533 | 0.00043943

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1