## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_118-18_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_118-18_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_118-18_0_3_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_118-18_0_3_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_118-18_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_118-18_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_118-18_0_3_node_65 | 0.4 | n |  | TRUE
7 | bus_LV_118-18_0_3_node_50 | 0.4 | n |  | TRUE
8 | bus_LV_118-18_0_3_node_27 | 0.4 | n |  | TRUE
9 | bus_LV_118-18_0_3_node_67 | 0.4 | n |  | TRUE
10 | bus_LV_118-18_0_3_node_78 | 0.4 | n |  | TRUE
11 | bus_LV_118-18_0_3_node_51 | 0.4 | n |  | TRUE
12 | bus_LV_118-18_0_3_node_127 | 0.4 | n |  | TRUE
13 | bus_LV_118-18_0_3_node_64 | 0.4 | n |  | TRUE
14 | bus_LV_118-18_0_3_node_25 | 0.4 | n |  | TRUE
15 | bus_LV_118-18_0_3_node_72 | 0.4 | n |  | TRUE
16 | bus_LV_118-18_0_3_node_6 | 0.4 | n |  | TRUE
17 | bus_LV_118-18_0_3_node_8 | 0.4 | n |  | TRUE
18 | bus_LV_118-18_0_3_node_7 | 0.4 | n |  | TRUE
19 | bus_LV_118-18_0_3_node_9 | 0.4 | n |  | TRUE
20 | bus_LV_118-18_0_3_node_10 | 0.4 | n |  | TRUE
21 | bus_LV_118-18_0_3_node_11 | 0.4 | n |  | TRUE
22 | bus_LV_118-18_0_3_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_118-18_0_3_node_79 | 0.4 | n |  | TRUE
24 | bus_LV_118-18_0_3_node_21 | 0.4 | n |  | TRUE
25 | bus_LV_118-18_0_3_node_143 | 0.4 | n |  | TRUE
26 | bus_LV_118-18_0_3_node_82 | 0.4 | n |  | TRUE
27 | bus_LV_118-18_0_3_node_153 | 0.4 | n |  | TRUE
28 | bus_LV_118-18_0_3_node_80 | 0.4 | n |  | TRUE
29 | bus_LV_118-18_0_3_node_81 | 0.4 | n |  | TRUE
30 | bus_LV_118-18_0_3_node_22 | 0.4 | n |  | TRUE
31 | bus_LV_118-18_0_3_node_23 | 0.4 | n |  | TRUE
32 | bus_LV_118-18_0_3_node_144 | 0.4 | n |  | TRUE
33 | bus_LV_118-18_0_3_node_13 | 0.4 | n |  | TRUE
34 | bus_LV_118-18_0_3_node_14 | 0.4 | n |  | TRUE
35 | bus_LV_118-18_0_3_node_15 | 0.4 | n |  | TRUE
36 | bus_LV_118-18_0_3_node_16 | 0.4 | n |  | TRUE
37 | bus_LV_118-18_0_3_node_17 | 0.4 | n |  | TRUE
38 | bus_LV_118-18_0_3_node_43 | 0.4 | n |  | TRUE
39 | bus_LV_118-18_0_3_node_18 | 0.4 | n |  | TRUE
40 | bus_LV_118-18_0_3_node_44 | 0.4 | n |  | TRUE
41 | bus_LV_118-18_0_3_node_106 | 0.4 | n |  | TRUE
42 | bus_LV_118-18_0_3_node_42 | 0.4 | n |  | TRUE
43 | bus_LV_118-18_0_3_node_57 | 0.4 | n |  | TRUE
44 | bus_LV_118-18_0_3_node_93 | 0.4 | n |  | TRUE
45 | bus_LV_118-18_0_3_node_56 | 0.4 | n |  | TRUE
46 | bus_LV_118-18_0_3_node_41 | 0.4 | n |  | TRUE
47 | bus_LV_118-18_0_3_node_19 | 0.4 | n |  | TRUE
48 | bus_LV_118-18_0_3_node_20 | 0.4 | n |  | TRUE
49 | bus_LV_118-18_0_3_node_55 | 0.4 | n |  | TRUE
50 | bus_LV_118-18_0_3_node_145 | 0.4 | n |  | TRUE
51 | bus_LV_118-18_0_3_node_63 | 0.4 | n |  | TRUE
52 | bus_LV_118-18_0_3_node_146 | 0.4 | n |  | TRUE
53 | bus_LV_118-18_0_3_node_36 | 0.4 | n |  | TRUE
54 | bus_LV_118-18_0_3_node_24 | 0.4 | n |  | TRUE
55 | bus_LV_118-18_0_3_node_26 | 0.4 | n |  | TRUE
56 | bus_LV_118-18_0_3_node_28 | 0.4 | n |  | TRUE
57 | bus_LV_118-18_0_3_node_29 | 0.4 | n |  | TRUE
58 | bus_LV_118-18_0_3_node_30 | 0.4 | n |  | TRUE
59 | bus_LV_118-18_0_3_node_31 | 0.4 | n |  | TRUE
60 | bus_LV_118-18_0_3_node_115 | 0.4 | n |  | TRUE
61 | bus_LV_118-18_0_3_node_113 | 0.4 | n |  | TRUE
62 | bus_LV_118-18_0_3_node_118 | 0.4 | n |  | TRUE
63 | bus_LV_118-18_0_3_node_75 | 0.4 | n |  | TRUE
64 | bus_LV_118-18_0_3_node_147 | 0.4 | n |  | TRUE
65 | bus_LV_118-18_0_3_node_148 | 0.4 | n |  | TRUE
66 | bus_LV_118-18_0_3_node_114 | 0.4 | n |  | TRUE
67 | bus_LV_118-18_0_3_node_119 | 0.4 | n |  | TRUE
68 | bus_LV_118-18_0_3_node_120 | 0.4 | n |  | TRUE
69 | bus_LV_118-18_0_3_node_77 | 0.4 | n |  | TRUE
70 | bus_LV_118-18_0_3_node_73 | 0.4 | n |  | TRUE
71 | bus_LV_118-18_0_3_node_32 | 0.4 | n |  | TRUE
72 | bus_LV_118-18_0_3_node_33 | 0.4 | n |  | TRUE
73 | bus_LV_118-18_0_3_node_34 | 0.4 | n |  | TRUE
74 | bus_LV_118-18_0_3_node_35 | 0.4 | n |  | TRUE
75 | bus_LV_118-18_0_3_node_40 | 0.4 | n |  | TRUE
76 | bus_LV_118-18_0_3_node_37 | 0.4 | n |  | TRUE
77 | bus_LV_118-18_0_3_node_52 | 0.4 | n |  | TRUE
78 | bus_LV_118-18_0_3_node_38 | 0.4 | n |  | TRUE
79 | bus_LV_118-18_0_3_node_39 | 0.4 | n |  | TRUE
80 | bus_LV_118-18_0_3_node_89 | 0.4 | n |  | TRUE
81 | bus_LV_118-18_0_3_node_104 | 0.4 | n |  | TRUE
82 | bus_LV_118-18_0_3_node_53 | 0.4 | n |  | TRUE
83 | bus_LV_118-18_0_3_node_54 | 0.4 | n |  | TRUE
84 | bus_LV_118-18_0_3_node_105 | 0.4 | n |  | TRUE
85 | bus_LV_118-18_0_3_node_45 | 0.4 | n |  | TRUE
86 | bus_LV_118-18_0_3_node_46 | 0.4 | n |  | TRUE
87 | bus_LV_118-18_0_3_node_47 | 0.4 | n |  | TRUE
88 | bus_LV_118-18_0_3_node_48 | 0.4 | n |  | TRUE
89 | bus_LV_118-18_0_3_node_49 | 0.4 | n |  | TRUE
90 | bus_LV_118-18_0_3_node_68 | 0.4 | n |  | TRUE
91 | bus_LV_118-18_0_3_node_129 | 0.4 | n |  | TRUE
92 | bus_LV_118-18_0_3_node_74 | 0.4 | n |  | TRUE
93 | bus_LV_118-18_0_3_node_69 | 0.4 | n |  | TRUE
94 | bus_LV_118-18_0_3_node_130 | 0.4 | n |  | TRUE
95 | bus_LV_118-18_0_3_node_76 | 0.4 | n |  | TRUE
96 | bus_LV_118-18_0_3_node_70 | 0.4 | n |  | TRUE
97 | bus_LV_118-18_0_3_node_91 | 0.4 | n |  | TRUE
98 | bus_LV_118-18_0_3_node_128 | 0.4 | n |  | TRUE
99 | bus_LV_118-18_0_3_node_86 | 0.4 | n |  | TRUE
100 | bus_LV_118-18_0_3_node_132 | 0.4 | n |  | TRUE
101 | bus_LV_118-18_0_3_node_84 | 0.4 | n |  | TRUE
102 | bus_LV_118-18_0_3_node_90 | 0.4 | n |  | TRUE
103 | bus_LV_118-18_0_3_node_95 | 0.4 | n |  | TRUE
104 | bus_LV_118-18_0_3_node_101 | 0.4 | n |  | TRUE
105 | bus_LV_118-18_0_3_node_94 | 0.4 | n |  | TRUE
106 | bus_LV_118-18_0_3_node_58 | 0.4 | n |  | TRUE
107 | bus_LV_118-18_0_3_node_59 | 0.4 | n |  | TRUE
108 | bus_LV_118-18_0_3_node_60 | 0.4 | n |  | TRUE
109 | bus_LV_118-18_0_3_node_61 | 0.4 | n |  | TRUE
110 | bus_LV_118-18_0_3_node_62 | 0.4 | n |  | TRUE
111 | bus_LV_118-18_0_3_node_107 | 0.4 | n |  | TRUE
112 | bus_LV_118-18_0_3_node_99 | 0.4 | n |  | TRUE
113 | bus_LV_118-18_0_3_node_111 | 0.4 | n |  | TRUE
114 | bus_LV_118-18_0_3_node_103 | 0.4 | n |  | TRUE
115 | bus_LV_118-18_0_3_node_97 | 0.4 | n |  | TRUE
116 | bus_LV_118-18_0_3_node_66 | 0.4 | n |  | TRUE
117 | bus_LV_118-18_0_3_node_151 | 0.4 | n |  | TRUE
118 | bus_LV_118-18_0_3_node_152 | 0.4 | n |  | TRUE
119 | bus_LV_118-18_0_3_node_71 | 0.4 | n |  | TRUE
120 | bus_LV_118-18_0_3_node_122 | 0.4 | n |  | TRUE
121 | bus_LV_118-18_0_3_node_149 | 0.4 | n |  | TRUE
122 | bus_LV_118-18_0_3_node_150 | 0.4 | n |  | TRUE
123 | bus_LV_118-18_0_3_node_124 | 0.4 | n |  | TRUE
124 | bus_LV_118-18_0_3_node_121 | 0.4 | n |  | TRUE
125 | bus_LV_118-18_0_3_node_109 | 0.4 | n |  | TRUE
126 | bus_LV_118-18_0_3_node_110 | 0.4 | n |  | TRUE
127 | bus_LV_118-18_0_3_node_108 | 0.4 | n |  | TRUE
128 | bus_LV_118-18_0_3_node_83 | 0.4 | n |  | TRUE
129 | bus_LV_118-18_0_3_node_85 | 0.4 | n |  | TRUE
130 | bus_LV_118-18_0_3_node_87 | 0.4 | n |  | TRUE
131 | bus_LV_118-18_0_3_node_88 | 0.4 | n |  | TRUE
132 | bus_LV_118-18_0_3_node_134 | 0.4 | n |  | TRUE
133 | bus_LV_118-18_0_3_node_141 | 0.4 | n |  | TRUE
134 | bus_LV_118-18_0_3_node_133 | 0.4 | n |  | TRUE
135 | bus_LV_118-18_0_3_node_135 | 0.4 | n |  | TRUE
136 | bus_LV_118-18_0_3_node_142 | 0.4 | n |  | TRUE
137 | bus_LV_118-18_0_3_node_140 | 0.4 | n |  | TRUE
138 | bus_LV_118-18_0_3_node_92 | 0.4 | n |  | TRUE
139 | bus_LV_118-18_0_3_node_102 | 0.4 | n |  | TRUE
140 | bus_LV_118-18_0_3_node_96 | 0.4 | n |  | TRUE
141 | bus_LV_118-18_0_3_node_100 | 0.4 | n |  | TRUE
142 | bus_LV_118-18_0_3_node_116 | 0.4 | n |  | TRUE
143 | bus_LV_118-18_0_3_node_117 | 0.4 | n |  | TRUE
144 | bus_LV_118-18_0_3_node_123 | 0.4 | n |  | TRUE
145 | bus_LV_118-18_0_3_node_125 | 0.4 | n |  | TRUE
146 | bus_LV_118-18_0_3_node_126 | 0.4 | n |  | TRUE
147 | bus_LV_118-18_0_3_node_131 | 0.4 | n |  | TRUE
148 | bus_LV_118-18_0_3_node_136 | 0.4 | n |  | TRUE
149 | bus_LV_118-18_0_3_node_137 | 0.4 | n |  | TRUE
150 | bus_LV_118-18_0_3_node_138 | 0.4 | n |  | TRUE
151 | bus_LV_118-18_0_3_node_139 | 0.4 | n |  | TRUE
152 | bus_MV_9_2_node_146 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_118-18_0_3_load_0 | 0 | 0.0019838 | 0.0004972 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_118-18_0_3_load_1 | 1 | 0.0043939 | 0.0011012 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_118-18_0_3_load_4 | 4 | 0.0035738 | 0.00089568 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_118-18_0_3_load_5 | 5 | 0.0049657 | 0.0012445 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_118-18_0_3_load_65 | 6 | 0.0036185 | 0.00090688 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_118-18_0_3_load_50 | 7 | 0.0025733 | 0.00064492 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_118-18_0_3_load_78 | 10 | 0.0025095 | 0.00062893 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_118-18_0_3_load_51 | 11 | 0.0013824 | 0.00034647 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_118-18_0_3_load_127 | 12 | 0.0014319 | 0.00035888 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_118-18_0_3_load_64 | 13 | 0.001488 | 0.00037293 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_118-18_0_3_load_72 | 15 | 0.0012146 | 0.0003044 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_118-18_0_3_load_6 | 16 | 0.0047291 | 0.0011852 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_118-18_0_3_load_10 | 20 | 0.0023155 | 0.00058032 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_118-18_0_3_load_11 | 21 | 0.004869 | 0.0012203 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_118-18_0_3_load_12 | 22 | 0.00089335 | 0.00022389 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_118-18_0_3_load_79 | 23 | 0.0013178 | 0.00033027 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_118-18_0_3_load_143 | 25 | 0.00088546 | 0.00022192 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_118-18_0_3_load_153 | 27 | 0.013965 | 0.0034999 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_118-18_0_3_load_22 | 30 | 0.00089336 | 0.0002239 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_118-18_0_3_load_23 | 31 | 0.0015742 | 0.00039453 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_118-18_0_3_load_144 | 32 | 0.00093565 | 0.0002345 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_118-18_0_3_load_13 | 33 | 0.001494 | 0.00037444 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_118-18_0_3_load_14 | 34 | 0.0044693 | 0.0011201 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_118-18_0_3_load_15 | 35 | 0.00148 | 0.00037093 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_118-18_0_3_load_17 | 37 | 0.00099168 | 0.00024854 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_118-18_0_3_load_18 | 39 | 0.0011362 | 0.00028477 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_118-18_0_3_load_106 | 41 | 0.0017357 | 0.00043501 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_118-18_0_3_load_93 | 44 | 0.0011788 | 0.00029543 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_118-18_0_3_load_56 | 45 | 0.00085528 | 0.00021435 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_118-18_0_3_load_41 | 46 | 0.0083041 | 0.0020812 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_118-18_0_3_load_19 | 47 | 0.00095757 | 0.00023999 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_118-18_0_3_load_20 | 48 | 0.0015644 | 0.00039208 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_118-18_0_3_load_55 | 49 | 0.0023139 | 0.00057991 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_118-18_0_3_load_145 | 50 | 0.00087762 | 0.00021995 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_118-18_0_3_load_63 | 51 | 0.0013393 | 0.00033567 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_118-18_0_3_load_146 | 52 | 0.00090051 | 0.00022569 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_118-18_0_3_load_36 | 53 | 0.0017699 | 0.00044359 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_118-18_0_3_load_24 | 54 | 0.0044468 | 0.0011145 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_118-18_0_3_load_29 | 57 | 0.0060685 | 0.0015209 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_118-18_0_3_load_30 | 58 | 0.0036898 | 0.00092475 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_118-18_0_3_load_31 | 59 | 0.0057687 | 0.0014458 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_118-18_0_3_load_113 | 61 | 0.0036909 | 0.00092504 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_118-18_0_3_load_148 | 65 | 0.0060722 | 0.0015218 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_118-18_0_3_load_119 | 67 | 0.0099157 | 0.0024851 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_118-18_0_3_load_120 | 68 | 0.0048328 | 0.0012112 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_118-18_0_3_load_73 | 70 | 0.0061038 | 0.0015298 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_118-18_0_3_load_32 | 71 | 0.0049826 | 0.0012488 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_118-18_0_3_load_33 | 72 | 0.0010023 | 0.00025121 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_118-18_0_3_load_34 | 73 | 0.0019498 | 0.00048868 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_118-18_0_3_load_40 | 75 | 0.0017075 | 0.00042795 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_118-18_0_3_load_37 | 76 | 0.006315 | 0.0015827 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_118-18_0_3_load_38 | 78 | 0.004855 | 0.0012168 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_118-18_0_3_load_39 | 79 | 0.0016455 | 0.0004124 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_118-18_0_3_load_89 | 80 | 0.0029737 | 0.00074527 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_118-18_0_3_load_54 | 83 | 0.0016686 | 0.0004182 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_118-18_0_3_load_105 | 84 | 0.0013318 | 0.00033379 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_118-18_0_3_load_45 | 85 | 0.0033842 | 0.00084816 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_118-18_0_3_load_46 | 86 | 0.0060514 | 0.0015166 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_118-18_0_3_load_47 | 87 | 0.0029644 | 0.00074295 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_118-18_0_3_load_48 | 88 | 0.0014172 | 0.00035518 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_118-18_0_3_load_68 | 90 | 0.0051764 | 0.0012973 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_118-18_0_3_load_129 | 91 | 0.0023186 | 0.00058109 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_118-18_0_3_load_130 | 94 | 0.0025526 | 0.00063973 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_118-18_0_3_load_76 | 95 | 0.0018068 | 0.00045282 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_118-18_0_3_load_70 | 96 | 0.0023287 | 0.00058364 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_118-18_0_3_load_91 | 97 | 0.0016322 | 0.00040907 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_118-18_0_3_load_128 | 98 | 0.0016684 | 0.00041814 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_118-18_0_3_load_132 | 100 | 0.0012732 | 0.0003191 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_118-18_0_3_load_84 | 101 | 0.0012891 | 0.00032307 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_118-18_0_3_load_90 | 102 | 0.0017049 | 0.0004273 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_118-18_0_3_load_101 | 104 | 0.0010377 | 0.00026006 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_118-18_0_3_load_94 | 105 | 0.0063329 | 0.0015872 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_118-18_0_3_load_58 | 106 | 0.002156 | 0.00054035 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_118-18_0_3_load_59 | 107 | 0.0037915 | 0.00095024 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_118-18_0_3_load_60 | 108 | 0.0011255 | 0.00028207 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_118-18_0_3_load_61 | 109 | 0.0016288 | 0.00040823 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_118-18_0_3_load_62 | 110 | 0.0012199 | 0.00030574 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_118-18_0_3_load_107 | 111 | 0.00068877 | 0.00017262 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_118-18_0_3_load_111 | 113 | 0.0037788 | 0.00094706 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_118-18_0_3_load_103 | 114 | 0.00069439 | 0.00017403 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_118-18_0_3_load_66 | 116 | 0.0047306 | 0.0011856 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_118-18_0_3_load_151 | 117 | 0.0023209 | 0.00058167 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_118-18_0_3_load_152 | 118 | 0.0013786 | 0.0003455 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_118-18_0_3_load_71 | 119 | 0.0026754 | 0.00067051 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_118-18_0_3_load_149 | 121 | 0.0057578 | 0.001443 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_118-18_0_3_load_150 | 122 | 0.0050414 | 0.0012635 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_118-18_0_3_load_124 | 123 | 0.0048367 | 0.0012122 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_118-18_0_3_load_121 | 124 | 0.0030612 | 0.00076721 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_118-18_0_3_load_110 | 126 | 0.0013062 | 0.00032737 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_118-18_0_3_load_108 | 127 | 0.0014206 | 0.00035604 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_118-18_0_3_load_83 | 128 | 0.0019058 | 0.00047765 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_118-18_0_3_load_87 | 130 | 0.0012871 | 0.00032257 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_118-18_0_3_load_88 | 131 | 0.0011094 | 0.00027803 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_118-18_0_3_load_134 | 132 | 0.0012902 | 0.00032335 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_118-18_0_3_load_133 | 134 | 0.0013284 | 0.00033294 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_118-18_0_3_load_135 | 135 | 0.0012796 | 0.0003207 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_118-18_0_3_load_142 | 136 | 0.0015514 | 0.00038882 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_118-18_0_3_load_140 | 137 | 0.00098837 | 0.00024771 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_118-18_0_3_load_92 | 138 | 0.0016925 | 0.00042418 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_118-18_0_3_load_102 | 139 | 0.0015656 | 0.00039237 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_118-18_0_3_load_96 | 140 | 0.0021183 | 0.00053089 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_118-18_0_3_load_100 | 141 | 0.0011362 | 0.00028475 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_118-18_0_3_load_116 | 142 | 0.0099815 | 0.0025016 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_118-18_0_3_load_117 | 143 | 0.0059295 | 0.0014861 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_118-18_0_3_load_125 | 145 | 0.0088711 | 0.0022233 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_118-18_0_3_load_126 | 146 | 0.0075899 | 0.0019022 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_118-18_0_3_load_131 | 147 | 0.0018174 | 0.00045549 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_118-18_0_3_load_136 | 148 | 0.0015014 | 0.00037628 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_118-18_0_3_load_137 | 149 | 0.002519 | 0.00063133 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_118-18_0_3_load_138 | 150 | 0.00095215 | 0.00023863 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_118-18_0_3_load_139 | 151 | 0.0028031 | 0.00070252 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 138 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_118-18_0_3_line_0 |  | 0 | 1 | 0.024753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_118-18_0_3_line_1 |  | 1 | 2 | 0.03401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_118-18_0_3_line_2 |  | 2 | 7 | 0.018128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_118-18_0_3_line_3 |  | 3 | 4 | 0.023846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_118-18_0_3_line_4 |  | 3 | 5 | 0.037564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_118-18_0_3_line_5 |  | 3 | 6 | 0.056586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_118-18_0_3_line_6 |  | 4 | 8 | 0.028423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_118-18_0_3_line_7 |  | 6 | 9 | 0.035558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_118-18_0_3_line_8 |  | 7 | 10 | 0.0040289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_118-18_0_3_line_9 |  | 8 | 13 | 0.024829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_118-18_0_3_line_10 |  | 8 | 14 | 0.037524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_118-18_0_3_line_11 |  | 9 | 15 | 0.023209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_118-18_0_3_line_12 |  | 10 | 96 | 0.014283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_118-18_0_3_line_13 |  | 11 | 12 | 0.0054874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_118-18_0_3_line_14 |  | 12 | 40 | 0.025633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_118-18_0_3_line_15 |  | 14 | 56 | 0.009034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_118-18_0_3_line_16 |  | 14 | 57 | 0.028871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_118-18_0_3_line_17 |  | 14 | 54 | 0.016637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_118-18_0_3_line_18 |  | 16 | 17 | 0.0060541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_118-18_0_3_line_19 |  | 17 | 21 | 0.022622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_118-18_0_3_line_20 |  | 17 | 22 | 0.014169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_118-18_0_3_line_21 |  | 18 | 19 | 0.017302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_118-18_0_3_line_22 |  | 18 | 20 | 0.0059918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_118-18_0_3_line_23 |  | 19 | 23 | 0.020382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_118-18_0_3_line_24 |  | 21 | 24 | 0.016462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_118-18_0_3_line_25 |  | 22 | 25 | 0.0070071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_118-18_0_3_line_26 |  | 23 | 28 | 0.0030319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_118-18_0_3_line_27 |  | 24 | 30 | 0.014658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_118-18_0_3_line_28 |  | 24 | 31 | 0.016746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_118-18_0_3_line_29 |  | 25 | 32 | 0.0070084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_118-18_0_3_line_30 |  | 26 | 27 | 0.013665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_118-18_0_3_line_31 |  | 26 | 28 | 0.029793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_118-18_0_3_line_32 |  | 26 | 29 | 0.020663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_118-18_0_3_line_33 |  | 29 | 125 | 0.024761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_118-18_0_3_line_34 |  | 29 | 113 | 0.022938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_118-18_0_3_line_35 |  | 30 | 50 | 0.0070834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_118-18_0_3_line_36 |  | 31 | 51 | 0.0014232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_118-18_0_3_line_37 |  | 32 | 136 | 0.0096328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_118-18_0_3_line_38 |  | 33 | 34 | 0.0088802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_118-18_0_3_line_39 |  | 33 | 35 | 0.0085563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_118-18_0_3_line_40 |  | 34 | 36 | 0.0067885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_118-18_0_3_line_41 |  | 35 | 37 | 0.0071444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_118-18_0_3_line_42 |  | 36 | 38 | 0.010084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_118-18_0_3_line_43 |  | 37 | 39 | 0.0043164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_118-18_0_3_line_44 |  | 38 | 46 | 0.0057082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_118-18_0_3_line_45 |  | 39 | 47 | 0.0019224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_118-18_0_3_line_46 |  | 40 | 41 | 0.020704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_118-18_0_3_line_47 |  | 40 | 42 | 0.005582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_118-18_0_3_line_48 |  | 41 | 84 | 0.008763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_118-18_0_3_line_49 |  | 42 | 46 | 0.021512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_118-18_0_3_line_50 |  | 43 | 44 | 0.021106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_118-18_0_3_line_51 |  | 43 | 45 | 0.00053968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_118-18_0_3_line_52 |  | 44 | 105 | 0.0010631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_118-18_0_3_line_53 |  | 45 | 49 | 0.0059094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_118-18_0_3_line_54 |  | 47 | 48 | 0.019668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_118-18_0_3_line_55 |  | 48 | 49 | 0.0037418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_118-18_0_3_line_56 |  | 50 | 52 | 0.0019183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_118-18_0_3_line_57 |  | 51 | 53 | 0.013403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_118-18_0_3_line_58 |  | 53 | 73 | 0.0046306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_118-18_0_3_line_59 |  | 54 | 55 | 0.020694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_118-18_0_3_line_60 |  | 55 | 58 | 0.045729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_118-18_0_3_line_61 |  | 55 | 59 | 0.0080329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_118-18_0_3_line_62 |  | 56 | 60 | 0.048277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_118-18_0_3_line_63 |  | 56 | 61 | 0.032232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_118-18_0_3_line_64 |  | 58 | 62 | 0.0038793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_118-18_0_3_line_65 |  | 59 | 63 | 0.003972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_118-18_0_3_line_66 |  | 60 | 64 | 0.024627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_118-18_0_3_line_67 |  | 60 | 65 | 0.010554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_118-18_0_3_line_68 |  | 61 | 66 | 0.0026415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_118-18_0_3_line_69 |  | 62 | 67 | 0.006382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_118-18_0_3_line_70 |  | 62 | 68 | 0.018467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_118-18_0_3_line_71 |  | 63 | 69 | 0.017726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_118-18_0_3_line_72 |  | 63 | 70 | 0.014581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_118-18_0_3_line_73 |  | 64 | 117 | 0.006554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_118-18_0_3_line_74 |  | 64 | 118 | 0.012671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_118-18_0_3_line_75 |  | 64 | 116 | 0.037019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_118-18_0_3_line_76 |  | 66 | 142 | 0.006066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_118-18_0_3_line_77 |  | 66 | 143 | 0.013094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_118-18_0_3_line_78 |  | 69 | 121 | 0.004218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_118-18_0_3_line_79 |  | 69 | 122 | 0.020437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_118-18_0_3_line_80 |  | 70 | 92 | 0.011754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_118-18_0_3_line_81 |  | 71 | 72 | 0.0038766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_118-18_0_3_line_82 |  | 71 | 73 | 0.01195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_118-18_0_3_line_83 |  | 72 | 74 | 0.0060947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_118-18_0_3_line_84 |  | 74 | 75 | 0.0075429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
85 | LV_118-18_0_3_line_85 |  | 74 | 76 | 0.018922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
86 | LV_118-18_0_3_line_86 |  | 75 | 77 | 0.01089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
87 | LV_118-18_0_3_line_87 |  | 76 | 78 | 0.013719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
88 | LV_118-18_0_3_line_88 |  | 77 | 82 | 0.011834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
89 | LV_118-18_0_3_line_89 |  | 77 | 83 | 0.020519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_118-18_0_3_line_90 |  | 78 | 79 | 0.0033608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
91 | LV_118-18_0_3_line_91 |  | 79 | 80 | 0.018915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
92 | LV_118-18_0_3_line_92 |  | 80 | 81 | 0.0022757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
93 | LV_118-18_0_3_line_93 |  | 81 | 84 | 0.0034796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_118-18_0_3_line_94 |  | 81 | 119 | 0.01243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
95 | LV_118-18_0_3_line_95 |  | 82 | 97 | 0.024296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
96 | LV_118-18_0_3_line_96 |  | 83 | 98 | 0.0097535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_118-18_0_3_line_97 |  | 85 | 86 | 0.0045939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_118-18_0_3_line_98 |  | 85 | 87 | 0.021377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_118-18_0_3_line_99 |  | 86 | 88 | 0.035411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
100 | LV_118-18_0_3_line_100 |  | 87 | 89 | 0.012034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_118-18_0_3_line_101 |  | 88 | 90 | 0.012103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
102 | LV_118-18_0_3_line_102 |  | 89 | 91 | 0.0071732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_118-18_0_3_line_103 |  | 89 | 92 | 0.014863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_118-18_0_3_line_104 |  | 90 | 93 | 0.021014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
105 | LV_118-18_0_3_line_105 |  | 91 | 94 | 0.025297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_118-18_0_3_line_106 |  | 92 | 95 | 0.0085279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_118-18_0_3_line_107 |  | 93 | 96 | 0.022062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_118-18_0_3_line_108 |  | 93 | 119 | 0.0052886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
109 | LV_118-18_0_3_line_109 |  | 94 | 147 | 0.0062354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_118-18_0_3_line_110 |  | 95 | 120 | 0.0050794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_118-18_0_3_line_111 |  | 97 | 102 | 0.0034719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
112 | LV_118-18_0_3_line_112 |  | 99 | 100 | 0.020871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_118-18_0_3_line_113 |  | 99 | 101 | 0.014644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_118-18_0_3_line_114 |  | 100 | 134 | 0.0041629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_118-18_0_3_line_115 |  | 101 | 128 | 0.0067536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_118-18_0_3_line_116 |  | 102 | 138 | 0.00048079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
117 | LV_118-18_0_3_line_117 |  | 103 | 104 | 0.031144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_118-18_0_3_line_118 |  | 103 | 105 | 0.038853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_118-18_0_3_line_119 |  | 104 | 139 | 0.020468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_118-18_0_3_line_120 |  | 106 | 107 | 0.028025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_118-18_0_3_line_121 |  | 106 | 108 | 0.0022353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_118-18_0_3_line_122 |  | 107 | 109 | 0.021724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_118-18_0_3_line_123 |  | 108 | 110 | 0.00062712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_118-18_0_3_line_124 |  | 109 | 111 | 0.0012833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_118-18_0_3_line_125 |  | 110 | 112 | 0.01323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_118-18_0_3_line_126 |  | 111 | 113 | 0.023207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_118-18_0_3_line_127 |  | 112 | 114 | 0.01703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_118-18_0_3_line_128 |  | 112 | 115 | 0.00352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_118-18_0_3_line_129 |  | 114 | 139 | 0.019694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_118-18_0_3_line_130 |  | 115 | 140 | 0.013596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_118-18_0_3_line_131 |  | 120 | 123 | 0.027851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_118-18_0_3_line_132 |  | 120 | 124 | 0.034911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_118-18_0_3_line_133 |  | 124 | 144 | 0.0039217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_118-18_0_3_line_134 |  | 125 | 126 | 0.04244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_118-18_0_3_line_135 |  | 125 | 127 | 0.027873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_118-18_0_3_line_136 |  | 127 | 141 | 0.017318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_118-18_0_3_line_137 |  | 128 | 129 | 0.011379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_118-18_0_3_line_138 |  | 129 | 130 | 0.013752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_118-18_0_3_line_139 |  | 129 | 131 | 0.01357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_118-18_0_3_line_140 |  | 130 | 132 | 0.0070508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_118-18_0_3_line_141 |  | 131 | 133 | 0.019441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_118-18_0_3_line_142 |  | 132 | 135 | 0.0071366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_118-18_0_3_line_143 |  | 133 | 136 | 0.013508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_118-18_0_3_line_144 |  | 133 | 137 | 0.014437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_118-18_0_3_line_145 |  | 135 | 148 | 0.0027592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_118-18_0_3_line_146 |  | 137 | 150 | 0.0069314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_118-18_0_3_line_147 |  | 144 | 145 | 0.023365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_118-18_0_3_line_148 |  | 144 | 146 | 0.005014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_118-18_0_3_line_149 |  | 149 | 150 | 0.0071651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_118-18_0_3_line_150 |  | 149 | 151 | 0.0026144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_118-18_0_3_trafo_92 | 0.63 MVA 20/0.4 kV | 152 | 138 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2707564.546 | 1234754.8994 | 2707541.5656 | 1234764.0983
1 | 2707509.9911 | 1234776.7375 | 2707541.5656 | 1234764.0983
2 | 2707509.9911 | 1234776.7375 | 2707498.3283 | 1234774.447 | 2707493.1148 | 1234771.0146
3 | 2707579.382 | 1234723.3857 | 2707590.0506 | 1234702.0597
4 | 2707547.3192 | 1234719.6469 | 2707550.7539 | 1234720.6209 | 2707557.4008 | 1234717.7057 | 2707565.006 | 1234712.8841 | 2707569.5165 | 1234715.9014 | 2707579.382 | 1234723.3857
5 | 2707579.382 | 1234723.3857 | 2707634.018 | 1234738.1136
6 | 2707602.7673 | 1234676.6398 | 2707590.0506 | 1234702.0597
7 | 2707664.871 | 1234749.2983 | 2707653.3205 | 1234742.8952 | 2707645.3885 | 1234735.6793 | 2707634.018 | 1234738.1136
8 | 2707493.1148 | 1234771.0146 | 2707489.7497 | 1234768.7991
9 | 2707602.7673 | 1234676.6398 | 2707624.9131 | 1234687.8665
10 | 2707567.9892 | 1234662.2992 | 2707602.7673 | 1234676.6398
11 | 2707664.871 | 1234749.2983 | 2707680.8671 | 1234732.4821
12 | 2707477.8202 | 1234760.945 | 2707489.7497 | 1234768.7991
13 | 2707467.8286 | 1234793.099 | 2707472.9443 | 1234791.1138
14 | 2707443.2732 | 1234799.5929 | 2707453.6478 | 1234798.6019 | 2707467.8286 | 1234793.099
15 | 2707567.9892 | 1234662.2992 | 2707571.1933 | 1234653.8507
16 | 2707567.9892 | 1234662.2992 | 2707564.3681 | 1234660.3322 | 2707566.8743 | 1234639.8396 | 2707562.7886 | 1234639.2763
17 | 2707567.9892 | 1234662.2992 | 2707565.2784 | 1234666.4978 | 2707553.6844 | 1234665.4713
18 | 2707352.3582 | 1234642.8962 | 2707348.7512 | 1234638.0339
19 | 2707352.3582 | 1234642.8962 | 2707365.9043 | 1234661.0143
20 | 2707352.3582 | 1234642.8962 | 2707363.4095 | 1234634.029
21 | 2707324.9013 | 1234605.883 | 2707321.6853 | 1234608.3045 | 2707320.3151 | 1234606.6229 | 2707318.4385 | 1234604.8877 | 2707316.619 | 1234604.1876 | 2707313.835 | 1234604.0706 | 2707311.2749 | 1234601.2
22 | 2707324.9013 | 1234605.883 | 2707328.6645 | 1234602.9264 | 2707327.9918 | 1234601.9253
23 | 2707311.2749 | 1234601.2 | 2707297.5254 | 1234616.2455
24 | 2707375.7616 | 1234674.1986 | 2707365.9043 | 1234661.0143
25 | 2707363.4095 | 1234634.029 | 2707368.8749 | 1234629.6438
26 | 2707295.4801 | 1234618.4836 | 2707297.5254 | 1234616.2455
27 | 2707375.7616 | 1234674.1986 | 2707385.5462 | 1234663.2842
28 | 2707375.7616 | 1234674.1986 | 2707385.7884 | 1234687.6114
29 | 2707374.3412 | 1234625.2578 | 2707368.8749 | 1234629.6438
30 | 2707292.1119 | 1234642.3188 | 2707291.1475 | 1234642.4793 | 2707278.5881 | 1234644.5319
31 | 2707292.1119 | 1234642.3188 | 2707289.3357 | 1234631.2936 | 2707291.7565 | 1234620.0842 | 2707292.484 | 1234616.6948 | 2707295.4801 | 1234618.4836
32 | 2707292.1119 | 1234642.3188 | 2707295.4097 | 1234658.4129 | 2707299.4882 | 1234657.2746
33 | 2707296.5419 | 1234678.7156 | 2707295.5159 | 1234676.4175 | 2707295.2436 | 1234663.4138 | 2707295.4097 | 1234658.4129 | 2707299.4882 | 1234657.2746
34 | 2707299.4882 | 1234657.2746 | 2707300.1932 | 1234666.8613 | 2707301.0083 | 1234677.8956 | 2707300.8932 | 1234680.1541
35 | 2707385.5462 | 1234663.2842 | 2707390.2745 | 1234658.0099
36 | 2707385.7884 | 1234687.6114 | 2707386.6406 | 1234688.7513
37 | 2707381.8545 | 1234619.2295 | 2707374.3412 | 1234625.2578
38 | 2707394.5364 | 1234824.9026 | 2707402.5196 | 1234821.0134
39 | 2707386.7261 | 1234828.3936 | 2707392.8949 | 1234825.7023 | 2707394.5364 | 1234824.9026
40 | 2707408.9899 | 1234819.0214 | 2707403.6568 | 1234820.4594 | 2707402.5196 | 1234821.0134
41 | 2707386.7261 | 1234828.3936 | 2707380.1777 | 1234831.2505
42 | 2707408.9899 | 1234819.0214 | 2707418.9607 | 1234817.3336
43 | 2707380.1777 | 1234831.2505 | 2707376.2215 | 1234832.9765
44 | 2707418.9607 | 1234817.3336 | 2707419.5781 | 1234812.9192 | 2707420.7076 | 1234812.3818
45 | 2707374.4594 | 1234833.7452 | 2707376.2215 | 1234832.9765
46 | 2707443.2732 | 1234799.5929 | 2707445.2591 | 1234780.2139 | 2707445.0374 | 1234779.0106
47 | 2707443.2732 | 1234799.5929 | 2707437.6845 | 1234799.2582
48 | 2707443.4493 | 1234770.3927 | 2707445.0374 | 1234779.0106
49 | 2707437.6845 | 1234799.2582 | 2707429.67 | 1234805.7961 | 2707422.6403 | 1234811.4623 | 2707420.7076 | 1234812.3818
50 | 2707346.5461 | 1234844.2012 | 2707327.1566 | 1234852.5398
51 | 2707347.0627 | 1234844.0454 | 2707346.5461 | 1234844.2012
52 | 2707327.1566 | 1234852.5398 | 2707326.18 | 1234852.9598
53 | 2707347.0627 | 1234844.0454 | 2707352.7202 | 1234842.3385
54 | 2707374.4594 | 1234833.7452 | 2707359.3421 | 1234840.3406 | 2707356.3025 | 1234841.2576
55 | 2707352.7202 | 1234842.3385 | 2707356.3025 | 1234841.2576
56 | 2707391.555 | 1234656.5816 | 2707390.2745 | 1234658.0099
57 | 2707386.6406 | 1234688.7513 | 2707394.6654 | 1234699.4861
58 | 2707397.438 | 1234703.1949 | 2707394.6654 | 1234699.4861
59 | 2707533.0706 | 1234663.6461 | 2707553.6844 | 1234665.4713
60 | 2707533.0706 | 1234663.6461 | 2707536.8619 | 1234631.9681 | 2707531.8632 | 1234619.0787
61 | 2707533.0706 | 1234663.6461 | 2707525.0692 | 1234662.9357
62 | 2707571.1933 | 1234653.8507 | 2707597.27 | 1234660.3945 | 2707603.9716 | 1234660.3158 | 2707609.5208 | 1234656.5689 | 2707614.5123 | 1234650.1766
63 | 2707571.1933 | 1234653.8507 | 2707573.6427 | 1234627.7194 | 2707572.6982 | 1234623.8549 | 2707572.8848 | 1234621.856
64 | 2707530.4606 | 1234615.4618 | 2707531.8632 | 1234619.0787
65 | 2707521.1127 | 1234662.5844 | 2707525.0692 | 1234662.9357
66 | 2707614.5123 | 1234650.1766 | 2707617.5852 | 1234637.2779 | 2707617.6841 | 1234631.82 | 2707615.5505 | 1234626.3104
67 | 2707614.5123 | 1234650.1766 | 2707610.3953 | 1234648.423 | 2707604.4551 | 1234647.0032
68 | 2707573.1303 | 1234619.2259 | 2707572.8848 | 1234621.856
69 | 2707530.4606 | 1234615.4618 | 2707524.1076 | 1234614.6796
70 | 2707530.4606 | 1234615.4618 | 2707532.3509 | 1234600.5401 | 2707530.3649 | 1234597.7465
71 | 2707521.1127 | 1234662.5844 | 2707523.1123 | 1234644.9738
72 | 2707521.1127 | 1234662.5844 | 2707506.6163 | 1234661.0167
73 | 2707615.5505 | 1234626.3104 | 2707609.0496 | 1234625.3364
74 | 2707615.5505 | 1234626.3104 | 2707616.3556 | 1234615.728 | 2707615.6943 | 1234613.7812
75 | 2707615.5505 | 1234626.3104 | 2707650.3792 | 1234638.8542
76 | 2707573.1303 | 1234619.2259 | 2707567.0676 | 1234618.7157
77 | 2707573.1303 | 1234619.2259 | 2707574.0826 | 1234608.8685 | 2707572.7623 | 1234606.5206
78 | 2707523.1123 | 1234644.9738 | 2707518.903 | 1234644.5528
79 | 2707523.1123 | 1234644.9738 | 2707524.94 | 1234628.9167 | 2707520.6872 | 1234628.3838
80 | 2707494.9309 | 1234659.753 | 2707506.6163 | 1234661.0167
81 | 2707406.9138 | 1234715.8706 | 2707404.5927 | 1234712.7657
82 | 2707397.438 | 1234703.1949 | 2707404.5927 | 1234712.7657
83 | 2707410.563 | 1234720.7521 | 2707406.9138 | 1234715.8706
84 | 2707410.563 | 1234720.7521 | 2707416.2681 | 1234716.7522 | 2707416.4293 | 1234716.1999
85 | 2707410.563 | 1234720.7521 | 2707422.4219 | 1234735.4965
86 | 2707419.4803 | 1234705.7462 | 2707416.4293 | 1234716.1999
87 | 2707431.0201 | 1234746.1867 | 2707422.4219 | 1234735.4965
88 | 2707419.4803 | 1234705.7462 | 2707422.7975 | 1234694.3864
89 | 2707419.4803 | 1234705.7462 | 2707439.5439 | 1234710.0435
90 | 2707431.0201 | 1234746.1867 | 2707433.1264 | 1234748.8056
91 | 2707442.3986 | 1234764.7341 | 2707441.3202 | 1234758.9931 | 2707433.1264 | 1234748.8056
92 | 2707442.8187 | 1234766.9707 | 2707442.3986 | 1234764.7341
93 | 2707442.8187 | 1234766.9707 | 2707443.4493 | 1234770.3927
94 | 2707442.8187 | 1234766.9707 | 2707452.6853 | 1234759.411
95 | 2707422.7975 | 1234694.3864 | 2707440.7484 | 1234690.1743 | 2707445.5421 | 1234686.8087
96 | 2707449.0811 | 1234712.0862 | 2707439.5439 | 1234710.0435
97 | 2707493.8727 | 1234698.8186 | 2707495.4755 | 1234703.1238
98 | 2707493.8727 | 1234698.8186 | 2707486.4141 | 1234678.7847
99 | 2707495.4755 | 1234703.1238 | 2707496.1279 | 1234704.876 | 2707492.3907 | 1234721.0319 | 2707479.6106 | 1234732.1792
100 | 2707482.2153 | 1234667.5068 | 2707486.4141 | 1234678.7847
101 | 2707470.8203 | 1234740.4675 | 2707473.2447 | 1234737.7318 | 2707479.6106 | 1234732.1792
102 | 2707482.2153 | 1234667.5068 | 2707479.7118 | 1234660.7847
103 | 2707482.2153 | 1234667.5068 | 2707494.9309 | 1234659.753
104 | 2707456.8833 | 1234756.1945 | 2707470.8203 | 1234740.4675
105 | 2707479.7118 | 1234660.7847 | 2707470.8829 | 1234637.0779
106 | 2707494.9309 | 1234659.753 | 2707495.8483 | 1234651.2746
107 | 2707456.8833 | 1234756.1945 | 2707472.3298 | 1234757.3303 | 2707477.8202 | 1234760.945
108 | 2707456.8833 | 1234756.1945 | 2707452.6853 | 1234759.411
109 | 2707468.7067 | 1234631.2346 | 2707470.8829 | 1234637.0779
110 | 2707496.3947 | 1234646.2247 | 2707495.8483 | 1234651.2746
111 | 2707448.3836 | 1234684.8137 | 2707445.5421 | 1234686.8087
112 | 2707427.548 | 1234671.5881 | 2707444.3101 | 1234659.1536
113 | 2707427.548 | 1234671.5881 | 2707427.7185 | 1234667.1878 | 2707421.9891 | 1234658.7006
114 | 2707447.6535 | 1234656.6735 | 2707444.3101 | 1234659.1536
115 | 2707418.2105 | 1234653.103 | 2707421.9891 | 1234658.7006
116 | 2707448.3836 | 1234684.8137 | 2707448.7771 | 1234684.5374
117 | 2707291.0591 | 1234858.5435 | 2707291.4434 | 1234852.7794 | 2707292.1185 | 1234842.6504 | 2707292.7422 | 1234832.8542 | 2707293.0282 | 1234827.4621
118 | 2707291.0591 | 1234858.5435 | 2707296.7019 | 1234856.7218 | 2707299.0369 | 1234859.0546 | 2707305.3063 | 1234861.9367 | 2707326.18 | 1234852.9598
119 | 2707293.0282 | 1234827.4621 | 2707293.6838 | 1234815.102 | 2707294.2011 | 1234807.0275
120 | 2707297.0598 | 1234754.2938 | 2707297.7551 | 1234743.1314 | 2707298.5918 | 1234726.3111
121 | 2707297.0598 | 1234754.2938 | 2707296.9209 | 1234756.5247
122 | 2707298.5918 | 1234726.3111 | 2707298.8134 | 1234721.8564 | 2707299.6697 | 1234704.614
123 | 2707296.9209 | 1234756.5247 | 2707296.8819 | 1234757.1507
124 | 2707299.7333 | 1234703.3322 | 2707299.6697 | 1234704.614
125 | 2707296.0594 | 1234770.355 | 2707296.8819 | 1234757.1507
126 | 2707300.8932 | 1234680.1541 | 2707300.8441 | 1234681.1174 | 2707300.3918 | 1234690.2273 | 2707300.192 | 1234694.16 | 2707299.7535 | 1234702.9255 | 2707299.7333 | 1234703.3322
127 | 2707296.0594 | 1234770.355 | 2707295.4734 | 1234787.3745
128 | 2707292.5452 | 1234770.0135 | 2707296.0594 | 1234770.355
129 | 2707295.4734 | 1234787.3745 | 2707295.4541 | 1234787.9353 | 2707295.0756 | 1234793.3771 | 2707294.2011 | 1234807.0275
130 | 2707292.5452 | 1234770.0135 | 2707291.7016 | 1234783.5831
131 | 2707496.3947 | 1234646.2247 | 2707495.7691 | 1234632.2693 | 2707493.8164 | 1234622.6155 | 2707489.9491 | 1234623.7909
132 | 2707496.3947 | 1234646.2247 | 2707499.1021 | 1234642.6265 | 2707500.8548 | 1234624.4331 | 2707495.2943 | 1234613.6522
133 | 2707493.4967 | 1234610.1668 | 2707495.2943 | 1234613.6522
134 | 2707296.5419 | 1234678.7156 | 2707276.9339 | 1234690.8376 | 2707272.1384 | 1234696.0439 | 2707264.2668 | 1234698.0256 | 2707260.2014 | 1234699.0474
135 | 2707296.5419 | 1234678.7156 | 2707297.9737 | 1234681.1767 | 2707297.0002 | 1234693.9912 | 2707296.5261 | 1234706.1563
136 | 2707296.5261 | 1234706.1563 | 2707295.8517 | 1234723.4613
137 | 2707411.8438 | 1234643.6717 | 2707418.2105 | 1234653.103
138 | 2707411.8438 | 1234643.6717 | 2707420.9505 | 1234633.3671
139 | 2707411.8438 | 1234643.6717 | 2707403.5165 | 1234632.9577
140 | 2707420.9505 | 1234633.3671 | 2707425.6196 | 1234628.0838
141 | 2707391.586 | 1234617.6078 | 2707403.5165 | 1234632.9577
142 | 2707430.3351 | 1234622.7271 | 2707427.0778 | 1234626.4338 | 2707425.6196 | 1234628.0838
143 | 2707391.586 | 1234617.6078 | 2707388.6266 | 1234613.7958 | 2707381.8545 | 1234619.2295
144 | 2707391.586 | 1234617.6078 | 2707400.8745 | 1234606.5556
145 | 2707432.1565 | 1234620.6545 | 2707430.3351 | 1234622.7271
146 | 2707405.3341 | 1234601.2494 | 2707400.8745 | 1234606.5556
147 | 2707493.4967 | 1234610.1668 | 2707493.713 | 1234603.6546 | 2707490.8842 | 1234591.7943 | 2707486.9628 | 1234589.2659
148 | 2707493.4967 | 1234610.1668 | 2707488.494 | 1234609.6537
149 | 2707409.944 | 1234595.7642 | 2707405.3341 | 1234601.2494
150 | 2707411.626 | 1234593.7628 | 2707409.944 | 1234595.7642

## bus_geodata
| x | y | coords
0 | 2707564.546 | 1234754.8994
1 | 2707541.5656 | 1234764.0983
2 | 2707509.9911 | 1234776.7375
3 | 2707579.382 | 1234723.3857
4 | 2707590.0506 | 1234702.0597
5 | 2707547.3192 | 1234719.6469
6 | 2707634.018 | 1234738.1136
7 | 2707493.1148 | 1234771.0146
8 | 2707602.7673 | 1234676.6398
9 | 2707664.871 | 1234749.2983
10 | 2707489.7497 | 1234768.7991
11 | 2707472.9443 | 1234791.1138
12 | 2707467.8286 | 1234793.099
13 | 2707624.9131 | 1234687.8665
14 | 2707567.9892 | 1234662.2992
15 | 2707680.8671 | 1234732.4821
16 | 2707348.7512 | 1234638.0339
17 | 2707352.3582 | 1234642.8962
18 | 2707324.9013 | 1234605.883
19 | 2707311.2749 | 1234601.2
20 | 2707327.9918 | 1234601.9253
21 | 2707365.9043 | 1234661.0143
22 | 2707363.4095 | 1234634.029
23 | 2707297.5254 | 1234616.2455
24 | 2707375.7616 | 1234674.1986
25 | 2707368.8749 | 1234629.6438
26 | 2707292.1119 | 1234642.3188
27 | 2707278.5881 | 1234644.5319
28 | 2707295.4801 | 1234618.4836
29 | 2707299.4882 | 1234657.2746
30 | 2707385.5462 | 1234663.2842
31 | 2707385.7884 | 1234687.6114
32 | 2707374.3412 | 1234625.2578
33 | 2707394.5364 | 1234824.9026
34 | 2707402.5196 | 1234821.0134
35 | 2707386.7261 | 1234828.3936
36 | 2707408.9899 | 1234819.0214
37 | 2707380.1777 | 1234831.2505
38 | 2707418.9607 | 1234817.3336
39 | 2707376.2215 | 1234832.9765
40 | 2707443.2732 | 1234799.5929
41 | 2707445.0374 | 1234779.0106
42 | 2707437.6845 | 1234799.2582
43 | 2707346.5461 | 1234844.2012
44 | 2707327.1566 | 1234852.5398
45 | 2707347.0627 | 1234844.0454
46 | 2707420.7076 | 1234812.3818
47 | 2707374.4594 | 1234833.7452
48 | 2707356.3025 | 1234841.2576
49 | 2707352.7202 | 1234842.3385
50 | 2707390.2745 | 1234658.0099
51 | 2707386.6406 | 1234688.7513
52 | 2707391.555 | 1234656.5816
53 | 2707394.6654 | 1234699.4861
54 | 2707553.6844 | 1234665.4713
55 | 2707533.0706 | 1234663.6461
56 | 2707571.1933 | 1234653.8507
57 | 2707562.7886 | 1234639.2763
58 | 2707531.8632 | 1234619.0787
59 | 2707525.0692 | 1234662.9357
60 | 2707614.5123 | 1234650.1766
61 | 2707572.8848 | 1234621.856
62 | 2707530.4606 | 1234615.4618
63 | 2707521.1127 | 1234662.5844
64 | 2707615.5505 | 1234626.3104
65 | 2707604.4551 | 1234647.0032
66 | 2707573.1303 | 1234619.2259
67 | 2707524.1076 | 1234614.6796
68 | 2707530.3649 | 1234597.7465
69 | 2707523.1123 | 1234644.9738
70 | 2707506.6163 | 1234661.0167
71 | 2707404.5927 | 1234712.7657
72 | 2707406.9138 | 1234715.8706
73 | 2707397.438 | 1234703.1949
74 | 2707410.563 | 1234720.7521
75 | 2707416.4293 | 1234716.1999
76 | 2707422.4219 | 1234735.4965
77 | 2707419.4803 | 1234705.7462
78 | 2707431.0201 | 1234746.1867
79 | 2707433.1264 | 1234748.8056
80 | 2707442.3986 | 1234764.7341
81 | 2707442.8187 | 1234766.9707
82 | 2707422.7975 | 1234694.3864
83 | 2707439.5439 | 1234710.0435
84 | 2707443.4493 | 1234770.3927
85 | 2707493.8727 | 1234698.8186
86 | 2707495.4755 | 1234703.1238
87 | 2707486.4141 | 1234678.7847
88 | 2707479.6106 | 1234732.1792
89 | 2707482.2153 | 1234667.5068
90 | 2707470.8203 | 1234740.4675
91 | 2707479.7118 | 1234660.7847
92 | 2707494.9309 | 1234659.753
93 | 2707456.8833 | 1234756.1945
94 | 2707470.8829 | 1234637.0779
95 | 2707495.8483 | 1234651.2746
96 | 2707477.8202 | 1234760.9451
97 | 2707445.5421 | 1234686.8087
98 | 2707449.0811 | 1234712.0862
99 | 2707427.548 | 1234671.5881
100 | 2707444.3101 | 1234659.1536
101 | 2707421.9891 | 1234658.7006
102 | 2707448.3836 | 1234684.8137
103 | 2707291.0591 | 1234858.5435
104 | 2707293.0282 | 1234827.4621
105 | 2707326.18 | 1234852.9598
106 | 2707297.0598 | 1234754.2938
107 | 2707298.5918 | 1234726.3111
108 | 2707296.9209 | 1234756.5247
109 | 2707299.6697 | 1234704.614
110 | 2707296.8819 | 1234757.1507
111 | 2707299.7333 | 1234703.3322
112 | 2707296.0594 | 1234770.355
113 | 2707300.8932 | 1234680.1541
114 | 2707295.4734 | 1234787.3745
115 | 2707292.5452 | 1234770.0135
116 | 2707650.3792 | 1234638.8542
117 | 2707609.0496 | 1234625.3364
118 | 2707615.6943 | 1234613.7812
119 | 2707452.6853 | 1234759.411
120 | 2707496.3947 | 1234646.2247
121 | 2707518.903 | 1234644.5528
122 | 2707520.6872 | 1234628.3838
123 | 2707489.9491 | 1234623.7909
124 | 2707495.2943 | 1234613.6522
125 | 2707296.5418 | 1234678.7156
126 | 2707260.2014 | 1234699.0474
127 | 2707296.5261 | 1234706.1563
128 | 2707418.2105 | 1234653.103
129 | 2707411.8438 | 1234643.6717
130 | 2707420.9505 | 1234633.3671
131 | 2707403.5165 | 1234632.9577
132 | 2707425.6196 | 1234628.0838
133 | 2707391.586 | 1234617.6078
134 | 2707447.6535 | 1234656.6735
135 | 2707430.3351 | 1234622.7271
136 | 2707381.8545 | 1234619.2295
137 | 2707400.8745 | 1234606.5556
138 | 2707448.7771 | 1234684.5374
139 | 2707294.2011 | 1234807.0275
140 | 2707291.7016 | 1234783.5831
141 | 2707295.8517 | 1234723.4613
142 | 2707567.0676 | 1234618.7157
143 | 2707572.7624 | 1234606.5206
144 | 2707493.4967 | 1234610.1668
145 | 2707486.9628 | 1234589.2659
146 | 2707488.494 | 1234609.6537
147 | 2707468.7067 | 1234631.2346
148 | 2707432.1565 | 1234620.6545
149 | 2707409.944 | 1234595.7642
150 | 2707405.3341 | 1234601.2494
151 | 2707411.626 | 1234593.7628
152 | 2707422.7975 | 1234694.3864

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98804 | -0.2278 | 0.0019838 | 0.0004972
1 | 0.98808 | -0.22693 | 0.0043939 | 0.0011012
2 | 0.98828 | -0.22305 | 0 | 0
3 | 0.97196 | -0.54082 | 0 | 0
4 | 0.97218 | -0.53651 | 0.0035738 | 0.00089568
5 | 0.97179 | -0.54426 | 0.0049657 | 0.0012445
6 | 0.97171 | -0.54587 | 0.0036185 | 0.00090688
7 | 0.98839 | -0.22099 | 0.0025733 | 0.00064492
8 | 0.97254 | -0.5295 | 0 | 0
9 | 0.97167 | -0.54667 | 0 | 0
10 | 0.98842 | -0.22035 | 0.0025095 | 0.00062893
11 | 0.98738 | -0.24037 | 0.0013824 | 0.00034647
12 | 0.98738 | -0.24024 | 0.0014319 | 0.00035888
13 | 0.9725 | -0.53018 | 0.001488 | 0.00037293
14 | 0.97306 | -0.51922 | 0 | 0
15 | 0.97164 | -0.54719 | 0.0012146 | 0.0003044
16 | 0.99102 | -0.17131 | 0.0047291 | 0.0011852
17 | 0.99105 | -0.1708 | 0 | 0
18 | 0.97192 | -0.54191 | 0 | 0
19 | 0.97196 | -0.54118 | 0 | 0
20 | 0.97191 | -0.54217 | 0.0023155 | 0.00058032
21 | 0.99164 | -0.15935 | 0.004869 | 0.0012203
22 | 0.99074 | -0.17678 | 0.00089335 | 0.00022389
23 | 0.972 | -0.5403 | 0.0013178 | 0.00033027
24 | 0.99214 | -0.14961 | 0 | 0
25 | 0.99059 | -0.17963 | 0.00088546 | 0.00022192
26 | 0.97211 | -0.5381 | 0 | 0
27 | 0.97193 | -0.54162 | 0.013965 | 0.0034999
28 | 0.97201 | -0.5401 | 0 | 0
29 | 0.97245 | -0.5314 | 0 | 0
30 | 0.9921 | -0.1503 | 0.00089336 | 0.0002239
31 | 0.99269 | -0.13892 | 0.0015742 | 0.00039453
32 | 0.99045 | -0.18237 | 0.00093565 | 0.0002345
33 | 0.98379 | -0.30957 | 0.001494 | 0.00037444
34 | 0.98428 | -0.30005 | 0.0044693 | 0.0011201
35 | 0.98333 | -0.31853 | 0.00148 | 0.00037093
36 | 0.98469 | -0.29223 | 0 | 0
37 | 0.98295 | -0.32582 | 0.00099168 | 0.00024854
38 | 0.98529 | -0.28062 | 0 | 0
39 | 0.98273 | -0.33015 | 0.0011362 | 0.00028477
40 | 0.98745 | -0.23895 | 0 | 0
41 | 0.98889 | -0.21117 | 0.0017357 | 0.00043501
42 | 0.98707 | -0.24617 | 0 | 0
43 | 0.98118 | -0.36037 | 0 | 0
44 | 0.98022 | -0.37903 | 0.0011788 | 0.00029543
45 | 0.9812 | -0.35989 | 0.00085528 | 0.00021435
46 | 0.98563 | -0.27406 | 0.0083041 | 0.0020812
47 | 0.98263 | -0.33204 | 0.00095757 | 0.00023999
48 | 0.98165 | -0.35107 | 0.0015644 | 0.00039208
49 | 0.98147 | -0.35458 | 0.0023139 | 0.00057991
50 | 0.99209 | -0.15053 | 0.00087762 | 0.00021995
51 | 0.99274 | -0.13797 | 0.0013393 | 0.00033567
52 | 0.99209 | -0.15056 | 0.00090051 | 0.00022569
53 | 0.99322 | -0.12874 | 0.0017699 | 0.00044359
54 | 0.97391 | -0.50238 | 0.0044468 | 0.0011145
55 | 0.97506 | -0.47978 | 0 | 0
56 | 0.97277 | -0.5249 | 0 | 0
57 | 0.97289 | -0.52245 | 0.0060685 | 0.0015209
58 | 0.97427 | -0.49525 | 0.0036898 | 0.00092475
59 | 0.97564 | -0.46831 | 0.0057687 | 0.0014458
60 | 0.97212 | -0.53781 | 0 | 0
61 | 0.97218 | -0.53654 | 0.0036909 | 0.00092504
62 | 0.97422 | -0.4963 | 0 | 0
63 | 0.97595 | -0.46222 | 0 | 0
64 | 0.97192 | -0.54164 | 0 | 0
65 | 0.97206 | -0.53899 | 0.0060722 | 0.0015218
66 | 0.97214 | -0.53732 | 0 | 0
67 | 0.97416 | -0.49747 | 0.0099157 | 0.0024851
68 | 0.97414 | -0.49794 | 0.0048328 | 0.0012112
69 | 0.97577 | -0.46573 | 0 | 0
70 | 0.97724 | -0.43704 | 0.0061038 | 0.0015298
71 | 0.99386 | -0.11639 | 0.0049826 | 0.0012488
72 | 0.99403 | -0.11313 | 0.0010023 | 0.00025121
73 | 0.99339 | -0.1254 | 0.0019498 | 0.00048868
74 | 0.9943 | -0.1079 | 0 | 0
75 | 0.99503 | -0.094094 | 0.0017075 | 0.00042795
76 | 0.99276 | -0.13719 | 0.006315 | 0.0015827
77 | 0.99608 | -0.074089 | 0 | 0
78 | 0.99167 | -0.15797 | 0.004855 | 0.0012168
79 | 0.99141 | -0.16297 | 0.0016455 | 0.0004124
80 | 0.98994 | -0.19098 | 0.0029737 | 0.00074527
81 | 0.98977 | -0.19431 | 0 | 0
82 | 0.99724 | -0.052167 | 0 | 0
83 | 0.99602 | -0.075292 | 0.0016686 | 0.0004182
84 | 0.98952 | -0.19916 | 0.0013318 | 0.00033379
85 | 0.9843 | -0.29952 | 0.0033842 | 0.00084816
86 | 0.9849 | -0.28797 | 0.0060514 | 0.0015166
87 | 0.98159 | -0.35213 | 0.0029644 | 0.00074295
88 | 0.9873 | -0.24167 | 0.0014172 | 0.00035518
89 | 0.98009 | -0.38123 | 0 | 0
90 | 0.98785 | -0.23106 | 0.0051764 | 0.0012973
91 | 0.98005 | -0.3821 | 0.0023186 | 0.00058109
92 | 0.97834 | -0.41548 | 0 | 0
93 | 0.98885 | -0.212 | 0 | 0
94 | 0.97995 | -0.38411 | 0.0025526 | 0.00063973
95 | 0.97813 | -0.41955 | 0.0018068 | 0.00045282
96 | 0.98857 | -0.21742 | 0.0023287 | 0.00058364
97 | 0.99961 | -0.0073186 | 0.0016322 | 0.00040907
98 | 0.996 | -0.075578 | 0.0016684 | 0.00041814
99 | 0.98954 | -0.19993 | 0 | 0
100 | 0.98949 | -0.2009 | 0.0012732 | 0.0003191
101 | 0.98958 | -0.19925 | 0.0012891 | 0.00032307
102 | 0.99995 | -0.00089408 | 0.0017049 | 0.0004273
103 | 0.97868 | -0.40909 | 0 | 0
104 | 0.97748 | -0.43252 | 0.0010377 | 0.00026006
105 | 0.98017 | -0.37995 | 0.0063329 | 0.0015872
106 | 0.97487 | -0.48379 | 0.002156 | 0.00054035
107 | 0.97405 | -0.49992 | 0.0037915 | 0.00095024
108 | 0.97494 | -0.48242 | 0.0011255 | 0.00028207
109 | 0.97349 | -0.51093 | 0.0016288 | 0.00040823
110 | 0.97496 | -0.48202 | 0.0012199 | 0.00030574
111 | 0.97346 | -0.51154 | 0.00068877 | 0.00017262
112 | 0.9754 | -0.47332 | 0 | 0
113 | 0.97291 | -0.52233 | 0.0037788 | 0.00094706
114 | 0.976 | -0.46148 | 0.00069439 | 0.00017403
115 | 0.97539 | -0.47346 | 0 | 0
116 | 0.97176 | -0.54487 | 0.0047306 | 0.0011856
117 | 0.97191 | -0.54192 | 0.0023209 | 0.00058167
118 | 0.97191 | -0.54196 | 0.0013786 | 0.0003455
119 | 0.98912 | -0.20678 | 0.0026754 | 0.00067051
120 | 0.97802 | -0.4218 | 0 | 0
121 | 0.97575 | -0.46617 | 0.0057578 | 0.001443
122 | 0.97568 | -0.46761 | 0.0050414 | 0.0012635
123 | 0.97789 | -0.42426 | 0.0048367 | 0.0012122
124 | 0.97738 | -0.43423 | 0.0030612 | 0.00076721
125 | 0.97236 | -0.53316 | 0 | 0
126 | 0.97231 | -0.53418 | 0.0013062 | 0.00032737
127 | 0.9723 | -0.53448 | 0.0014206 | 0.00035604
128 | 0.9896 | -0.19878 | 0.0019058 | 0.00047765
129 | 0.98966 | -0.19761 | 0 | 0
130 | 0.9896 | -0.19892 | 0.0012871 | 0.00032257
131 | 0.9898 | -0.19492 | 0.0011094 | 0.00027803
132 | 0.98957 | -0.19943 | 0.0012902 | 0.00032335
133 | 0.99002 | -0.19067 | 0 | 0
134 | 0.98949 | -0.201 | 0.0013284 | 0.00033294
135 | 0.98955 | -0.19979 | 0.0012796 | 0.0003207
136 | 0.99026 | -0.18598 | 0.0015514 | 0.00038882
137 | 0.98992 | -0.19254 | 0.00098837 | 0.00024771
138 | 1 | 0 | -0.32738 | -0.083844
139 | 0.97671 | -0.44756 | 0.0015656 | 0.00039237
140 | 0.97536 | -0.47399 | 0.0021183 | 0.00053089
141 | 0.97228 | -0.53484 | 0.0011362 | 0.00028475
142 | 0.97209 | -0.53843 | 0.0099815 | 0.0025016
143 | 0.97207 | -0.53875 | 0.0059295 | 0.0014861
144 | 0.97732 | -0.43541 | 0 | 0
145 | 0.97713 | -0.43919 | 0.0088711 | 0.0022233
146 | 0.97729 | -0.4361 | 0.0075899 | 0.0019022
147 | 0.97993 | -0.38431 | 0.0018174 | 0.00045549
148 | 0.98955 | -0.19986 | 0.0015014 | 0.00037628
149 | 0.98985 | -0.19399 | 0.002519 | 0.00063133
150 | 0.98988 | -0.19331 | 0.00095215 | 0.00023863
151 | 0.98984 | -0.19412 | 0.0028031 | 0.00070252
152 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0019838 | -0.0004972 | 0.0019839 | 0.00049693 | 8.2857e-08 | -2.6401e-07 | 0.0029877 | 0.0029876 | 0.0029877 | 0.98804 | -0.2278 | 0.98808 | -0.22693 | 0.82081
1 | -0.0063778 | -0.0015982 | 0.006379 | 0.0015985 | 1.1765e-06 | 3.1727e-07 | 0.0096047 | 0.0096046 | 0.0096047 | 0.98808 | -0.22693 | 0.98828 | -0.22305 | 2.6387
2 | -0.006379 | -0.0015985 | 0.0063796 | 0.0015986 | 6.2708e-07 | 1.6903e-07 | 0.0096046 | 0.0096045 | 0.0096046 | 0.98828 | -0.22305 | 0.98839 | -0.22099 | 2.6386
3 | -0.0098008 | -0.0024552 | 0.0098028 | 0.0024562 | 2.013e-06 | 9.9274e-07 | 0.015004 | 0.015004 | 0.015004 | 0.97196 | -0.54082 | 0.97218 | -0.53651 | 4.122
4 | 0.0049665 | 0.0012446 | -0.0049657 | -0.0012445 | 8.1437e-07 | 5.5713e-08 | 0.0076033 | 0.0076035 | 0.0076035 | 0.97196 | -0.54082 | 0.97179 | -0.54426 | 2.0889
5 | 0.0048343 | 0.0012106 | -0.0048332 | -0.0012106 | 1.1623e-06 | 4.2698e-08 | 0.0074007 | 0.0074009 | 0.0074009 | 0.97196 | -0.54082 | 0.97171 | -0.54587 | 2.0332
6 | -0.013377 | -0.0033519 | 0.013381 | 0.0033544 | 4.4679e-06 | 2.5069e-06 | 0.020474 | 0.020474 | 0.020474 | 0.97218 | -0.53651 | 0.97254 | -0.5295 | 5.6247
7 | 0.0012147 | 0.00030372 | -0.0012146 | -0.00030413 | 4.6125e-08 | -4.1093e-07 | 0.0018598 | 0.00186 | 0.00186 | 0.97171 | -0.54587 | 0.97167 | -0.54667 | 0.51098
8 | -0.0089529 | -0.0022436 | 0.0089532 | 0.0022437 | 2.7447e-07 | 1.2403e-07 | 0.013479 | 0.013479 | 0.013479 | 0.98839 | -0.22099 | 0.98842 | -0.22035 | 3.7029
9 | 0.0014881 | 0.00037265 | -0.001488 | -0.00037293 | 4.8263e-08 | -2.7719e-07 | 0.0022767 | 0.0022768 | 0.0022768 | 0.97254 | -0.5295 | 0.9725 | -0.53018 | 0.62549
10 | -0.014869 | -0.0037271 | 0.014876 | 0.0037312 | 7.2831e-06 | 4.1953e-06 | 0.02275 | 0.02275 | 0.02275 | 0.97254 | -0.5295 | 0.97306 | -0.51922 | 6.2501
11 | 0.0012146 | 0.00030413 | -0.0012146 | -0.0003044 | 3.011e-08 | -2.682e-07 | 0.00186 | 0.0018601 | 0.0018601 | 0.97167 | -0.54667 | 0.97164 | -0.54719 | 0.511
12 | -0.011463 | -0.0028726 | 0.011464 | 0.0028735 | 1.5949e-06 | 8.3767e-07 | 0.017256 | 0.017256 | 0.017256 | 0.98842 | -0.22035 | 0.98857 | -0.21742 | 4.7408
13 | -0.0013824 | -0.00034647 | 0.0013824 | 0.00034641 | 8.9317e-09 | -6.4469e-08 | 0.0020834 | 0.0020834 | 0.0020834 | 0.98738 | -0.24037 | 0.98738 | -0.24024 | 0.57236
14 | -0.0028144 | -0.00070528 | 0.0028145 | 0.00070506 | 1.7291e-07 | -2.1721e-07 | 0.0042413 | 0.0042412 | 0.0042413 | 0.98738 | -0.24024 | 0.98745 | -0.23895 | 1.1652
15 | 0.034137 | 0.0085661 | -0.034128 | -0.0085603 | 9.2336e-06 | 5.7973e-06 | 0.052207 | 0.052207 | 0.052207 | 0.97306 | -0.51922 | 0.97277 | -0.5249 | 14.3427
16 | 0.0060694 | 0.0015211 | -0.0060685 | -0.0015209 | 9.3268e-07 | 2.3834e-07 | 0.0092814 | 0.0092816 | 0.0092816 | 0.97306 | -0.51922 | 0.97289 | -0.52245 | 2.5499
17 | -0.055083 | -0.013818 | 0.055127 | 0.013847 | 4.4272e-05 | 2.8127e-05 | 0.084239 | 0.084239 | 0.084239 | 0.97306 | -0.51922 | 0.97391 | -0.50238 | 23.1426
18 | -0.0047291 | -0.0011852 | 0.0047292 | 0.0011852 | 1.1447e-07 | -4.7483e-09 | 0.0071007 | 0.0071007 | 0.0071007 | 0.99102 | -0.17131 | 0.99105 | -0.1708 | 1.9507
19 | -0.028549 | -0.0071628 | 0.028564 | 0.0071725 | 1.5589e-05 | 9.6853e-06 | 0.042867 | 0.042867 | 0.042867 | 0.99105 | -0.1708 | 0.99164 | -0.15935 | 11.7768
20 | 0.023819 | 0.0059776 | -0.023813 | -0.0059734 | 6.7972e-06 | 4.1677e-06 | 0.035767 | 0.035767 | 0.035767 | 0.99105 | -0.1708 | 0.99074 | -0.17678 | 9.8261
21 | -0.0023155 | -0.00058026 | 0.0023156 | 0.0005801 | 8.1538e-08 | -1.6224e-07 | 0.003545 | 0.003545 | 0.003545 | 0.97192 | -0.54191 | 0.97196 | -0.54118 | 0.97391
22 | 0.0023155 | 0.00058026 | -0.0023155 | -0.00058032 | 2.8238e-08 | -5.6182e-08 | 0.003545 | 0.0035451 | 0.0035451 | 0.97192 | -0.54191 | 0.97191 | -0.54217 | 0.97392
23 | -0.0023156 | -0.0005801 | 0.0023157 | 0.00057991 | 9.6048e-08 | -1.9115e-07 | 0.003545 | 0.0035449 | 0.003545 | 0.97196 | -0.54118 | 0.972 | -0.5403 | 0.97389
24 | -0.033433 | -0.0083927 | 0.033449 | 0.0084025 | 1.554e-05 | 9.7333e-06 | 0.050174 | 0.050174 | 0.050174 | 0.99164 | -0.15935 | 0.99214 | -0.14961 | 13.784
25 | 0.022919 | 0.0057495 | -0.022916 | -0.0057476 | 3.114e-06 | 1.9028e-06 | 0.034425 | 0.034425 | 0.034425 | 0.99074 | -0.17678 | 0.99059 | -0.17963 | 9.4575
26 | -0.0036335 | -0.00091017 | 0.0036335 | 0.00091016 | 3.5175e-08 | -1.5068e-08 | 0.0055622 | 0.0055622 | 0.0055622 | 0.972 | -0.5403 | 0.97201 | -0.5401 | 1.5281
27 | 0.0026716 | 0.0006693 | -0.0026715 | -0.00066943 | 8.8249e-08 | -1.3281e-07 | 0.0040068 | 0.0040068 | 0.0040068 | 0.99214 | -0.14961 | 0.9921 | -0.1503 | 1.1008
28 | -0.03612 | -0.0090718 | 0.036139 | 0.0090834 | 1.8435e-05 | 1.1582e-05 | 0.05418 | 0.05418 | 0.05418 | 0.99214 | -0.14961 | 0.99269 | -0.13892 | 14.8847
29 | 0.022031 | 0.0055257 | -0.022028 | -0.0055239 | 2.8786e-06 | 1.7521e-06 | 0.033095 | 0.033095 | 0.033095 | 0.99059 | -0.17963 | 0.99045 | -0.18237 | 9.0921
30 | 0.013967 | 0.0035013 | -0.013965 | -0.0034999 | 2.3424e-06 | 1.3297e-06 | 0.02138 | 0.02138 | 0.02138 | 0.97211 | -0.5381 | 0.97193 | -0.54162 | 5.8736
31 | 0.0036339 | 0.00091001 | -0.0036335 | -0.00091016 | 3.4565e-07 | -1.4812e-07 | 0.0055621 | 0.0055622 | 0.0055622 | 0.97211 | -0.5381 | 0.97201 | -0.5401 | 1.5281
32 | -0.017601 | -0.0044113 | 0.017607 | 0.0044146 | 5.6245e-06 | 3.3434e-06 | 0.026942 | 0.026942 | 0.026942 | 0.97211 | -0.5381 | 0.97245 | -0.5314 | 7.4016
33 | 0.0038636 | 0.00096713 | -0.0038633 | -0.00096723 | 3.245e-07 | -9.9494e-08 | 0.0059115 | 0.0059116 | 0.0059116 | 0.97245 | -0.5314 | 0.97236 | -0.53316 | 1.6241
34 | -0.02147 | -0.0053817 | 0.02148 | 0.0053874 | 9.2844e-06 | 5.6573e-06 | 0.032853 | 0.032853 | 0.032853 | 0.97245 | -0.5314 | 0.97291 | -0.52233 | 9.0257
35 | 0.0017781 | 0.00044554 | -0.0017781 | -0.00044562 | 1.8893e-08 | -7.9375e-08 | 0.0026669 | 0.002667 | 0.002667 | 0.9921 | -0.1503 | 0.99209 | -0.15053 | 0.73268
36 | -0.037713 | -0.0094779 | 0.037715 | 0.009479 | 1.7062e-06 | 1.0735e-06 | 0.05654 | 0.05654 | 0.05654 | 0.99269 | -0.13892 | 0.99274 | -0.13797 | 15.533
37 | 0.021092 | 0.0052894 | -0.021089 | -0.0052872 | 3.6275e-06 | 2.1977e-06 | 0.031689 | 0.031689 | 0.031689 | 0.99045 | -0.18237 | 0.99026 | -0.18598 | 8.7059
38 | -0.06002 | -0.015211 | 0.060048 | 0.015228 | 2.7481e-05 | 1.7475e-05 | 0.090843 | 0.090843 | 0.090843 | 0.98379 | -0.30957 | 0.98428 | -0.30005 | 24.9568
39 | 0.058526 | 0.014836 | -0.058501 | -0.01482 | 2.5178e-05 | 1.6005e-05 | 0.088583 | 0.088583 | 0.088583 | 0.98379 | -0.30957 | 0.98333 | -0.31853 | 24.336
40 | -0.064517 | -0.016348 | 0.064541 | 0.016364 | 2.4249e-05 | 1.5433e-05 | 0.097599 | 0.097599 | 0.097599 | 0.98428 | -0.30005 | 0.98469 | -0.29223 | 26.813
41 | 0.057021 | 0.014449 | -0.057001 | -0.014436 | 1.9974e-05 | 1.2693e-05 | 0.086343 | 0.086343 | 0.086343 | 0.98333 | -0.31853 | 0.98295 | -0.32582 | 23.7207
42 | -0.064541 | -0.016364 | 0.064577 | 0.016386 | 3.6021e-05 | 2.2925e-05 | 0.097599 | 0.097599 | 0.097599 | 0.98469 | -0.29223 | 0.98529 | -0.28062 | 26.813
43 | 0.056009 | 0.014188 | -0.055998 | -0.014181 | 1.1651e-05 | 7.4021e-06 | 0.084842 | 0.084842 | 0.084842 | 0.98295 | -0.32582 | 0.98273 | -0.33015 | 23.3083
44 | -0.064577 | -0.016386 | 0.064598 | 0.016399 | 2.039e-05 | 1.2977e-05 | 0.097599 | 0.097599 | 0.097599 | 0.98529 | -0.28062 | 0.98563 | -0.27406 | 26.813
45 | 0.054862 | 0.013896 | -0.054857 | -0.013893 | 4.9809e-06 | 3.1634e-06 | 0.083122 | 0.083122 | 0.083122 | 0.98273 | -0.33015 | 0.98263 | -0.33204 | 22.8357
46 | -0.07584 | -0.019264 | 0.075941 | 0.019329 | 0.00010157 | 6.4739e-05 | 0.11438 | 0.11438 | 0.11438 | 0.98745 | -0.23895 | 0.98889 | -0.21117 | 31.4223
47 | 0.073025 | 0.018559 | -0.073 | -0.018543 | 2.5391e-05 | 1.6179e-05 | 0.11014 | 0.11014 | 0.11014 | 0.98745 | -0.23895 | 0.98707 | -0.24617 | 30.2571
48 | -0.077677 | -0.019764 | 0.077722 | 0.019793 | 4.4975e-05 | 2.8672e-05 | 0.11699 | 0.11699 | 0.11699 | 0.98889 | -0.21117 | 0.98952 | -0.19916 | 32.1397
49 | 0.073 | 0.018543 | -0.072902 | -0.018481 | 9.7853e-05 | 6.2351e-05 | 0.11014 | 0.11014 | 0.11014 | 0.98707 | -0.24617 | 0.98563 | -0.27406 | 30.2571
50 | 0.049094 | 0.012421 | -0.04905 | -0.012393 | 4.3924e-05 | 2.7845e-05 | 0.074495 | 0.074496 | 0.074496 | 0.98118 | -0.36037 | 0.98022 | -0.37903 | 20.4658
51 | -0.049094 | -0.012421 | 0.049095 | 0.012421 | 1.1231e-06 | 7.1198e-07 | 0.074495 | 0.074495 | 0.074495 | 0.98118 | -0.36037 | 0.9812 | -0.35989 | 20.4658
52 | 0.047871 | 0.012097 | -0.047869 | -0.012096 | 2.1073e-06 | 1.3353e-06 | 0.072706 | 0.072706 | 0.072706 | 0.98022 | -0.37903 | 0.98017 | -0.37995 | 19.9742
53 | -0.04995 | -0.012636 | 0.049963 | 0.012644 | 1.273e-05 | 8.0724e-06 | 0.075793 | 0.075792 | 0.075793 | 0.9812 | -0.35989 | 0.98147 | -0.35458 | 20.8221
54 | 0.053899 | 0.013653 | -0.05385 | -0.013621 | 4.9197e-05 | 3.1237e-05 | 0.081672 | 0.081672 | 0.081672 | 0.98263 | -0.33204 | 0.98165 | -0.35107 | 22.4373
55 | 0.052285 | 0.013229 | -0.052277 | -0.013224 | 8.8241e-06 | 5.6001e-06 | 0.079301 | 0.079301 | 0.079301 | 0.98165 | -0.35107 | 0.98147 | -0.35458 | 21.7859
56 | 0.00090051 | 0.00022566 | -0.00090051 | -0.00022569 | 1.3123e-09 | -2.393e-08 | 0.0013506 | 0.0013507 | 0.0013507 | 0.99209 | -0.15053 | 0.99209 | -0.15056 | 0.37106
57 | -0.039054 | -0.0098146 | 0.039071 | 0.0098255 | 1.7228e-05 | 1.0853e-05 | 0.058547 | 0.058547 | 0.058547 | 0.99274 | -0.13797 | 0.99322 | -0.12874 | 16.0845
58 | -0.040841 | -0.010269 | 0.040848 | 0.010273 | 6.5036e-06 | 4.1024e-06 | 0.061199 | 0.061199 | 0.061199 | 0.99322 | -0.12874 | 0.99339 | -0.1254 | 16.8129
59 | -0.059574 | -0.014961 | 0.059639 | 0.015002 | 6.4311e-05 | 4.0901e-05 | 0.091033 | 0.091033 | 0.091033 | 0.97391 | -0.50238 | 0.97506 | -0.47978 | 25.0091
60 | 0.018454 | 0.0046299 | -0.01844 | -0.0046218 | 1.3602e-05 | 8.1352e-06 | 0.028163 | 0.028164 | 0.028164 | 0.97506 | -0.47978 | 0.97427 | -0.49525 | 7.7373
61 | -0.078092 | -0.019632 | 0.078135 | 0.019659 | 4.2799e-05 | 2.7291e-05 | 0.1192 | 0.1192 | 0.1192 | 0.97506 | -0.47978 | 0.97564 | -0.46831 | 32.7463
62 | 0.014514 | 0.0036403 | -0.014505 | -0.0036352 | 8.9243e-06 | 5.1126e-06 | 0.022202 | 0.022203 | 0.022203 | 0.97277 | -0.5249 | 0.97212 | -0.53781 | 6.0996
63 | 0.019614 | 0.00492 | -0.019603 | -0.0049134 | 1.0882e-05 | 6.5644e-06 | 0.030005 | 0.030005 | 0.030005 | 0.97277 | -0.5249 | 0.97218 | -0.53654 | 8.2431
64 | 0.01475 | 0.003697 | -0.014749 | -0.0036966 | 7.3832e-07 | 4.2422e-07 | 0.022528 | 0.022528 | 0.022528 | 0.97427 | -0.49525 | 0.97422 | -0.4963 | 6.1891
65 | -0.083904 | -0.021105 | 0.083928 | 0.021121 | 2.4402e-05 | 1.5568e-05 | 0.12799 | 0.12799 | 0.12799 | 0.97564 | -0.46831 | 0.97595 | -0.46222 | 35.1634
66 | 0.0084323 | 0.0021132 | -0.0084308 | -0.0021126 | 1.5386e-06 | 6.7943e-07 | 0.012907 | 0.012907 | 0.012907 | 0.97212 | -0.53781 | 0.97192 | -0.54164 | 3.546
67 | 0.0060726 | 0.0015219 | -0.0060722 | -0.0015218 | 3.4196e-07 | 8.8015e-08 | 0.0092953 | 0.0092953 | 0.0092953 | 0.97212 | -0.53781 | 0.97206 | -0.53899 | 2.5537
68 | 0.015912 | 0.0039884 | -0.015912 | -0.003988 | 5.8761e-07 | 3.4332e-07 | 0.024356 | 0.024356 | 0.024356 | 0.97218 | -0.53654 | 0.97214 | -0.53732 | 6.6911
69 | 0.0099163 | 0.0024854 | -0.0099157 | -0.0024851 | 5.4902e-07 | 2.7191e-07 | 0.015146 | 0.015146 | 0.015146 | 0.97422 | -0.4963 | 0.97416 | -0.49747 | 4.161
70 | 0.0048332 | 0.0012112 | -0.0048328 | -0.0012112 | 3.774e-07 | 1.1611e-08 | 0.0073822 | 0.0073823 | 0.0073823 | 0.97422 | -0.4963 | 0.97414 | -0.49794 | 2.0281
71 | 0.010802 | 0.0027075 | -0.0108 | -0.0027066 | 1.803e-06 | 9.3243e-07 | 0.016469 | 0.016469 | 0.016469 | 0.97595 | -0.46222 | 0.97577 | -0.46573 | 4.5245
72 | -0.09473 | -0.023828 | 0.094844 | 0.023901 | 0.00011411 | 7.285e-05 | 0.14446 | 0.14446 | 0.14446 | 0.97595 | -0.46222 | 0.97724 | -0.43704 | 39.6878
73 | 0.0023209 | 0.00058161 | -0.0023209 | -0.00058167 | 3.1032e-08 | -6.1362e-08 | 0.0035533 | 0.0035534 | 0.0035534 | 0.97192 | -0.54164 | 0.97191 | -0.54192 | 0.9762
74 | 0.0013786 | 0.00034536 | -0.0013786 | -0.0003455 | 2.1167e-08 | -1.4348e-07 | 0.0021106 | 0.0021106 | 0.0021106 | 0.97192 | -0.54164 | 0.97191 | -0.54196 | 0.57984
75 | 0.0047313 | 0.0011856 | -0.0047306 | -0.0011856 | 7.2839e-07 | 7.4768e-09 | 0.0072435 | 0.0072437 | 0.0072437 | 0.97192 | -0.54164 | 0.97176 | -0.54487 | 1.99
76 | 0.009982 | 0.0025019 | -0.0099815 | -0.0025016 | 5.3104e-07 | 2.6466e-07 | 0.015279 | 0.015279 | 0.015279 | 0.97214 | -0.53732 | 0.97209 | -0.53843 | 4.1975
77 | 0.0059299 | 0.0014862 | -0.0059295 | -0.0014861 | 4.0453e-07 | 9.6568e-08 | 0.0090766 | 0.0090767 | 0.0090767 | 0.97214 | -0.53732 | 0.97207 | -0.53875 | 2.4936
78 | 0.0057579 | 0.0014431 | -0.0057578 | -0.001443 | 1.2195e-07 | 2.5361e-08 | 0.0087806 | 0.0087806 | 0.0087806 | 0.97577 | -0.46573 | 0.97575 | -0.46617 | 2.4122
79 | 0.0050419 | 0.0012635 | -0.0050414 | -0.0012635 | 4.5305e-07 | 3.4694e-08 | 0.0076886 | 0.0076887 | 0.0076887 | 0.97577 | -0.46573 | 0.97568 | -0.46761 | 2.1123
80 | -0.10095 | -0.025431 | 0.10105 | 0.025497 | 0.0001042 | 6.6541e-05 | 0.15376 | 0.15376 | 0.15376 | 0.97724 | -0.43704 | 0.97834 | -0.41548 | 42.2411
81 | -0.047799 | -0.012022 | 0.047806 | 0.012027 | 7.4484e-06 | 4.7167e-06 | 0.07158 | 0.07158 | 0.07158 | 0.99386 | -0.11639 | 0.99403 | -0.11313 | 19.6648
82 | 0.042816 | 0.010773 | -0.042798 | -0.010762 | 1.8423e-05 | 1.1636e-05 | 0.06412 | 0.06412 | 0.06412 | 0.99386 | -0.11639 | 0.99339 | -0.1254 | 17.6153
83 | -0.048808 | -0.012278 | 0.048821 | 0.012286 | 1.2206e-05 | 7.733e-06 | 0.07308 | 0.07308 | 0.07308 | 0.99403 | -0.11313 | 0.9943 | -0.1079 | 20.077
84 | -0.31568 | -0.080673 | 0.31589 | 0.080807 | 0.00021093 | 0.0001347 | 0.47298 | 0.47298 | 0.47298 | 0.9943 | -0.1079 | 0.99503 | -0.094094 | 43.313
85 | 0.26685 | 0.068387 | -0.26648 | -0.068146 | 0.00037824 | 0.00024134 | 0.3999 | 0.3999 | 0.3999 | 0.9943 | -0.1079 | 0.99276 | -0.13719 | 36.6207
86 | -0.31759 | -0.081235 | 0.3179 | 0.081432 | 0.00030781 | 0.00019658 | 0.47553 | 0.47553 | 0.47553 | 0.99503 | -0.094094 | 0.99608 | -0.074089 | 43.5468
87 | 0.26016 | 0.066563 | -0.2599 | -0.066396 | 0.00026141 | 0.00016677 | 0.39043 | 0.39043 | 0.39043 | 0.99276 | -0.13719 | 0.99167 | -0.15797 | 35.754
88 | -0.32124 | -0.082268 | 0.32158 | 0.082486 | 0.00034155 | 0.00021813 | 0.48052 | 0.48052 | 0.48052 | 0.99608 | -0.074089 | 0.99724 | -0.052167 | 44.0033
89 | 0.0033373 | 0.00083609 | -0.0033371 | -0.00083623 | 1.9124e-07 | -1.4467e-07 | 0.0049853 | 0.0049854 | 0.0049854 | 0.99608 | -0.074089 | 0.99602 | -0.075292 | 1.3696
90 | 0.25505 | 0.065179 | -0.25498 | -0.06514 | 6.1673e-05 | 3.934e-05 | 0.38315 | 0.38315 | 0.38315 | 0.99167 | -0.15797 | 0.99141 | -0.16297 | 35.0869
91 | 0.25334 | 0.064728 | -0.253 | -0.064509 | 0.00034264 | 0.00021856 | 0.38068 | 0.38068 | 0.38068 | 0.99141 | -0.16297 | 0.98994 | -0.19098 | 34.8607
92 | 0.25002 | 0.063764 | -0.24998 | -0.063738 | 4.0261e-05 | 2.5679e-05 | 0.37621 | 0.37621 | 0.37621 | 0.98994 | -0.19098 | 0.98977 | -0.19431 | 34.4514
93 | 0.079072 | 0.020138 | -0.079054 | -0.020126 | 1.8475e-05 | 1.1779e-05 | 0.11899 | 0.11899 | 0.11899 | 0.98977 | -0.19431 | 0.98952 | -0.19916 | 32.6899
94 | 0.17091 | 0.0436 | -0.17081 | -0.043535 | 0.0001028 | 6.531e-05 | 0.25722 | 0.25722 | 0.25722 | 0.98977 | -0.19431 | 0.98912 | -0.20678 | 23.5548
95 | -0.32158 | -0.082486 | 0.32228 | 0.082934 | 0.00070122 | 0.00044783 | 0.48052 | 0.48052 | 0.48052 | 0.99724 | -0.052167 | 0.99961 | -0.0073186 | 44.0033
96 | 0.0016684 | 0.00041803 | -0.0016684 | -0.00041814 | 2.2724e-08 | -1.124e-07 | 0.0024925 | 0.0024926 | 0.0024926 | 0.99602 | -0.075292 | 0.996 | -0.075578 | 0.68477
97 | -0.14102 | -0.035811 | 0.1411 | 0.035861 | 7.842e-05 | 5.013e-05 | 0.21336 | 0.21336 | 0.21336 | 0.9843 | -0.29952 | 0.9849 | -0.28797 | 58.6146
98 | 0.13764 | 0.034963 | -0.13729 | -0.03474 | 0.00034763 | 0.00022221 | 0.20824 | 0.20824 | 0.20824 | 0.9843 | -0.29952 | 0.98159 | -0.35213 | 57.2091
99 | -0.14715 | -0.037378 | 0.14748 | 0.037587 | 0.0003287 | 0.00020946 | 0.2225 | 0.2225 | 0.2225 | 0.9849 | -0.28797 | 0.9873 | -0.24167 | 30.5632
100 | 0.13433 | 0.033998 | -0.13414 | -0.033878 | 0.00018734 | 0.00011975 | 0.20375 | 0.20375 | 0.20375 | 0.98159 | -0.35213 | 0.98009 | -0.38123 | 55.9746
101 | -0.1489 | -0.037942 | 0.14897 | 0.037991 | 7.6339e-05 | 4.8392e-05 | 0.22464 | 0.22464 | 0.22464 | 0.9873 | -0.24167 | 0.98785 | -0.23106 | 20.571
102 | 0.0066892 | 0.0016763 | -0.006689 | -0.0016762 | 2.7744e-07 | 8.717e-08 | 0.010156 | 0.010156 | 0.010156 | 0.98009 | -0.38123 | 0.98005 | -0.3821 | 2.7901
103 | 0.12745 | 0.032202 | -0.12724 | -0.032068 | 0.00020889 | 0.0001335 | 0.19359 | 0.19359 | 0.19359 | 0.98009 | -0.38123 | 0.97834 | -0.41548 | 53.1846
104 | -0.15415 | -0.039288 | 0.15429 | 0.039378 | 0.00014191 | 9.0013e-05 | 0.23243 | 0.23243 | 0.23243 | 0.98785 | -0.23106 | 0.98885 | -0.212 | 21.285
105 | 0.0043704 | 0.0010951 | -0.00437 | -0.0010952 | 4.177e-07 | -5.1408e-08 | 0.0066356 | 0.0066357 | 0.0066357 | 0.98005 | -0.3821 | 0.97995 | -0.38411 | 1.823
106 | 0.026188 | 0.0065708 | -0.026183 | -0.0065677 | 5.0744e-06 | 3.1405e-06 | 0.039834 | 0.039834 | 0.039834 | 0.97834 | -0.41548 | 0.97813 | -0.41955 | 10.9434
107 | 0.013797 | 0.0034591 | -0.013793 | -0.0034571 | 3.5661e-06 | 1.9994e-06 | 0.020762 | 0.020762 | 0.020762 | 0.98885 | -0.212 | 0.98857 | -0.21742 | 5.7037
108 | -0.16809 | -0.042837 | 0.16813 | 0.042864 | 4.2379e-05 | 2.6919e-05 | 0.25319 | 0.25319 | 0.25319 | 0.98885 | -0.212 | 0.98912 | -0.20678 | 23.1862
109 | 0.0018174 | 0.00045542 | -0.0018174 | -0.00045549 | 1.7808e-08 | -6.7157e-08 | 0.0027597 | 0.0027597 | 0.0027597 | 0.97995 | -0.38411 | 0.97993 | -0.38431 | 0.75817
110 | 0.024376 | 0.0061149 | -0.024374 | -0.0061133 | 2.6197e-06 | 1.6129e-06 | 0.037086 | 0.037086 | 0.037086 | 0.97813 | -0.41955 | 0.97802 | -0.4218 | 10.1883
111 | -0.32391 | -0.083343 | 0.32402 | 0.083408 | 0.00010122 | 6.4646e-05 | 0.48295 | 0.48295 | 0.48295 | 0.99961 | -0.0073186 | 0.99995 | -0.00089408 | 44.2258
112 | 0.0026018 | 0.0006518 | -0.0026017 | -0.00065199 | 1.198e-07 | -1.9143e-07 | 0.0039123 | 0.0039124 | 0.0039124 | 0.98954 | -0.19993 | 0.98949 | -0.2009 | 1.0748
113 | -0.0026018 | -0.0006518 | 0.0026019 | 0.00065166 | 8.405e-08 | -1.3433e-07 | 0.0039123 | 0.0039122 | 0.0039123 | 0.98954 | -0.19993 | 0.98958 | -0.19925 | 1.0748
114 | 0.0013284 | 0.00033289 | -0.0013284 | -0.00033294 | 6.2301e-09 | -4.9485e-08 | 0.0019977 | 0.0019977 | 0.0019977 | 0.98949 | -0.2009 | 0.98949 | -0.201 | 0.54883
115 | -0.0038909 | -0.00097473 | 0.003891 | 0.0009747 | 8.6689e-08 | -3.1286e-08 | 0.0058506 | 0.0058506 | 0.0058506 | 0.98958 | -0.19925 | 0.9896 | -0.19878 | 1.6073
116 | -0.32572 | -0.083835 | 0.32573 | 0.083844 | 1.4165e-05 | 9.0466e-06 | 0.48548 | 0.48548 | 0.48548 | 0.99995 | -0.00089408 | 1 | 0 | 44.4581
117 | 0.041478 | 0.010472 | -0.041431 | -0.010443 | 4.649e-05 | 2.9363e-05 | 0.063092 | 0.063092 | 0.063092 | 0.97868 | -0.40909 | 0.97748 | -0.43252 | 17.3331
118 | -0.041478 | -0.010472 | 0.041536 | 0.010509 | 5.7996e-05 | 3.6629e-05 | 0.063092 | 0.063092 | 0.063092 | 0.97868 | -0.40909 | 0.98017 | -0.37995 | 17.333
119 | 0.040394 | 0.010183 | -0.040365 | -0.010164 | 2.9043e-05 | 1.8331e-05 | 0.061513 | 0.061513 | 0.061513 | 0.97748 | -0.43252 | 0.97671 | -0.44756 | 16.8991
120 | 0.03142 | 0.0078982 | -0.031396 | -0.007883 | 2.4181e-05 | 1.5126e-05 | 0.047967 | 0.047967 | 0.047967 | 0.97487 | -0.48379 | 0.97405 | -0.49992 | 13.1778
121 | -0.033576 | -0.0084385 | 0.033578 | 0.0084399 | 2.2024e-06 | 1.3816e-06 | 0.051258 | 0.051258 | 0.051258 | 0.97487 | -0.48379 | 0.97494 | -0.48242 | 14.0819
122 | 0.027604 | 0.0069328 | -0.02759 | -0.0069238 | 1.449e-05 | 9.0037e-06 | 0.042175 | 0.042175 | 0.042175 | 0.97405 | -0.49992 | 0.97349 | -0.51093 | 11.5866
123 | -0.034704 | -0.008722 | 0.034704 | 0.0087224 | 6.5999e-07 | 4.1457e-07 | 0.052976 | 0.052976 | 0.052976 | 0.97494 | -0.48242 | 0.97496 | -0.48202 | 14.5538
124 | 0.025961 | 0.0065156 | -0.02596 | -0.0065151 | 7.5795e-07 | 4.6913e-07 | 0.039686 | 0.039686 | 0.039686 | 0.97349 | -0.51093 | 0.97346 | -0.51154 | 10.9026
125 | -0.035924 | -0.0090281 | 0.035939 | 0.0090375 | 1.4919e-05 | 9.3833e-06 | 0.054838 | 0.054838 | 0.054838 | 0.97496 | -0.48202 | 0.9754 | -0.47332 | 15.0653
126 | 0.025271 | 0.0063425 | -0.025258 | -0.0063345 | 1.2989e-05 | 8.0244e-06 | 0.038633 | 0.038633 | 0.038633 | 0.97346 | -0.51154 | 0.97291 | -0.52233 | 10.6134
127 | -0.038057 | -0.0095682 | 0.038079 | 0.0095818 | 2.1534e-05 | 1.3569e-05 | 0.058069 | 0.058069 | 0.058069 | 0.9754 | -0.47332 | 0.976 | -0.46148 | 15.9531
128 | 0.0021183 | 0.00053072 | -0.0021183 | -0.00053075 | 1.3785e-08 | -3.5113e-08 | 0.0032316 | 0.0032316 | 0.0032316 | 0.9754 | -0.47332 | 0.97539 | -0.47346 | 0.88779
129 | -0.038773 | -0.0097558 | 0.038799 | 0.0097721 | 2.582e-05 | 1.6279e-05 | 0.059128 | 0.059128 | 0.059128 | 0.976 | -0.46148 | 0.97671 | -0.44756 | 16.2439
130 | 0.0021183 | 0.00053075 | -0.0021183 | -0.00053089 | 5.3244e-08 | -1.3562e-07 | 0.0032316 | 0.0032316 | 0.0032316 | 0.97539 | -0.47346 | 0.97536 | -0.47399 | 0.88781
131 | 0.0048372 | 0.0012122 | -0.0048367 | -0.0012122 | 5.657e-07 | 1.2598e-08 | 0.0073596 | 0.0073597 | 0.0073597 | 0.97802 | -0.4218 | 0.97789 | -0.42426 | 2.0219
132 | 0.019537 | 0.0049011 | -0.019525 | -0.0048941 | 1.1568e-05 | 6.9659e-06 | 0.029726 | 0.029726 | 0.029726 | 0.97802 | -0.4218 | 0.97738 | -0.43423 | 8.1665
133 | 0.016464 | 0.0041269 | -0.016463 | -0.0041264 | 9.2397e-07 | 5.422e-07 | 0.025066 | 0.025066 | 0.025066 | 0.97738 | -0.43423 | 0.97732 | -0.43541 | 6.8862
134 | 0.0013063 | 0.00032688 | -0.0013062 | -0.00032737 | 6.3592e-08 | -4.857e-07 | 0.0019988 | 0.001999 | 0.001999 | 0.97236 | -0.53316 | 0.97231 | -0.53418 | 0.54918
135 | 0.002557 | 0.00064035 | -0.0025568 | -0.00064059 | 1.6003e-07 | -2.433e-07 | 0.0039128 | 0.0039129 | 0.0039129 | 0.97236 | -0.53316 | 0.9723 | -0.53448 | 1.075
136 | 0.0011362 | 0.00028455 | -0.0011362 | -0.00028475 | 1.9635e-08 | -2.0222e-07 | 0.0017388 | 0.0017388 | 0.0017388 | 0.9723 | -0.53448 | 0.97228 | -0.53484 | 0.4777
137 | -0.0057969 | -0.0014523 | 0.0057972 | 0.0014524 | 3.2419e-07 | 6.1274e-08 | 0.0087163 | 0.0087162 | 0.0087163 | 0.9896 | -0.19878 | 0.98966 | -0.19761 | 2.3946
138 | 0.0053587 | 0.0013428 | -0.0053584 | -0.0013428 | 3.3477e-07 | 3.7562e-08 | 0.0080571 | 0.0080571 | 0.0080571 | 0.98966 | -0.19761 | 0.9896 | -0.19892 | 2.2135
139 | -0.011156 | -0.0027952 | 0.011157 | 0.002796 | 1.4316e-06 | 7.4186e-07 | 0.016773 | 0.016773 | 0.016773 | 0.98966 | -0.19761 | 0.9898 | -0.19492 | 4.608
140 | 0.0040713 | 0.0010202 | -0.0040712 | -0.0010202 | 9.909e-08 | -2.7167e-08 | 0.0061218 | 0.0061218 | 0.0061218 | 0.9896 | -0.19892 | 0.98957 | -0.19943 | 1.6818
141 | -0.012267 | -0.003074 | 0.012269 | 0.0030753 | 2.4792e-06 | 1.3368e-06 | 0.018441 | 0.018441 | 0.018441 | 0.9898 | -0.19492 | 0.99002 | -0.19067 | 5.0662
142 | 0.002781 | 0.00069688 | -0.002781 | -0.00069694 | 4.68e-08 | -6.173e-08 | 0.0041818 | 0.0041818 | 0.0041818 | 0.98957 | -0.19943 | 0.98955 | -0.19979 | 1.1489
143 | -0.019533 | -0.0048958 | 0.019537 | 0.0048984 | 4.3661e-06 | 2.6206e-06 | 0.029358 | 0.029358 | 0.029358 | 0.99002 | -0.19067 | 0.99026 | -0.18598 | 8.0655
144 | 0.0072637 | 0.0018205 | -0.0072631 | -0.0018202 | 6.4529e-07 | 2.2736e-07 | 0.010917 | 0.010918 | 0.010918 | 0.99002 | -0.19067 | 0.98992 | -0.19254 | 2.9993
145 | 0.0015014 | 0.00037624 | -0.0015014 | -0.00037628 | 5.2737e-09 | -3.2071e-08 | 0.0022576 | 0.0022576 | 0.0022576 | 0.98955 | -0.19979 | 0.98955 | -0.19986 | 0.62023
146 | 0.0062747 | 0.0015725 | -0.0062745 | -0.0015725 | 2.3123e-07 | 5.888e-08 | 0.0094319 | 0.0094319 | 0.0094319 | 0.98992 | -0.19254 | 0.98988 | -0.19331 | 2.5912
147 | 0.0088727 | 0.002224 | -0.0088711 | -0.0022233 | 1.599e-06 | 7.3066e-07 | 0.013509 | 0.013509 | 0.013509 | 0.97732 | -0.43541 | 0.97713 | -0.43919 | 3.7114
148 | 0.0075902 | 0.0019023 | -0.0075899 | -0.0019022 | 2.5111e-07 | 9.788e-08 | 0.011556 | 0.011556 | 0.011556 | 0.97732 | -0.43541 | 0.97729 | -0.4361 | 3.1748
149 | -0.0053221 | -0.0013338 | 0.0053223 | 0.0013338 | 1.7199e-07 | 1.7967e-08 | 0.0080006 | 0.0080006 | 0.0080006 | 0.98985 | -0.19399 | 0.98988 | -0.19331 | 2.198
150 | 0.0028031 | 0.0007025 | -0.0028031 | -0.00070252 | 1.7408e-08 | -2.2465e-08 | 0.0042138 | 0.0042138 | 0.0042138 | 0.98985 | -0.19399 | 0.98984 | -0.19412 | 1.1576

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.32908 | 0.084268

## res_load
| p_mw | q_mvar
0 | 0.0019838 | 0.0004972
1 | 0.0043939 | 0.0011012
2 | 0.0035738 | 0.00089568
3 | 0.0049657 | 0.0012445
4 | 0.0036185 | 0.00090688
5 | 0.0025733 | 0.00064492
6 | 0.0025095 | 0.00062893
7 | 0.0013824 | 0.00034647
8 | 0.0014319 | 0.00035888
9 | 0.001488 | 0.00037293
10 | 0.0012146 | 0.0003044
11 | 0.0047291 | 0.0011852
12 | 0.0023155 | 0.00058032
13 | 0.004869 | 0.0012203
14 | 0.00089335 | 0.00022389
15 | 0.0013178 | 0.00033027
16 | 0.00088546 | 0.00022192
17 | 0.013965 | 0.0034999
18 | 0.00089336 | 0.0002239
19 | 0.0015742 | 0.00039453
20 | 0.00093565 | 0.0002345
21 | 0.001494 | 0.00037444
22 | 0.0044693 | 0.0011201
23 | 0.00148 | 0.00037093
24 | 0.00099168 | 0.00024854
25 | 0.0011362 | 0.00028477
26 | 0.0017357 | 0.00043501
27 | 0.0011788 | 0.00029543
28 | 0.00085528 | 0.00021435
29 | 0.0083041 | 0.0020812
30 | 0.00095757 | 0.00023999
31 | 0.0015644 | 0.00039208
32 | 0.0023139 | 0.00057991
33 | 0.00087762 | 0.00021995
34 | 0.0013393 | 0.00033567
35 | 0.00090051 | 0.00022569
36 | 0.0017699 | 0.00044359
37 | 0.0044468 | 0.0011145
38 | 0.0060685 | 0.0015209
39 | 0.0036898 | 0.00092475
40 | 0.0057687 | 0.0014458
41 | 0.0036909 | 0.00092504
42 | 0.0060722 | 0.0015218
43 | 0.0099157 | 0.0024851
44 | 0.0048328 | 0.0012112
45 | 0.0061038 | 0.0015298
46 | 0.0049826 | 0.0012488
47 | 0.0010023 | 0.00025121
48 | 0.0019498 | 0.00048868
49 | 0.0017075 | 0.00042795
50 | 0.006315 | 0.0015827
51 | 0.004855 | 0.0012168
52 | 0.0016455 | 0.0004124
53 | 0.0029737 | 0.00074527
54 | 0.0016686 | 0.0004182
55 | 0.0013318 | 0.00033379
56 | 0.0033842 | 0.00084816
57 | 0.0060514 | 0.0015166
58 | 0.0029644 | 0.00074295
59 | 0.0014172 | 0.00035518
60 | 0.0051764 | 0.0012973
61 | 0.0023186 | 0.00058109
62 | 0.0025526 | 0.00063973
63 | 0.0018068 | 0.00045282
64 | 0.0023287 | 0.00058364
65 | 0.0016322 | 0.00040907
66 | 0.0016684 | 0.00041814
67 | 0.0012732 | 0.0003191
68 | 0.0012891 | 0.00032307
69 | 0.0017049 | 0.0004273
70 | 0.0010377 | 0.00026006
71 | 0.0063329 | 0.0015872
72 | 0.002156 | 0.00054035
73 | 0.0037915 | 0.00095024
74 | 0.0011255 | 0.00028207
75 | 0.0016288 | 0.00040823
76 | 0.0012199 | 0.00030574
77 | 0.00068877 | 0.00017262
78 | 0.0037788 | 0.00094706
79 | 0.00069439 | 0.00017403
80 | 0.0047306 | 0.0011856
81 | 0.0023209 | 0.00058167
82 | 0.0013786 | 0.0003455
83 | 0.0026754 | 0.00067051
84 | 0.0057578 | 0.001443
85 | 0.0050414 | 0.0012635
86 | 0.0048367 | 0.0012122
87 | 0.0030612 | 0.00076721
88 | 0.0013062 | 0.00032737
89 | 0.0014206 | 0.00035604
90 | 0.0019058 | 0.00047765
91 | 0.0012871 | 0.00032257
92 | 0.0011094 | 0.00027803
93 | 0.0012902 | 0.00032335
94 | 0.0013284 | 0.00033294
95 | 0.0012796 | 0.0003207
96 | 0.0015514 | 0.00038882
97 | 0.00098837 | 0.00024771
98 | 0.0016925 | 0.00042418
99 | 0.0015656 | 0.00039237
100 | 0.0021183 | 0.00053089
101 | 0.0011362 | 0.00028475
102 | 0.0099815 | 0.0025016
103 | 0.0059295 | 0.0014861
104 | 0.0088711 | 0.0022233
105 | 0.0075899 | 0.0019022
106 | 0.0018174 | 0.00045549
107 | 0.0015014 | 0.00037628
108 | 0.002519 | 0.00063133
109 | 0.00095215 | 0.00023863
110 | 0.0028031 | 0.00070252

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1