## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_118-19_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_118-19_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_118-19_0_6_node_74 | 0.4 | n |  | TRUE
3 | bus_LV_118-19_0_6_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_118-19_0_6_node_70 | 0.4 | n |  | TRUE
5 | bus_LV_118-19_0_6_node_72 | 0.4 | n |  | TRUE
6 | bus_LV_118-19_0_6_node_67 | 0.4 | n |  | TRUE
7 | bus_LV_118-19_0_6_node_71 | 0.4 | n |  | TRUE
8 | bus_LV_118-19_0_6_node_73 | 0.4 | n |  | TRUE
9 | bus_LV_118-19_0_6_node_3 | 0.4 | n |  | TRUE
10 | bus_LV_118-19_0_6_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_118-19_0_6_node_4 | 0.4 | n |  | TRUE
12 | bus_LV_118-19_0_6_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_118-19_0_6_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_118-19_0_6_node_6 | 0.4 | n |  | TRUE
15 | bus_LV_118-19_0_6_node_65 | 0.4 | n |  | TRUE
16 | bus_LV_118-19_0_6_node_66 | 0.4 | n |  | TRUE
17 | bus_LV_118-19_0_6_node_68 | 0.4 | n |  | TRUE
18 | bus_LV_118-19_0_6_node_69 | 0.4 | n |  | TRUE
19 | bus_LV_118-19_0_6_node_17 | 0.4 | n |  | TRUE
20 | bus_LV_118-19_0_6_node_9 | 0.4 | n |  | TRUE
21 | bus_LV_118-19_0_6_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_118-19_0_6_node_20 | 0.4 | n |  | TRUE
23 | bus_LV_118-19_0_6_node_11 | 0.4 | n |  | TRUE
24 | bus_LV_118-19_0_6_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_118-19_0_6_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_118-19_0_6_node_13 | 0.4 | n |  | TRUE
27 | bus_LV_118-19_0_6_node_19 | 0.4 | n |  | TRUE
28 | bus_LV_118-19_0_6_node_134 | 0.4 | n |  | TRUE
29 | bus_LV_118-19_0_6_node_128 | 0.4 | n |  | TRUE
30 | bus_LV_118-19_0_6_node_126 | 0.4 | n |  | TRUE
31 | bus_LV_118-19_0_6_node_21 | 0.4 | n |  | TRUE
32 | bus_LV_118-19_0_6_node_43 | 0.4 | n |  | TRUE
33 | bus_LV_118-19_0_6_node_44 | 0.4 | n |  | TRUE
34 | bus_LV_118-19_0_6_node_25 | 0.4 | n |  | TRUE
35 | bus_LV_118-19_0_6_node_23 | 0.4 | n |  | TRUE
36 | bus_LV_118-19_0_6_node_137 | 0.4 | n |  | TRUE
37 | bus_LV_118-19_0_6_node_18 | 0.4 | n |  | TRUE
38 | bus_LV_118-19_0_6_node_136 | 0.4 | n |  | TRUE
39 | bus_LV_118-19_0_6_node_135 | 0.4 | n |  | TRUE
40 | bus_LV_118-19_0_6_node_26 | 0.4 | n |  | TRUE
41 | bus_LV_118-19_0_6_node_24 | 0.4 | n |  | TRUE
42 | bus_LV_118-19_0_6_node_127 | 0.4 | n |  | TRUE
43 | bus_LV_118-19_0_6_node_22 | 0.4 | n |  | TRUE
44 | bus_LV_118-19_0_6_node_38 | 0.4 | n |  | TRUE
45 | bus_LV_118-19_0_6_node_39 | 0.4 | n |  | TRUE
46 | bus_LV_118-19_0_6_node_27 | 0.4 | n |  | TRUE
47 | bus_LV_118-19_0_6_node_28 | 0.4 | n |  | TRUE
48 | bus_LV_118-19_0_6_node_29 | 0.4 | n |  | TRUE
49 | bus_LV_118-19_0_6_node_30 | 0.4 | n |  | TRUE
50 | bus_LV_118-19_0_6_node_31 | 0.4 | n |  | TRUE
51 | bus_LV_118-19_0_6_node_32 | 0.4 | n |  | TRUE
52 | bus_LV_118-19_0_6_node_33 | 0.4 | n |  | TRUE
53 | bus_LV_118-19_0_6_node_41 | 0.4 | n |  | TRUE
54 | bus_LV_118-19_0_6_node_132 | 0.4 | n |  | TRUE
55 | bus_LV_118-19_0_6_node_36 | 0.4 | n |  | TRUE
56 | bus_LV_118-19_0_6_node_42 | 0.4 | n |  | TRUE
57 | bus_LV_118-19_0_6_node_61 | 0.4 | n |  | TRUE
58 | bus_LV_118-19_0_6_node_34 | 0.4 | n |  | TRUE
59 | bus_LV_118-19_0_6_node_35 | 0.4 | n |  | TRUE
60 | bus_LV_118-19_0_6_node_37 | 0.4 | n |  | TRUE
61 | bus_LV_118-19_0_6_node_60 | 0.4 | n |  | TRUE
62 | bus_LV_118-19_0_6_node_62 | 0.4 | n |  | TRUE
63 | bus_LV_118-19_0_6_node_63 | 0.4 | n |  | TRUE
64 | bus_LV_118-19_0_6_node_64 | 0.4 | n |  | TRUE
65 | bus_LV_118-19_0_6_node_40 | 0.4 | n |  | TRUE
66 | bus_LV_118-19_0_6_node_47 | 0.4 | n |  | TRUE
67 | bus_LV_118-19_0_6_node_48 | 0.4 | n |  | TRUE
68 | bus_LV_118-19_0_6_node_49 | 0.4 | n |  | TRUE
69 | bus_LV_118-19_0_6_node_57 | 0.4 | n |  | TRUE
70 | bus_LV_118-19_0_6_node_45 | 0.4 | n |  | TRUE
71 | bus_LV_118-19_0_6_node_46 | 0.4 | n |  | TRUE
72 | bus_LV_118-19_0_6_node_51 | 0.4 | n |  | TRUE
73 | bus_LV_118-19_0_6_node_52 | 0.4 | n |  | TRUE
74 | bus_LV_118-19_0_6_node_54 | 0.4 | n |  | TRUE
75 | bus_LV_118-19_0_6_node_55 | 0.4 | n |  | TRUE
76 | bus_LV_118-19_0_6_node_50 | 0.4 | n |  | TRUE
77 | bus_LV_118-19_0_6_node_58 | 0.4 | n |  | TRUE
78 | bus_LV_118-19_0_6_node_53 | 0.4 | n |  | TRUE
79 | bus_LV_118-19_0_6_node_81 | 0.4 | n |  | TRUE
80 | bus_LV_118-19_0_6_node_77 | 0.4 | n |  | TRUE
81 | bus_LV_118-19_0_6_node_79 | 0.4 | n |  | TRUE
82 | bus_LV_118-19_0_6_node_133 | 0.4 | n |  | TRUE
83 | bus_LV_118-19_0_6_node_84 | 0.4 | n |  | TRUE
84 | bus_LV_118-19_0_6_node_80 | 0.4 | n |  | TRUE
85 | bus_LV_118-19_0_6_node_78 | 0.4 | n |  | TRUE
86 | bus_LV_118-19_0_6_node_76 | 0.4 | n |  | TRUE
87 | bus_LV_118-19_0_6_node_59 | 0.4 | n |  | TRUE
88 | bus_LV_118-19_0_6_node_118 | 0.4 | n |  | TRUE
89 | bus_LV_118-19_0_6_node_87 | 0.4 | n |  | TRUE
90 | bus_LV_118-19_0_6_node_85 | 0.4 | n |  | TRUE
91 | bus_LV_118-19_0_6_node_117 | 0.4 | n |  | TRUE
92 | bus_LV_118-19_0_6_node_130 | 0.4 | n |  | TRUE
93 | bus_LV_118-19_0_6_node_75 | 0.4 | n |  | TRUE
94 | bus_LV_118-19_0_6_node_83 | 0.4 | n |  | TRUE
95 | bus_LV_118-19_0_6_node_86 | 0.4 | n |  | TRUE
96 | bus_LV_118-19_0_6_node_122 | 0.4 | n |  | TRUE
97 | bus_LV_118-19_0_6_node_121 | 0.4 | n |  | TRUE
98 | bus_LV_118-19_0_6_node_88 | 0.4 | n |  | TRUE
99 | bus_LV_118-19_0_6_node_89 | 0.4 | n |  | TRUE
100 | bus_LV_118-19_0_6_node_90 | 0.4 | n |  | TRUE
101 | bus_LV_118-19_0_6_node_91 | 0.4 | n |  | TRUE
102 | bus_LV_118-19_0_6_node_92 | 0.4 | n |  | TRUE
103 | bus_LV_118-19_0_6_node_100 | 0.4 | n |  | TRUE
104 | bus_LV_118-19_0_6_node_120 | 0.4 | n |  | TRUE
105 | bus_LV_118-19_0_6_node_98 | 0.4 | n |  | TRUE
106 | bus_LV_118-19_0_6_node_119 | 0.4 | n |  | TRUE
107 | bus_LV_118-19_0_6_node_93 | 0.4 | n |  | TRUE
108 | bus_LV_118-19_0_6_node_94 | 0.4 | n |  | TRUE
109 | bus_LV_118-19_0_6_node_95 | 0.4 | n |  | TRUE
110 | bus_LV_118-19_0_6_node_96 | 0.4 | n |  | TRUE
111 | bus_LV_118-19_0_6_node_97 | 0.4 | n |  | TRUE
112 | bus_LV_118-19_0_6_node_112 | 0.4 | n |  | TRUE
113 | bus_LV_118-19_0_6_node_124 | 0.4 | n |  | TRUE
114 | bus_LV_118-19_0_6_node_110 | 0.4 | n |  | TRUE
115 | bus_LV_118-19_0_6_node_99 | 0.4 | n |  | TRUE
116 | bus_LV_118-19_0_6_node_101 | 0.4 | n |  | TRUE
117 | bus_LV_118-19_0_6_node_102 | 0.4 | n |  | TRUE
118 | bus_LV_118-19_0_6_node_105 | 0.4 | n |  | TRUE
119 | bus_LV_118-19_0_6_node_104 | 0.4 | n |  | TRUE
120 | bus_LV_118-19_0_6_node_106 | 0.4 | n |  | TRUE
121 | bus_LV_118-19_0_6_node_107 | 0.4 | n |  | TRUE
122 | bus_LV_118-19_0_6_node_113 | 0.4 | n |  | TRUE
123 | bus_LV_118-19_0_6_node_114 | 0.4 | n |  | TRUE
124 | bus_LV_118-19_0_6_node_108 | 0.4 | n |  | TRUE
125 | bus_LV_118-19_0_6_node_109 | 0.4 | n |  | TRUE
126 | bus_LV_118-19_0_6_node_111 | 0.4 | n |  | TRUE
127 | bus_LV_118-19_0_6_node_125 | 0.4 | n |  | TRUE
128 | bus_LV_118-19_0_6_node_115 | 0.4 | n |  | TRUE
129 | bus_LV_118-19_0_6_node_116 | 0.4 | n |  | TRUE
130 | bus_LV_118-19_0_6_node_129 | 0.4 | n |  | TRUE
131 | bus_MV_9_2_node_74 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_118-19_0_6_load_0 | 0 | 0.016076 | 0.0040289 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_118-19_0_6_load_1 | 1 | 0.015409 | 0.003862 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_118-19_0_6_load_74 | 2 | 0.0027588 | 0.00069141 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_118-19_0_6_load_70 | 4 | 0.0012217 | 0.0003062 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_118-19_0_6_load_72 | 5 | 0.0013959 | 0.00034984 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_118-19_0_6_load_71 | 7 | 0.0011103 | 0.00027827 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_118-19_0_6_load_3 | 9 | 0.015654 | 0.0039233 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_118-19_0_6_load_5 | 10 | 0.018811 | 0.0047146 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_118-19_0_6_load_8 | 12 | 0.0018482 | 0.00046319 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_118-19_0_6_load_7 | 13 | 0.018934 | 0.0047453 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_118-19_0_6_load_6 | 14 | 0.018576 | 0.0046555 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_118-19_0_6_load_65 | 15 | 0.0023184 | 0.00058104 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_118-19_0_6_load_66 | 16 | 0.0035886 | 0.00089939 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_118-19_0_6_load_68 | 17 | 0.0024631 | 0.00061731 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_118-19_0_6_load_69 | 18 | 0.0018315 | 0.00045902 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_118-19_0_6_load_20 | 22 | 0.0071993 | 0.0018043 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_118-19_0_6_load_15 | 24 | 0.010133 | 0.0025396 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_118-19_0_6_load_16 | 25 | 0.011352 | 0.002845 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_118-19_0_6_load_13 | 26 | 0.0084044 | 0.0021063 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_118-19_0_6_load_134 | 28 | 0.0078024 | 0.0019555 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_118-19_0_6_load_128 | 29 | 0.0075081 | 0.0018817 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_118-19_0_6_load_126 | 30 | 0.001847 | 0.00046289 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_118-19_0_6_load_21 | 31 | 0.0039285 | 0.00098457 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_118-19_0_6_load_43 | 32 | 0.0050398 | 0.0012631 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_118-19_0_6_load_44 | 33 | 0.0027669 | 0.00069346 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_118-19_0_6_load_25 | 34 | 0.0093807 | 0.002351 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_118-19_0_6_load_23 | 35 | 0.011907 | 0.0029842 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_118-19_0_6_load_137 | 36 | 0.007926 | 0.0019864 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_118-19_0_6_load_136 | 38 | 0.005455 | 0.0013671 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_118-19_0_6_load_135 | 39 | 0.00554 | 0.0013885 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_118-19_0_6_load_26 | 40 | 0.011112 | 0.0027849 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_118-19_0_6_load_24 | 41 | 0.013982 | 0.0035042 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_118-19_0_6_load_22 | 43 | 0.0099313 | 0.002489 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_118-19_0_6_load_38 | 44 | 0.0050155 | 0.001257 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_118-19_0_6_load_39 | 45 | 0.0024811 | 0.00062183 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_118-19_0_6_load_27 | 46 | 0.0045438 | 0.0011388 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_118-19_0_6_load_28 | 47 | 0.0063833 | 0.0015998 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_118-19_0_6_load_29 | 48 | 0.014118 | 0.0035383 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_118-19_0_6_load_30 | 49 | 0.0065541 | 0.0016426 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_118-19_0_6_load_32 | 51 | 0.0079809 | 0.0020002 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_118-19_0_6_load_41 | 53 | 0.0084664 | 0.0021219 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_118-19_0_6_load_132 | 54 | 0.012565 | 0.0031492 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_118-19_0_6_load_36 | 55 | 0.0060801 | 0.0015238 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_118-19_0_6_load_42 | 56 | 0.0019693 | 0.00049357 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_118-19_0_6_load_61 | 57 | 0.0019847 | 0.0004974 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_118-19_0_6_load_34 | 58 | 0.0035382 | 0.00088675 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_118-19_0_6_load_35 | 59 | 0.0045915 | 0.0011507 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_118-19_0_6_load_37 | 60 | 0.0060046 | 0.0015049 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_118-19_0_6_load_60 | 61 | 0.0042777 | 0.0010721 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_118-19_0_6_load_62 | 62 | 0.011979 | 0.0030022 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_118-19_0_6_load_63 | 63 | 0.0014935 | 0.00037429 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_118-19_0_6_load_64 | 64 | 0.00076565 | 0.00019189 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_118-19_0_6_load_47 | 66 | 0.0013634 | 0.00034171 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_118-19_0_6_load_48 | 67 | 0.00059529 | 0.00014919 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_118-19_0_6_load_49 | 68 | 0.00073399 | 0.00018396 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_118-19_0_6_load_57 | 69 | 0.00069754 | 0.00017482 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_118-19_0_6_load_45 | 70 | 0.0006785 | 0.00017005 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_118-19_0_6_load_46 | 71 | 0.0009241 | 0.0002316 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_118-19_0_6_load_52 | 73 | 0.0008469 | 0.00021225 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_118-19_0_6_load_58 | 77 | 0.0013402 | 0.0003359 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_118-19_0_6_load_53 | 78 | 0.0048033 | 0.0012038 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_118-19_0_6_load_79 | 81 | 0.00068991 | 0.00017291 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_118-19_0_6_load_133 | 82 | 0.002862 | 0.00071729 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_118-19_0_6_load_84 | 83 | 0.0019154 | 0.00048005 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_118-19_0_6_load_76 | 86 | 0.0040527 | 0.0010157 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_118-19_0_6_load_118 | 88 | 0.0017142 | 0.00042962 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_118-19_0_6_load_87 | 89 | 0.0019747 | 0.0004949 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_118-19_0_6_load_117 | 91 | 0.0012288 | 0.00030797 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_118-19_0_6_load_130 | 92 | 0.0052461 | 0.0013148 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_118-19_0_6_load_75 | 93 | 0.0048763 | 0.0012221 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_118-19_0_6_load_83 | 94 | 0.0085847 | 0.0021515 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_118-19_0_6_load_122 | 96 | 0.0039681 | 0.0009945 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_118-19_0_6_load_121 | 97 | 0.0023198 | 0.0005814 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_118-19_0_6_load_88 | 98 | 0.0026123 | 0.0006547 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_118-19_0_6_load_89 | 99 | 0.0056858 | 0.001425 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_118-19_0_6_load_90 | 100 | 0.00050987 | 0.00012779 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_118-19_0_6_load_91 | 101 | 0.0044263 | 0.0011093 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_118-19_0_6_load_92 | 102 | 0.0012312 | 0.00030858 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_118-19_0_6_load_100 | 103 | 0.0022203 | 0.00055645 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_118-19_0_6_load_120 | 104 | 0.0033898 | 0.00084957 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_118-19_0_6_load_98 | 105 | 0.0079428 | 0.0019906 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_118-19_0_6_load_119 | 106 | 0.0019324 | 0.0004843 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_118-19_0_6_load_93 | 107 | 0.0037452 | 0.00093864 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_118-19_0_6_load_94 | 108 | 0.0030175 | 0.00075627 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_118-19_0_6_load_95 | 109 | 0.0021104 | 0.00052892 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_118-19_0_6_load_96 | 110 | 0.0048025 | 0.0012036 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_118-19_0_6_load_97 | 111 | 0.00076234 | 0.00019106 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_118-19_0_6_load_124 | 113 | 0.0010203 | 0.00025572 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_118-19_0_6_load_110 | 114 | 0.0011157 | 0.00027961 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_118-19_0_6_load_99 | 115 | 0.0074038 | 0.0018556 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_118-19_0_6_load_101 | 116 | 0.0014655 | 0.00036728 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_118-19_0_6_load_102 | 117 | 0.0021523 | 0.00053942 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_118-19_0_6_load_105 | 118 | 0.0021211 | 0.0005316 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_118-19_0_6_load_104 | 119 | 0.0023471 | 0.00058824 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_118-19_0_6_load_106 | 120 | 0.0020128 | 0.00050446 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_118-19_0_6_load_107 | 121 | 0.0018077 | 0.00045305 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_118-19_0_6_load_113 | 122 | 0.0022796 | 0.00057132 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_118-19_0_6_load_108 | 124 | 0.0011196 | 0.00028059 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_118-19_0_6_load_109 | 125 | 0.0010425 | 0.00026126 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_118-19_0_6_load_111 | 126 | 0.0035809 | 0.00089747 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_118-19_0_6_load_125 | 127 | 0.0019787 | 0.00049592 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_118-19_0_6_load_115 | 128 | 0.0011018 | 0.00027615 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_118-19_0_6_load_116 | 129 | 0.00097368 | 0.00024403 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_118-19_0_6_load_129 | 130 | 0.0052632 | 0.0013191 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 34 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_118-19_0_6_line_0 |  | 0 | 1 | 0.033762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_118-19_0_6_line_1 |  | 0 | 2 | 0.096391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_118-19_0_6_line_2 |  | 1 | 3 | 0.033362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_118-19_0_6_line_3 |  | 2 | 8 | 0.05668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_118-19_0_6_line_4 |  | 3 | 9 | 0.026939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_118-19_0_6_line_5 |  | 4 | 5 | 0.0052665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_118-19_0_6_line_6 |  | 4 | 6 | 0.028799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_118-19_0_6_line_7 |  | 5 | 7 | 0.020245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_118-19_0_6_line_8 |  | 6 | 18 | 0.052724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_118-19_0_6_line_9 |  | 6 | 15 | 0.016668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_118-19_0_6_line_10 |  | 7 | 8 | 0.01662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_118-19_0_6_line_11 |  | 9 | 10 | 0.015569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
12 | LV_118-19_0_6_line_12 |  | 10 | 14 | 0.023006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
13 | LV_118-19_0_6_line_13 |  | 11 | 12 | 0.018747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
14 | LV_118-19_0_6_line_14 |  | 11 | 13 | 0.057466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
15 | LV_118-19_0_6_line_15 |  | 12 | 19 | 0.0054201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
16 | LV_118-19_0_6_line_16 |  | 13 | 14 | 0.020161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
17 | LV_118-19_0_6_line_17 |  | 15 | 16 | 0.012286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_118-19_0_6_line_18 |  | 16 | 17 | 0.016978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_118-19_0_6_line_19 |  | 19 | 29 | 0.004398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_118-19_0_6_line_20 |  | 19 | 27 | 0.059467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
21 | LV_118-19_0_6_line_21 |  | 19 | 30 | 0.0067163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_118-19_0_6_line_22 |  | 20 | 21 | 0.047354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
23 | LV_118-19_0_6_line_23 |  | 20 | 22 | 0.011886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
24 | LV_118-19_0_6_line_24 |  | 21 | 27 | 0.015566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
25 | LV_118-19_0_6_line_25 |  | 21 | 28 | 0.007686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_118-19_0_6_line_26 |  | 22 | 31 | 0.05472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
27 | LV_118-19_0_6_line_27 |  | 23 | 24 | 0.031725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_118-19_0_6_line_28 |  | 23 | 25 | 0.021372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_118-19_0_6_line_29 |  | 23 | 26 | 0.019903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_118-19_0_6_line_30 |  | 24 | 34 | 0.030241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_118-19_0_6_line_31 |  | 24 | 35 | 0.023025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_118-19_0_6_line_32 |  | 27 | 36 | 0.007179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_118-19_0_6_line_33 |  | 27 | 37 | 0.030113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_118-19_0_6_line_34 |  | 30 | 42 | 0.009489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_118-19_0_6_line_35 |  | 31 | 43 | 0.018517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
36 | LV_118-19_0_6_line_36 |  | 32 | 33 | 0.030829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_118-19_0_6_line_37 |  | 33 | 70 | 0.051757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_118-19_0_6_line_38 |  | 34 | 40 | 0.010978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
39 | LV_118-19_0_6_line_39 |  | 35 | 41 | 0.0038356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_118-19_0_6_line_40 |  | 37 | 38 | 0.006724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_118-19_0_6_line_41 |  | 37 | 39 | 0.022339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_118-19_0_6_line_42 |  | 40 | 46 | 0.017762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
43 | LV_118-19_0_6_line_43 |  | 42 | 130 | 0.004334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_118-19_0_6_line_44 |  | 42 | 92 | 0.020375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_118-19_0_6_line_45 |  | 43 | 44 | 0.043536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
46 | LV_118-19_0_6_line_46 |  | 44 | 45 | 0.013829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
47 | LV_118-19_0_6_line_47 |  | 45 | 65 | 0.039502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
48 | LV_118-19_0_6_line_48 |  | 46 | 47 | 0.021544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
49 | LV_118-19_0_6_line_49 |  | 47 | 48 | 0.00708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
50 | LV_118-19_0_6_line_50 |  | 48 | 49 | 0.0019781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
51 | LV_118-19_0_6_line_51 |  | 49 | 50 | 0.0089162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
52 | LV_118-19_0_6_line_52 |  | 50 | 51 | 0.034558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
53 | LV_118-19_0_6_line_53 |  | 50 | 52 | 0.041645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_118-19_0_6_line_54 |  | 51 | 53 | 0.019368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
55 | LV_118-19_0_6_line_55 |  | 52 | 54 | 0.022015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_118-19_0_6_line_56 |  | 52 | 55 | 0.0023459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_118-19_0_6_line_57 |  | 53 | 56 | 0.0067758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
58 | LV_118-19_0_6_line_58 |  | 54 | 57 | 0.18902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_118-19_0_6_line_59 |  | 55 | 58 | 0.038336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_118-19_0_6_line_60 |  | 56 | 65 | 0.020953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
61 | LV_118-19_0_6_line_61 |  | 57 | 61 | 0.014536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_118-19_0_6_line_62 |  | 58 | 59 | 0.019425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_118-19_0_6_line_63 |  | 59 | 60 | 0.0070913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_118-19_0_6_line_64 |  | 61 | 62 | 0.0622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_118-19_0_6_line_65 |  | 62 | 63 | 0.027277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_118-19_0_6_line_66 |  | 62 | 64 | 0.036383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_118-19_0_6_line_67 |  | 65 | 66 | 0.017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_118-19_0_6_line_68 |  | 65 | 67 | 0.015498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
69 | LV_118-19_0_6_line_69 |  | 66 | 68 | 0.030092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_118-19_0_6_line_70 |  | 67 | 69 | 0.015811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
71 | LV_118-19_0_6_line_71 |  | 68 | 76 | 0.021366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_118-19_0_6_line_72 |  | 69 | 77 | 0.012961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_118-19_0_6_line_73 |  | 70 | 71 | 0.029833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_118-19_0_6_line_74 |  | 71 | 72 | 0.02939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_118-19_0_6_line_75 |  | 72 | 73 | 0.012925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_118-19_0_6_line_76 |  | 72 | 74 | 0.047227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_118-19_0_6_line_77 |  | 72 | 75 | 0.13034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_118-19_0_6_line_78 |  | 73 | 76 | 0.024239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_118-19_0_6_line_79 |  | 74 | 80 | 0.032909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_118-19_0_6_line_80 |  | 74 | 81 | 0.042587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_118-19_0_6_line_81 |  | 75 | 82 | 0.038297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_118-19_0_6_line_82 |  | 77 | 87 | 0.0088181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_118-19_0_6_line_83 |  | 78 | 79 | 0.0097131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_118-19_0_6_line_84 |  | 79 | 83 | 0.028214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_118-19_0_6_line_85 |  | 79 | 84 | 0.009578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_118-19_0_6_line_86 |  | 80 | 85 | 0.027036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_118-19_0_6_line_87 |  | 81 | 84 | 0.043277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_118-19_0_6_line_88 |  | 83 | 94 | 0.014097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_118-19_0_6_line_89 |  | 85 | 86 | 0.010597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_118-19_0_6_line_90 |  | 86 | 93 | 0.016094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_118-19_0_6_line_91 |  | 87 | 88 | 0.016295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_118-19_0_6_line_92 |  | 88 | 91 | 0.034857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_118-19_0_6_line_93 |  | 89 | 90 | 0.025908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_118-19_0_6_line_94 |  | 90 | 95 | 0.028511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_118-19_0_6_line_95 |  | 91 | 106 | 0.0029375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_118-19_0_6_line_96 |  | 95 | 96 | 0.026203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_118-19_0_6_line_97 |  | 96 | 97 | 0.0353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_118-19_0_6_line_98 |  | 97 | 128 | 0.031635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_118-19_0_6_line_99 |  | 98 | 99 | 0.0013096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_118-19_0_6_line_100 |  | 98 | 100 | 0.019164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_118-19_0_6_line_101 |  | 99 | 101 | 0.0069895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_118-19_0_6_line_102 |  | 100 | 102 | 0.011594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_118-19_0_6_line_103 |  | 101 | 103 | 0.009968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_118-19_0_6_line_104 |  | 102 | 104 | 0.012764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_118-19_0_6_line_105 |  | 103 | 105 | 0.020647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_118-19_0_6_line_106 |  | 104 | 106 | 0.01855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_118-19_0_6_line_107 |  | 105 | 115 | 0.00014451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_118-19_0_6_line_108 |  | 107 | 108 | 0.031631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_118-19_0_6_line_109 |  | 107 | 109 | 0.050087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_118-19_0_6_line_110 |  | 108 | 110 | 0.035991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_118-19_0_6_line_111 |  | 109 | 111 | 0.023488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_118-19_0_6_line_112 |  | 111 | 112 | 0.0051948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_118-19_0_6_line_113 |  | 112 | 113 | 0.014061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_118-19_0_6_line_114 |  | 112 | 114 | 0.021946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_118-19_0_6_line_115 |  | 113 | 127 | 0.0018978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_118-19_0_6_line_116 |  | 114 | 124 | 0.0013936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_118-19_0_6_line_117 |  | 115 | 116 | 0.0050395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_118-19_0_6_line_118 |  | 116 | 117 | 0.021551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_118-19_0_6_line_119 |  | 117 | 118 | 0.0081469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_118-19_0_6_line_120 |  | 118 | 119 | 0.00037467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_118-19_0_6_line_121 |  | 119 | 120 | 0.0083485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_118-19_0_6_line_122 |  | 120 | 121 | 0.0005218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_118-19_0_6_line_123 |  | 121 | 122 | 0.0051194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_118-19_0_6_line_124 |  | 122 | 123 | 0.014984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_118-19_0_6_line_125 |  | 123 | 128 | 0.0073944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_118-19_0_6_line_126 |  | 123 | 129 | 0.0077818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_118-19_0_6_line_127 |  | 124 | 125 | 0.0011865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_118-19_0_6_line_128 |  | 125 | 126 | 0.013472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_118-19_0_6_line_129 |  | 127 | 129 | 0.0086828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_118-19_0_6_trafo_25 | 0.63 MVA 20/0.4 kV | 131 | 34 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16
0 | 2707940.5388 | 1234649.5285 | 2707969.7926 | 1234644.3165 | 2707973.7464 | 1234643.4525
1 | 2707940.5388 | 1234649.5285 | 2707896.036 | 1234735.031
2 | 2708006.3388 | 1234636.33 | 2707973.7464 | 1234643.4525
3 | 2707892.0967 | 1234791.5742 | 2707896.036 | 1234735.031
4 | 2708006.3388 | 1234636.33 | 2708010.7868 | 1234646.1073 | 2708011.8369 | 1234652.4757 | 2708017.1342 | 1234658.8436 | 2708018.315 | 1234659.7022
5 | 2707928.6731 | 1234796.1805 | 2707933.8983 | 1234796.8385
6 | 2707962.472 | 1234800.4369 | 2707933.8983 | 1234796.8385
7 | 2707908.5867 | 1234793.6509 | 2707928.6731 | 1234796.1805
8 | 2707962.472 | 1234800.4369 | 2708015.1317 | 1234803.0335
9 | 2707962.472 | 1234800.4369 | 2707964.0454 | 1234790.102 | 2707966.063 | 1234784.2248
10 | 2707892.0967 | 1234791.5742 | 2707908.5867 | 1234793.6509
11 | 2708018.315 | 1234659.7022 | 2708024.2701 | 1234664.0328 | 2708032.2657 | 1234665.8772
12 | 2708032.2657 | 1234665.8772 | 2708037.6145 | 1234667.1111 | 2708055.0971 | 1234668.2027
13 | 2708132.4277 | 1234663.2104 | 2708131.6168 | 1234681.9394
14 | 2708132.4277 | 1234663.2104 | 2708120.5202 | 1234664.3724 | 2708094.0593 | 1234667.738 | 2708075.2392 | 1234668.2635
15 | 2708131.3824 | 1234687.3544 | 2708131.6168 | 1234681.9394
16 | 2708055.0971 | 1234668.2027 | 2708061.9954 | 1234668.6334 | 2708075.2392 | 1234668.2635
17 | 2707966.063 | 1234784.2248 | 2707969.4894 | 1234774.2443 | 2707970.337 | 1234772.7316
18 | 2707978.6364 | 1234757.9201 | 2707970.337 | 1234772.7316
19 | 2708131.3824 | 1234687.3544 | 2708126.9816 | 1234687.0518
20 | 2708131.3824 | 1234687.3544 | 2708175.7127 | 1234690.1077 | 2708176.955 | 1234675.1077
21 | 2708131.3824 | 1234687.3544 | 2708130.9466 | 1234694.0565
22 | 2708169.7262 | 1234616.4309 | 2708169.083 | 1234630.1298 | 2708170.2306 | 1234635.288 | 2708176.6139 | 1234643.5439 | 2708179.4519 | 1234644.8521 | 2708178.2369 | 1234659.5969
23 | 2708169.7262 | 1234616.4309 | 2708179.3951 | 1234609.518
24 | 2708176.955 | 1234675.1077 | 2708178.2369 | 1234659.5969
25 | 2708170.536 | 1234659.2564 | 2708178.2369 | 1234659.5969
26 | 2708179.3951 | 1234609.518 | 2708186.303 | 1234604.5791 | 2708201.957 | 1234599.3268 | 2708231.24 | 1234594.2676
27 | 2708220.6553 | 1234653.0308 | 2708252.1775 | 1234657.3527
28 | 2708220.6553 | 1234653.0308 | 2708225.4016 | 1234648.9141 | 2708228.0079 | 1234639.2541 | 2708227.9796 | 1234634.1608
29 | 2708220.6553 | 1234653.0308 | 2708224.2158 | 1234669.108 | 2708224.2754 | 1234672.5435
30 | 2708252.1775 | 1234657.3527 | 2708282.1195 | 1234661.598
31 | 2708252.1775 | 1234657.3527 | 2708252.6924 | 1234680.3719
32 | 2708169.7603 | 1234674.8209 | 2708176.955 | 1234675.1077
33 | 2708174.9541 | 1234705.15 | 2708175.7127 | 1234690.1077 | 2708176.955 | 1234675.1077
34 | 2708130.3308 | 1234703.5255 | 2708130.9466 | 1234694.0565
35 | 2708249.4869 | 1234591.1151 | 2708231.24 | 1234594.2676
36 | 2708244.4715 | 1234551.5366 | 2708261.73 | 1234540.3589 | 2708271.055 | 1234536.0625
37 | 2708271.055 | 1234536.0625 | 2708318.0622 | 1234514.4046
38 | 2708282.1195 | 1234661.598 | 2708285.2979 | 1234662.0486 | 2708293.0634 | 1234662.2414
39 | 2708252.7781 | 1234684.2066 | 2708252.6924 | 1234680.3719
40 | 2708174.9541 | 1234705.15 | 2708168.2237 | 1234704.7271
41 | 2708167.4403 | 1234720.3026 | 2708174.3089 | 1234720.6168 | 2708174.9541 | 1234705.15
42 | 2708310.8196 | 1234662.6821 | 2708293.0634 | 1234662.2414
43 | 2708130.3308 | 1234703.5255 | 2708125.9886 | 1234703.3352
44 | 2708125.0086 | 1234719.3186 | 2708129.3042 | 1234719.5747 | 2708130.3308 | 1234703.5255
45 | 2708249.4869 | 1234591.1151 | 2708292.3871 | 1234583.7033
46 | 2708292.3871 | 1234583.7033 | 2708306.0139 | 1234581.349
47 | 2708344.9392 | 1234574.6239 | 2708306.0139 | 1234581.349
48 | 2708310.8196 | 1234662.6821 | 2708320.7742 | 1234662.9292 | 2708332.0512 | 1234660.2716
49 | 2708338.9425 | 1234658.6475 | 2708332.0512 | 1234660.2716
50 | 2708338.9425 | 1234658.6475 | 2708340.8679 | 1234658.1937
51 | 2708349.5463 | 1234656.1485 | 2708340.8679 | 1234658.1937
52 | 2708349.5463 | 1234656.1485 | 2708348.9334 | 1234645.3401 | 2708347.5951 | 1234621.6458
53 | 2708390.5164 | 1234648.0561 | 2708385.4179 | 1234649.0638 | 2708349.5463 | 1234656.1485
54 | 2708347.5951 | 1234621.6458 | 2708346.5029 | 1234602.3081
55 | 2708390.5164 | 1234648.0561 | 2708395.9414 | 1234669.3937
56 | 2708390.5164 | 1234648.0561 | 2708392.8178 | 1234647.6015
57 | 2708346.1207 | 1234595.5431 | 2708346.5029 | 1234602.3081
58 | 2708395.9414 | 1234669.3937 | 2708409.2876 | 1234857.9395
59 | 2708392.8178 | 1234647.6015 | 2708401.8531 | 1234645.8167 | 2708414.0973 | 1234642.8044 | 2708422.0427 | 1234650.0772 | 2708426.2797 | 1234653.9575 | 2708426.2797 | 1234653.9575
60 | 2708344.9392 | 1234574.6239 | 2708346.1207 | 1234595.5431
61 | 2708423.5665 | 1234860.6605 | 2708409.2876 | 1234857.9395
62 | 2708426.2797 | 1234653.9575 | 2708438.952 | 1234660.6716 | 2708442.4442 | 1234664.3664
63 | 2708447.3152 | 1234669.52 | 2708442.4442 | 1234664.3664
64 | 2708468.2909 | 1234895.5771 | 2708462.5585 | 1234881.1502 | 2708457.5095 | 1234871.9954 | 2708443.9352 | 1234864.542 | 2708423.5665 | 1234860.6605
65 | 2708468.2909 | 1234895.5771 | 2708469.4633 | 1234898.5341 | 2708486.3242 | 1234912.9753 | 2708487.77 | 1234914.2021
66 | 2708468.2909 | 1234895.5771 | 2708490.7658 | 1234892.3849 | 2708504.4471 | 1234892.2494
67 | 2708344.9392 | 1234574.6239 | 2708345.9468 | 1234557.6543
68 | 2708344.9392 | 1234574.6239 | 2708360.3365 | 1234576.3884
69 | 2708345.9468 | 1234557.6543 | 2708346.3381 | 1234551.0646 | 2708349.5594 | 1234542.5724 | 2708363.354 | 1234538.4128
70 | 2708360.3365 | 1234576.3884 | 2708376.0451 | 1234578.1886
71 | 2708383.8101 | 1234532.2445 | 2708363.354 | 1234538.4128
72 | 2708388.9214 | 1234579.6642 | 2708376.0451 | 1234578.1886
73 | 2708318.0622 | 1234514.4046 | 2708321.7658 | 1234512.6983 | 2708345.258 | 1234502.1415
74 | 2708373.6053 | 1234496.5087 | 2708355.8655 | 1234497.3748 | 2708345.258 | 1234502.1415
75 | 2708373.6053 | 1234496.5087 | 2708377.1543 | 1234508.9368
76 | 2708373.6053 | 1234496.5087 | 2708372.915 | 1234494.0942 | 2708369.1341 | 1234481.3933 | 2708397.8078 | 1234468.4396
77 | 2708265.7087 | 1234530.5905 | 2708281.3347 | 1234521.913 | 2708324.456 | 1234501.7722 | 2708369.1341 | 1234481.3933 | 2708372.915 | 1234494.0942 | 2708373.6053 | 1234496.5087
78 | 2708383.8101 | 1234532.2445 | 2708377.1543 | 1234508.9368
79 | 2708375.8925 | 1234444.199 | 2708394.7615 | 1234462.7797 | 2708397.8078 | 1234468.4396
80 | 2708397.8078 | 1234468.4396 | 2708436.6224 | 1234450.9151
81 | 2708265.7087 | 1234530.5905 | 2708262.0497 | 1234522.4064 | 2708260.8943 | 1234520.584 | 2708259.1846 | 1234519.2629 | 2708257.1297 | 1234518.6028 | 2708254.9708 | 1234518.6635 | 2708252.9577 | 1234519.4496 | 2708251.4504 | 1234520.7343 | 2708250.4127 | 1234522.4167 | 2708249.9536 | 1234524.3431 | 2708250.1221 | 1234526.3144 | 2708250.0987 | 1234528.0153 | 2708249.5772 | 1234529.6292 | 2708248.5978 | 1234531.0236 | 2708247.1162 | 1234532.1419 | 2708245.3567 | 1234532.7214 | 2708243.5018 | 1234532.7209
82 | 2708397.6822 | 1234580.6682 | 2708388.9214 | 1234579.6642
83 | 2708481.0336 | 1234441.304 | 2708472.3772 | 1234445.71
84 | 2708481.0336 | 1234441.304 | 2708484.1882 | 1234446.8325 | 2708492.2649 | 1234449.4153 | 2708501.5786 | 1234450.5973 | 2708505.5581 | 1234450.7141
85 | 2708481.0336 | 1234441.304 | 2708476.0652 | 1234433.107
86 | 2708375.8925 | 1234444.199 | 2708392.8882 | 1234423.1372
87 | 2708476.0652 | 1234433.107 | 2708436.6224 | 1234450.9151
88 | 2708519.6489 | 1234451.1277 | 2708505.5581 | 1234450.7141
89 | 2708392.8882 | 1234423.1372 | 2708384.5979 | 1234416.5371
90 | 2708372.0066 | 1234406.5128 | 2708384.5979 | 1234416.5371
91 | 2708397.6822 | 1234580.6682 | 2708408.3409 | 1234586.9564 | 2708412.2609 | 1234586.9676
92 | 2708447.1179 | 1234587.0672 | 2708412.2609 | 1234586.9676
93 | 2708562.0226 | 1234495.1467 | 2708539.7576 | 1234502.9237 | 2708537.499 | 1234503.4691
94 | 2708562.0226 | 1234495.1467 | 2708570.0531 | 1234503.5665 | 2708581.893 | 1234515.6477
95 | 2708447.1179 | 1234587.0672 | 2708448.0488 | 1234587.0698 | 2708449.992 | 1234586.5696
96 | 2708581.893 | 1234515.6477 | 2708583.4873 | 1234515.8214 | 2708602.0636 | 1234531.947
97 | 2708616.6198 | 1234557.9705 | 2708616.6198 | 1234557.9705 | 2708615.9673 | 1234555.1453 | 2708619.7054 | 1234549.4648 | 2708618.7642 | 1234545.4556 | 2708603.9527 | 1234533.5868 | 2708602.0636 | 1234531.947
98 | 2708614.3765 | 1234584.5325 | 2708615.9614 | 1234575.7499 | 2708622.9815 | 1234562.8238 | 2708616.6198 | 1234557.9705
99 | 2708510.5031 | 1234584.6687 | 2708511.7884 | 1234584.9202
100 | 2708510.5031 | 1234584.6687 | 2708491.6956 | 1234580.9895
101 | 2708511.7884 | 1234584.9202 | 2708518.6479 | 1234586.2621
102 | 2708491.6956 | 1234580.9895 | 2708480.3168 | 1234578.7635 | 2708480.3168 | 1234578.7635
103 | 2708518.6479 | 1234586.2621 | 2708528.4305 | 1234588.1758
104 | 2708467.9562 | 1234581.9453 | 2708480.3168 | 1234578.7635
105 | 2708548.9213 | 1234590.4672 | 2708534.3624 | 1234589.3362 | 2708528.4305 | 1234588.1758
106 | 2708467.9562 | 1234581.9453 | 2708449.992 | 1234586.5696
107 | 2708548.9213 | 1234590.4672 | 2708549.0653 | 1234590.4784
108 | 2708720.4339 | 1234601.2424 | 2708744.4201 | 1234588.9316 | 2708747.5559 | 1234585.4714
109 | 2708671.1885 | 1234608.0533 | 2708676.5251 | 1234608.6826 | 2708717.288 | 1234602.857 | 2708720.4339 | 1234601.2424
110 | 2708775.1283 | 1234563.3252 | 2708761.6286 | 1234569.943 | 2708747.5559 | 1234585.4714
111 | 2708671.1885 | 1234608.0533 | 2708647.8618 | 1234605.3027
112 | 2708642.7027 | 1234604.6944 | 2708647.8618 | 1234605.3027
113 | 2708642.7027 | 1234604.6944 | 2708630.022 | 1234598.6183
114 | 2708642.7027 | 1234604.6944 | 2708650.1229 | 1234625.3484
115 | 2708630.022 | 1234598.6183 | 2708628.3106 | 1234597.7982
116 | 2708650.5941 | 1234626.6599 | 2708650.1229 | 1234625.3484
117 | 2708549.0653 | 1234590.4784 | 2708554.0897 | 1234590.8687
118 | 2708575.5758 | 1234592.5378 | 2708554.0897 | 1234590.8687
119 | 2708575.5758 | 1234592.5378 | 2708575.7322 | 1234592.55 | 2708583.7207 | 1234592.3915
120 | 2708583.7207 | 1234592.3915 | 2708584.0953 | 1234592.384
121 | 2708584.0953 | 1234592.384 | 2708592.4421 | 1234592.2185
122 | 2708592.4421 | 1234592.2185 | 2708592.9638 | 1234592.2081
123 | 2708598.0822 | 1234592.1066 | 2708592.9638 | 1234592.2081
124 | 2708613.0633 | 1234591.8093 | 2708598.0822 | 1234592.1066
125 | 2708613.0633 | 1234591.8093 | 2708614.3765 | 1234584.5325
126 | 2708613.0633 | 1234591.8093 | 2708618.551 | 1234593.1218 | 2708620.4802 | 1234594.0462
127 | 2708650.5941 | 1234626.6599 | 2708650.9952 | 1234627.7766
128 | 2708650.9952 | 1234627.7766 | 2708655.5501 | 1234640.4549
129 | 2708620.4802 | 1234594.0462 | 2708628.3106 | 1234597.7982

## bus_geodata
| x | y | coords
0 | 2707940.5388 | 1234649.5285
1 | 2707973.7464 | 1234643.4525
2 | 2707896.036 | 1234735.031
3 | 2708006.3388 | 1234636.33
4 | 2707933.8983 | 1234796.8385
5 | 2707928.6731 | 1234796.1805
6 | 2707962.472 | 1234800.4369
7 | 2707908.5867 | 1234793.6509
8 | 2707892.0967 | 1234791.5742
9 | 2708018.315 | 1234659.7022
10 | 2708032.2657 | 1234665.8772
11 | 2708132.4277 | 1234663.2104
12 | 2708131.6168 | 1234681.9394
13 | 2708075.2392 | 1234668.2635
14 | 2708055.0971 | 1234668.2027
15 | 2707966.063 | 1234784.2248
16 | 2707970.337 | 1234772.7316
17 | 2707978.6364 | 1234757.9201
18 | 2708015.1317 | 1234803.0335
19 | 2708131.3824 | 1234687.3544
20 | 2708169.7262 | 1234616.4309
21 | 2708178.2369 | 1234659.5969
22 | 2708179.3951 | 1234609.518
23 | 2708220.6553 | 1234653.0308
24 | 2708252.1775 | 1234657.3527
25 | 2708227.9796 | 1234634.1608
26 | 2708224.2754 | 1234672.5435
27 | 2708176.955 | 1234675.1077
28 | 2708170.536 | 1234659.2564
29 | 2708126.9816 | 1234687.0518
30 | 2708130.9466 | 1234694.0565
31 | 2708231.24 | 1234594.2676
32 | 2708244.4715 | 1234551.5366
33 | 2708271.055 | 1234536.0625
34 | 2708282.1195 | 1234661.598
35 | 2708252.6924 | 1234680.3719
36 | 2708169.7603 | 1234674.8209
37 | 2708174.9541 | 1234705.15
38 | 2708168.2237 | 1234704.7271
39 | 2708167.4403 | 1234720.3026
40 | 2708293.0634 | 1234662.2414
41 | 2708252.7781 | 1234684.2066
42 | 2708130.3308 | 1234703.5255
43 | 2708249.4869 | 1234591.1151
44 | 2708292.3871 | 1234583.7033
45 | 2708306.0139 | 1234581.349
46 | 2708310.8196 | 1234662.6821
47 | 2708332.0512 | 1234660.2716
48 | 2708338.9425 | 1234658.6475
49 | 2708340.8679 | 1234658.1937
50 | 2708349.5463 | 1234656.1485
51 | 2708347.5951 | 1234621.6458
52 | 2708390.5164 | 1234648.0561
53 | 2708346.5029 | 1234602.3081
54 | 2708395.9414 | 1234669.3937
55 | 2708392.8178 | 1234647.6015
56 | 2708346.1207 | 1234595.5431
57 | 2708409.2876 | 1234857.9395
58 | 2708426.2797 | 1234653.9575
59 | 2708442.4442 | 1234664.3664
60 | 2708447.3152 | 1234669.52
61 | 2708423.5665 | 1234860.6605
62 | 2708468.2909 | 1234895.5771
63 | 2708487.77 | 1234914.2021
64 | 2708504.4472 | 1234892.2494
65 | 2708344.9392 | 1234574.6239
66 | 2708345.9468 | 1234557.6543
67 | 2708360.3365 | 1234576.3884
68 | 2708363.354 | 1234538.4128
69 | 2708376.0451 | 1234578.1886
70 | 2708318.0622 | 1234514.4046
71 | 2708345.258 | 1234502.1415
72 | 2708373.6053 | 1234496.5087
73 | 2708377.1543 | 1234508.9368
74 | 2708397.8078 | 1234468.4396
75 | 2708265.7087 | 1234530.5905
76 | 2708383.8101 | 1234532.2445
77 | 2708388.9214 | 1234579.6642
78 | 2708472.3772 | 1234445.71
79 | 2708481.0336 | 1234441.304
80 | 2708375.8925 | 1234444.199
81 | 2708436.6224 | 1234450.9151
82 | 2708243.5018 | 1234532.7209
83 | 2708505.5581 | 1234450.7141
84 | 2708476.0652 | 1234433.107
85 | 2708392.8882 | 1234423.1372
86 | 2708384.5979 | 1234416.5371
87 | 2708397.6822 | 1234580.6682
88 | 2708412.2609 | 1234586.9676
89 | 2708537.499 | 1234503.4691
90 | 2708562.0226 | 1234495.1467
91 | 2708447.1179 | 1234587.0672
92 | 2708125.0086 | 1234719.3186
93 | 2708372.0066 | 1234406.5128
94 | 2708519.6489 | 1234451.1277
95 | 2708581.893 | 1234515.6477
96 | 2708602.0636 | 1234531.947
97 | 2708616.6198 | 1234557.9705
98 | 2708510.5031 | 1234584.6687
99 | 2708511.7884 | 1234584.9202
100 | 2708491.6956 | 1234580.9895
101 | 2708518.6479 | 1234586.2621
102 | 2708480.3168 | 1234578.7635
103 | 2708528.4305 | 1234588.1758
104 | 2708467.9562 | 1234581.9453
105 | 2708548.9213 | 1234590.4672
106 | 2708449.992 | 1234586.5696
107 | 2708720.4339 | 1234601.2424
108 | 2708747.5559 | 1234585.4714
109 | 2708671.1885 | 1234608.0533
110 | 2708775.1283 | 1234563.3252
111 | 2708647.8618 | 1234605.3027
112 | 2708642.7027 | 1234604.6944
113 | 2708630.022 | 1234598.6183
114 | 2708650.1229 | 1234625.3484
115 | 2708549.0653 | 1234590.4784
116 | 2708554.0897 | 1234590.8687
117 | 2708575.5758 | 1234592.5378
118 | 2708583.7207 | 1234592.3915
119 | 2708584.0953 | 1234592.384
120 | 2708592.4421 | 1234592.2185
121 | 2708592.9638 | 1234592.2081
122 | 2708598.0822 | 1234592.1066
123 | 2708613.0633 | 1234591.8093
124 | 2708650.5941 | 1234626.6599
125 | 2708650.9952 | 1234627.7766
126 | 2708655.5501 | 1234640.4549
127 | 2708628.3106 | 1234597.7982
128 | 2708614.3765 | 1234584.5325
129 | 2708620.4802 | 1234594.0462
130 | 2708125.9886 | 1234703.3352
131 | 2708282.1195 | 1234661.598

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97382 | -0.50495 | 0.016076 | 0.0040289
1 | 0.97485 | -0.48463 | 0.015409 | 0.003862
2 | 0.97232 | -0.53457 | 0.0027588 | 0.00069141
3 | 0.97635 | -0.45519 | 0 | 0
4 | 0.97107 | -0.55933 | 0.0012217 | 0.0003062
5 | 0.97112 | -0.55822 | 0.0013959 | 0.00034984
6 | 0.97079 | -0.56477 | 0 | 0
7 | 0.97137 | -0.55342 | 0.0011103 | 0.00027827
8 | 0.97158 | -0.54915 | 0 | 0
9 | 0.97696 | -0.44333 | 0.015654 | 0.0039233
10 | 0.97714 | -0.43971 | 0.018811 | 0.0047146
11 | 0.97916 | -0.40018 | 0 | 0
12 | 0.97958 | -0.39199 | 0.0018482 | 0.00046319
13 | 0.97787 | -0.42532 | 0.018934 | 0.0047453
14 | 0.97749 | -0.43277 | 0.018576 | 0.0046555
15 | 0.97066 | -0.56735 | 0.0023184 | 0.00058104
16 | 0.97059 | -0.56872 | 0.0035886 | 0.00089939
17 | 0.97056 | -0.5695 | 0.0024631 | 0.00061731
18 | 0.9707 | -0.56655 | 0.0018315 | 0.00045902
19 | 0.9797 | -0.38959 | 0 | 0
20 | 0.98321 | -0.32109 | 0 | 0
21 | 0.98173 | -0.34993 | 0 | 0
22 | 0.98359 | -0.31387 | 0.0071993 | 0.0018043
23 | 0.9979 | -0.040412 | 0 | 0
24 | 0.99847 | -0.029447 | 0.010133 | 0.0025396
25 | 0.99768 | -0.04466 | 0.011352 | 0.002845
26 | 0.99775 | -0.043341 | 0.0084044 | 0.0021063
27 | 0.98127 | -0.35899 | 0 | 0
28 | 0.98168 | -0.35102 | 0.0078024 | 0.0019555
29 | 0.97967 | -0.39019 | 0.0075081 | 0.0018817
30 | 0.97962 | -0.3911 | 0.001847 | 0.00046289
31 | 0.98537 | -0.27926 | 0.0039285 | 0.00098457
32 | 0.98472 | -0.29258 | 0.0050398 | 0.0012631
33 | 0.98486 | -0.28979 | 0.0027669 | 0.00069346
34 | 1 | 0 | -0.50846 | -0.12991
35 | 0.99793 | -0.039875 | 0.011907 | 0.0029842
36 | 0.98121 | -0.36002 | 0.007926 | 0.0019864
37 | 0.98096 | -0.36499 | 0 | 0
38 | 0.98093 | -0.36565 | 0.005455 | 0.0013671
39 | 0.98085 | -0.36723 | 0.00554 | 0.0013885
40 | 0.9991 | -0.016992 | 0.011112 | 0.0027849
41 | 0.99788 | -0.040813 | 0.013982 | 0.0035042
42 | 0.97953 | -0.39291 | 0 | 0
43 | 0.98599 | -0.26731 | 0.0099313 | 0.002489
44 | 0.98752 | -0.23774 | 0.0050155 | 0.001257
45 | 0.98802 | -0.22812 | 0.0024811 | 0.00062183
46 | 0.99768 | -0.043856 | 0.0045438 | 0.0011388
47 | 0.99597 | -0.0762 | 0.0063833 | 0.0015998
48 | 0.99542 | -0.086694 | 0.014118 | 0.0035383
49 | 0.99527 | -0.08953 | 0.0065541 | 0.0016426
50 | 0.99461 | -0.10212 | 0 | 0
51 | 0.99238 | -0.14454 | 0.0079809 | 0.0020002
52 | 0.99258 | -0.1413 | 0 | 0
53 | 0.99116 | -0.16785 | 0.0084664 | 0.0021219
54 | 0.99191 | -0.15419 | 0.012565 | 0.0031492
55 | 0.99253 | -0.14214 | 0.0060801 | 0.0015238
56 | 0.99075 | -0.17582 | 0.0019693 | 0.00049357
57 | 0.98835 | -0.22311 | 0.0019847 | 0.0004974
58 | 0.99204 | -0.15173 | 0.0035382 | 0.00088675
59 | 0.99185 | -0.15538 | 0.0045915 | 0.0011507
60 | 0.99181 | -0.15613 | 0.0060046 | 0.0015049
61 | 0.98811 | -0.22791 | 0.0042777 | 0.0010721
62 | 0.98729 | -0.24374 | 0.011979 | 0.0030022
63 | 0.98725 | -0.24447 | 0.0014935 | 0.00037429
64 | 0.98727 | -0.24424 | 0.00076565 | 0.00019189
65 | 0.98947 | -0.20034 | 0 | 0
66 | 0.98884 | -0.2125 | 0.0013634 | 0.00034171
67 | 0.9892 | -0.20541 | 0.00059529 | 0.00014919
68 | 0.98776 | -0.23333 | 0.00073399 | 0.00018396
69 | 0.98853 | -0.21825 | 0.00069754 | 0.00017482
70 | 0.98523 | -0.28253 | 0.0006785 | 0.00017005
71 | 0.98547 | -0.27798 | 0.0009241 | 0.0002316
72 | 0.98572 | -0.27302 | 0 | 0
73 | 0.98616 | -0.26439 | 0.0008469 | 0.00021225
74 | 0.98463 | -0.29416 | 0 | 0
75 | 0.98538 | -0.27972 | 0 | 0
76 | 0.98701 | -0.24787 | 0 | 0
77 | 0.98744 | -0.23919 | 0.0013402 | 0.0003359
78 | 0.98322 | -0.32183 | 0.0048033 | 0.0012038
79 | 0.98326 | -0.32099 | 0 | 0
80 | 0.98436 | -0.29945 | 0 | 0
81 | 0.98401 | -0.30642 | 0.00068991 | 0.00017291
82 | 0.98528 | -0.28169 | 0.002862 | 0.00071729
83 | 0.98299 | -0.32633 | 0.0019154 | 0.00048005
84 | 0.9834 | -0.31835 | 0 | 0
85 | 0.98414 | -0.30379 | 0 | 0
86 | 0.98405 | -0.30549 | 0.0040527 | 0.0010157
87 | 0.98671 | -0.25325 | 0 | 0
88 | 0.98535 | -0.27929 | 0.0017142 | 0.00042962
89 | 0.97199 | -0.54036 | 0.0019747 | 0.0004949
90 | 0.97204 | -0.53941 | 0 | 0
91 | 0.98252 | -0.33415 | 0.0012288 | 0.00030797
92 | 0.97943 | -0.39485 | 0.0052461 | 0.0013148
93 | 0.98398 | -0.30691 | 0.0048763 | 0.0012221
94 | 0.98288 | -0.32852 | 0.0085847 | 0.0021515
95 | 0.97209 | -0.53837 | 0 | 0
96 | 0.97214 | -0.53742 | 0.0039681 | 0.0009945
97 | 0.97233 | -0.53355 | 0.0023198 | 0.0005814
98 | 0.97759 | -0.43011 | 0.0026123 | 0.0006547
99 | 0.9775 | -0.43194 | 0.0056858 | 0.001425
100 | 0.979 | -0.40249 | 0.00050987 | 0.00012779
101 | 0.97704 | -0.44097 | 0.0044263 | 0.0011093
102 | 0.97986 | -0.38572 | 0.0012312 | 0.00030858
103 | 0.97642 | -0.45307 | 0.0022203 | 0.00055645
104 | 0.98082 | -0.367 | 0.0033898 | 0.00084957
105 | 0.97519 | -0.47732 | 0.0079428 | 0.0019906
106 | 0.98228 | -0.33872 | 0.0019324 | 0.0004843
107 | 0.97103 | -0.55929 | 0.0037452 | 0.00093864
108 | 0.9708 | -0.56387 | 0.0030175 | 0.00075627
109 | 0.97157 | -0.54859 | 0.0021104 | 0.00052892
110 | 0.97064 | -0.56706 | 0.0048025 | 0.0012036
111 | 0.97187 | -0.54266 | 0.00076234 | 0.00019106
112 | 0.97194 | -0.54127 | 0 | 0
113 | 0.97222 | -0.53575 | 0.0010203 | 0.00025572
114 | 0.9718 | -0.54405 | 0.0011157 | 0.00027961
115 | 0.97518 | -0.47747 | 0.0074038 | 0.0018556
116 | 0.97495 | -0.48198 | 0.0014655 | 0.00036728
117 | 0.974 | -0.50072 | 0.0021523 | 0.00053942
118 | 0.97365 | -0.50749 | 0.0021211 | 0.0005316
119 | 0.97364 | -0.50779 | 0.0023471 | 0.00058824
120 | 0.97332 | -0.51404 | 0.0020128 | 0.00050446
121 | 0.9733 | -0.51441 | 0.0018077 | 0.00045305
122 | 0.97313 | -0.51789 | 0.0022796 | 0.00057132
123 | 0.97264 | -0.52745 | 0 | 0
124 | 0.97179 | -0.5442 | 0.0011196 | 0.00028059
125 | 0.97179 | -0.5443 | 0.0010425 | 0.00026126
126 | 0.97174 | -0.54519 | 0.0035809 | 0.00089747
127 | 0.97226 | -0.53497 | 0.0019787 | 0.00049592
128 | 0.97258 | -0.52873 | 0.0011018 | 0.00027615
129 | 0.97246 | -0.53108 | 0.00097368 | 0.00024403
130 | 0.97951 | -0.39332 | 0.0052632 | 0.0013191
131 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.032808 | -0.0082356 | 0.03284 | 0.0082555 | 3.1823e-05 | 1.9946e-05 | 0.050136 | 0.050135 | 0.050136 | 0.97382 | -0.50495 | 0.97485 | -0.48463 | 13.7735
1 | 0.016732 | 0.0042067 | -0.016709 | -0.0041927 | 2.3638e-05 | 1.3931e-05 | 0.025572 | 0.025572 | 0.025572 | 0.97382 | -0.50495 | 0.97232 | -0.53457 | 7.0254
2 | -0.048249 | -0.012117 | 0.048317 | 0.012161 | 6.7873e-05 | 4.3022e-05 | 0.073656 | 0.073656 | 0.073656 | 0.97485 | -0.48463 | 0.97635 | -0.45519 | 20.2353
3 | 0.01395 | 0.0035013 | -0.01394 | -0.0034958 | 9.6891e-06 | 5.4985e-06 | 0.02135 | 0.021351 | 0.021351 | 0.97232 | -0.53457 | 0.97158 | -0.54915 | 5.8656
4 | -0.048317 | -0.012161 | 0.048344 | 0.012177 | 2.7403e-05 | 1.6864e-05 | 0.073656 | 0.073656 | 0.073656 | 0.97635 | -0.45519 | 0.97696 | -0.44333 | 10.1176
5 | -0.011428 | -0.0028641 | 0.011428 | 0.0028645 | 6.0559e-07 | 3.2242e-07 | 0.017511 | 0.017511 | 0.017511 | 0.97107 | -0.55933 | 0.97112 | -0.55822 | 4.8108
6 | 0.010206 | 0.0025579 | -0.010203 | -0.0025566 | 2.6414e-06 | 1.3343e-06 | 0.015639 | 0.015639 | 0.015639 | 0.97107 | -0.55933 | 0.97079 | -0.56477 | 4.2965
7 | -0.012824 | -0.0032143 | 0.012827 | 0.0032159 | 2.9314e-06 | 1.6255e-06 | 0.01965 | 0.01965 | 0.01965 | 0.97112 | -0.55822 | 0.97137 | -0.55342 | 5.3984
8 | 0.0018317 | 0.00045847 | -0.0018315 | -0.00045902 | 1.5583e-07 | -5.5209e-07 | 0.0028073 | 0.0028076 | 0.0028076 | 0.97079 | -0.56477 | 0.9707 | -0.56655 | 0.77131
9 | 0.0083716 | 0.0020981 | -0.0083706 | -0.0020977 | 1.0292e-06 | 4.5262e-07 | 0.012832 | 0.012832 | 0.012832 | 0.97079 | -0.56477 | 0.97066 | -0.56735 | 3.5253
10 | -0.013937 | -0.0034942 | 0.01394 | 0.0034958 | 2.8412e-06 | 1.6126e-06 | 0.021351 | 0.021351 | 0.021351 | 0.97137 | -0.55342 | 0.97158 | -0.54915 | 5.8656
11 | -0.063999 | -0.016101 | 0.06401 | 0.016107 | 1.11e-05 | 6.129e-06 | 0.097499 | 0.097499 | 0.097499 | 0.97696 | -0.44333 | 0.97714 | -0.43971 | 5.3571
12 | -0.082821 | -0.020821 | 0.082849 | 0.020838 | 2.7456e-05 | 1.6131e-05 | 0.12615 | 0.12614 | 0.12615 | 0.97714 | -0.43971 | 0.97749 | -0.43277 | 6.9311
13 | -0.12054 | -0.030349 | 0.12059 | 0.030378 | 4.7205e-05 | 2.9031e-05 | 0.18323 | 0.18323 | 0.18323 | 0.97916 | -0.40018 | 0.97958 | -0.39199 | 10.0677
14 | 0.12054 | 0.030349 | -0.12039 | -0.03026 | 0.0001447 | 8.9e-05 | 0.18323 | 0.18323 | 0.18323 | 0.97916 | -0.40018 | 0.97787 | -0.42532 | 10.0678
15 | -0.12243 | -0.030841 | 0.12245 | 0.03085 | 1.4069e-05 | 8.6632e-06 | 0.18604 | 0.18604 | 0.18604 | 0.97958 | -0.39199 | 0.9797 | -0.38959 | 10.2219
16 | 0.10146 | 0.025515 | -0.10142 | -0.025493 | 3.6056e-05 | 2.1812e-05 | 0.15442 | 0.15442 | 0.15442 | 0.97787 | -0.42532 | 0.97749 | -0.43277 | 8.4847
17 | 0.0060522 | 0.0015167 | -0.0060518 | -0.0015166 | 3.966e-07 | 1.0197e-07 | 0.0092779 | 0.009278 | 0.009278 | 0.97066 | -0.56735 | 0.97059 | -0.56872 | 2.5489
18 | 0.0024632 | 0.00061716 | -0.0024631 | -0.00061731 | 9.0794e-08 | -1.5172e-07 | 0.0037763 | 0.0037763 | 0.0037763 | 0.97059 | -0.56872 | 0.97056 | -0.5695 | 1.0375
19 | 0.0075083 | 0.0018818 | -0.0075081 | -0.0018817 | 2.1449e-07 | 8.1893e-08 | 0.011404 | 0.011404 | 0.011404 | 0.9797 | -0.38959 | 0.97967 | -0.39019 | 3.133
20 | -0.14232 | -0.03583 | 0.14252 | 0.035959 | 0.0002085 | 0.00012969 | 0.21621 | 0.21621 | 0.21621 | 0.9797 | -0.38959 | 0.98127 | -0.35899 | 11.8799
21 | 0.012359 | 0.0030978 | -0.012358 | -0.0030973 | 8.8745e-07 | 4.834e-07 | 0.018771 | 0.018771 | 0.018771 | 0.9797 | -0.38959 | 0.97962 | -0.3911 | 5.1569
22 | 0.16956 | 0.04285 | -0.16932 | -0.042703 | 0.0002341 | 0.00014682 | 0.25674 | 0.25674 | 0.25674 | 0.98321 | -0.32109 | 0.98173 | -0.34993 | 14.1065
23 | -0.16956 | -0.04285 | 0.16961 | 0.042886 | 5.8759e-05 | 3.6852e-05 | 0.25674 | 0.25674 | 0.25674 | 0.98321 | -0.32109 | 0.98359 | -0.31387 | 14.1064
24 | 0.16152 | 0.040747 | -0.16145 | -0.040703 | 7.0026e-05 | 4.3833e-05 | 0.24491 | 0.24491 | 0.24491 | 0.98173 | -0.34993 | 0.98127 | -0.35899 | 13.4567
25 | 0.0078028 | 0.0019556 | -0.0078024 | -0.0019555 | 4.0315e-07 | 1.6084e-07 | 0.011827 | 0.011827 | 0.011827 | 0.98173 | -0.34993 | 0.98168 | -0.35102 | 3.2491
26 | -0.17681 | -0.044691 | 0.17711 | 0.044875 | 0.00029395 | 0.00018465 | 0.26763 | 0.26763 | 0.26763 | 0.98359 | -0.31387 | 0.98537 | -0.27926 | 14.7048
27 | -0.01976 | -0.004953 | 0.01977 | 0.0049592 | 1.0329e-05 | 6.1956e-06 | 0.029465 | 0.029465 | 0.029465 | 0.9979 | -0.040412 | 0.99847 | -0.029447 | 8.0947
28 | 0.011354 | 0.0028462 | -0.011352 | -0.002845 | 2.2974e-06 | 1.1912e-06 | 0.016931 | 0.016931 | 0.016931 | 0.9979 | -0.040412 | 0.99768 | -0.04466 | 4.6513
29 | 0.0084056 | 0.0021068 | -0.0084044 | -0.0021063 | 1.1725e-06 | 4.9045e-07 | 0.012534 | 0.012534 | 0.012534 | 0.9979 | -0.040412 | 0.99775 | -0.043341 | 3.4434
30 | -0.055806 | -0.013996 | 0.055884 | 0.014045 | 7.8446e-05 | 4.9809e-05 | 0.083171 | 0.08317 | 0.083171 | 0.99847 | -0.029447 | 1 | 0 | 22.849
31 | 0.025902 | 0.0064967 | -0.02589 | -0.0064887 | 1.2868e-05 | 7.9343e-06 | 0.038604 | 0.038604 | 0.038604 | 0.99847 | -0.029447 | 0.99793 | -0.039875 | 10.6056
32 | 0.0079264 | 0.0019866 | -0.007926 | -0.0019864 | 3.8895e-07 | 1.5824e-07 | 0.01202 | 0.01202 | 0.01202 | 0.98127 | -0.35899 | 0.98121 | -0.36002 | 3.3022
33 | 0.010999 | 0.0027573 | -0.010996 | -0.0027557 | 3.1415e-06 | 1.6303e-06 | 0.016679 | 0.016679 | 0.016679 | 0.98127 | -0.35899 | 0.98096 | -0.36499 | 4.5822
34 | 0.010511 | 0.0026344 | -0.01051 | -0.002634 | 9.0705e-07 | 4.6105e-07 | 0.015966 | 0.015966 | 0.015966 | 0.97962 | -0.3911 | 0.97953 | -0.39291 | 4.3862
35 | -0.18104 | -0.04586 | 0.18114 | 0.045925 | 0.00010393 | 6.5335e-05 | 0.27356 | 0.27356 | 0.27356 | 0.98537 | -0.27926 | 0.98599 | -0.26731 | 15.0307
36 | -0.0050398 | -0.0012631 | 0.0050405 | 0.0012631 | 6.7051e-07 | 3.6878e-08 | 0.0076157 | 0.0076155 | 0.0076157 | 0.98472 | -0.29258 | 0.98486 | -0.28979 | 2.0922
37 | -0.0078074 | -0.0019566 | 0.0078101 | 0.0019577 | 2.7006e-06 | 1.0695e-06 | 0.011796 | 0.011796 | 0.011796 | 0.98486 | -0.28979 | 0.98523 | -0.28253 | 3.2407
38 | 0.45093 | 0.11586 | -0.45055 | -0.11562 | 0.00037181 | 0.00023724 | 0.672 | 0.672 | 0.672 | 1 | 0 | 0.9991 | -0.016992 | 36.9228
39 | 0.013983 | 0.0035046 | -0.013982 | -0.0035042 | 6.2527e-07 | 3.5006e-07 | 0.02085 | 0.02085 | 0.02085 | 0.99793 | -0.039875 | 0.99788 | -0.040813 | 5.728
40 | 0.0054551 | 0.0013672 | -0.005455 | -0.0013671 | 1.7266e-07 | 2.5616e-08 | 0.0082749 | 0.0082749 | 0.0082749 | 0.98096 | -0.36499 | 0.98093 | -0.36565 | 2.2733
41 | 0.0055406 | 0.0013885 | -0.00554 | -0.0013885 | 5.9173e-07 | 9.6719e-08 | 0.0084045 | 0.0084046 | 0.0084046 | 0.98096 | -0.36499 | 0.98085 | -0.36723 | 2.3089
42 | 0.43944 | 0.11284 | -0.43887 | -0.11247 | 0.00057229 | 0.00036511 | 0.65545 | 0.65545 | 0.65545 | 0.9991 | -0.016992 | 0.99768 | -0.043856 | 36.0135
43 | 0.0052633 | 0.0013191 | -0.0052632 | -0.0013191 | 1.039e-07 | 1.1943e-08 | 0.0079956 | 0.0079956 | 0.0079956 | 0.97953 | -0.39291 | 0.97951 | -0.39332 | 2.1966
44 | 0.0052466 | 0.0013149 | -0.0052461 | -0.0013148 | 4.8537e-07 | 5.4188e-08 | 0.0079702 | 0.0079703 | 0.0079703 | 0.97953 | -0.39291 | 0.97943 | -0.39485 | 2.1896
45 | -0.19107 | -0.048414 | 0.19134 | 0.048586 | 0.00027186 | 0.00017121 | 0.28855 | 0.28855 | 0.28855 | 0.98599 | -0.26731 | 0.98752 | -0.23774 | 15.8542
46 | -0.19636 | -0.049843 | 0.19645 | 0.0499 | 9.0934e-05 | 5.7313e-05 | 0.2961 | 0.2961 | 0.2961 | 0.98752 | -0.23774 | 0.98802 | -0.22812 | 16.2694
47 | -0.19893 | -0.050522 | 0.1992 | 0.05069 | 0.00026635 | 0.00016793 | 0.29984 | 0.29984 | 0.29984 | 0.98802 | -0.22812 | 0.98947 | -0.20034 | 16.4747
48 | 0.43433 | 0.11133 | -0.43365 | -0.1109 | 0.00067987 | 0.00043371 | 0.64867 | 0.64867 | 0.64867 | 0.99768 | -0.043856 | 0.99597 | -0.0762 | 35.6412
49 | 0.42726 | 0.1093 | -0.42705 | -0.10916 | 0.00021691 | 0.00013836 | 0.63913 | 0.63913 | 0.63913 | 0.99597 | -0.0762 | 0.99542 | -0.086694 | 35.1172
50 | 0.41293 | 0.10562 | -0.41287 | -0.10559 | 5.6668e-05 | 3.6139e-05 | 0.61803 | 0.61803 | 0.61803 | 0.99542 | -0.086694 | 0.99527 | -0.08953 | 33.9577
51 | 0.40632 | 0.10394 | -0.40607 | -0.10379 | 0.00024739 | 0.00015775 | 0.60823 | 0.60823 | 0.60823 | 0.99527 | -0.08953 | 0.99461 | -0.10212 | 33.4193
52 | 0.35258 | 0.090304 | -0.35185 | -0.089843 | 0.00072304 | 0.00046051 | 0.52817 | 0.52818 | 0.52818 | 0.99461 | -0.10212 | 0.99238 | -0.14454 | 29.0206
53 | 0.053493 | 0.013483 | -0.053393 | -0.01342 | 0.00010009 | 6.3518e-05 | 0.080057 | 0.080057 | 0.080057 | 0.99461 | -0.10212 | 0.99258 | -0.1413 | 21.9937
54 | 0.34387 | 0.087843 | -0.34349 | -0.087596 | 0.00038709 | 0.00024648 | 0.51621 | 0.51621 | 0.51621 | 0.99238 | -0.14454 | 0.99116 | -0.16785 | 28.3631
55 | 0.033169 | 0.0083486 | -0.033149 | -0.0083358 | 2.0423e-05 | 1.2786e-05 | 0.049738 | 0.049738 | 0.049738 | 0.99258 | -0.1413 | 0.99191 | -0.15419 | 13.6643
56 | 0.020224 | 0.0050713 | -0.020223 | -0.0050708 | 8.0867e-07 | 4.8723e-07 | 0.030319 | 0.030319 | 0.030319 | 0.99258 | -0.1413 | 0.99253 | -0.14214 | 8.3295
57 | 0.33502 | 0.085475 | -0.33489 | -0.085393 | 0.00012883 | 8.2015e-05 | 0.5035 | 0.5035 | 0.5035 | 0.99116 | -0.16785 | 0.99075 | -0.17582 | 27.6648
58 | 0.020583 | 0.0051866 | -0.020515 | -0.0051457 | 6.7627e-05 | 4.085e-05 | 0.030888 | 0.030889 | 0.030889 | 0.99191 | -0.15419 | 0.98835 | -0.22311 | 8.4859
59 | 0.014143 | 0.003547 | -0.014136 | -0.0035434 | 6.4636e-06 | 3.6415e-06 | 0.021204 | 0.021204 | 0.021204 | 0.99253 | -0.14214 | 0.99204 | -0.15173 | 5.8253
60 | 0.33292 | 0.084899 | -0.33253 | -0.084648 | 0.00039371 | 0.00025063 | 0.50054 | 0.50054 | 0.50054 | 0.99075 | -0.17582 | 0.98947 | -0.20034 | 27.5023
61 | 0.018531 | 0.0046483 | -0.018527 | -0.0046458 | 4.2433e-06 | 2.5295e-06 | 0.027901 | 0.027901 | 0.027901 | 0.98835 | -0.22311 | 0.98811 | -0.22791 | 7.665
62 | 0.010598 | 0.0026566 | -0.010596 | -0.0026557 | 1.8409e-06 | 9.274e-07 | 0.015897 | 0.015897 | 0.015897 | 0.99204 | -0.15173 | 0.99185 | -0.15538 | 4.3673
63 | 0.0060048 | 0.0015049 | -0.0060046 | -0.0015049 | 2.1582e-07 | 4.6603e-08 | 0.0090087 | 0.0090087 | 0.0090087 | 0.99185 | -0.15538 | 0.99181 | -0.15613 | 2.4749
64 | 0.014249 | 0.0035737 | -0.014238 | -0.0035676 | 1.0741e-05 | 6.078e-06 | 0.021459 | 0.021459 | 0.021459 | 0.98811 | -0.22791 | 0.98729 | -0.24374 | 5.8953
65 | 0.0014935 | 0.00037398 | -0.0014935 | -0.00037429 | 5.1825e-08 | -3.1564e-07 | 0.0022508 | 0.002251 | 0.002251 | 0.98729 | -0.24374 | 0.98725 | -0.24447 | 0.6184
66 | 0.00076567 | 0.00019144 | -0.00076565 | -0.00019189 | 1.8167e-08 | -4.5362e-07 | 0.0011538 | 0.001154 | 0.001154 | 0.98729 | -0.24374 | 0.98727 | -0.24424 | 0.31703
67 | 0.040335 | 0.010177 | -0.040311 | -0.010162 | 2.3474e-05 | 1.4805e-05 | 0.060682 | 0.060682 | 0.060682 | 0.98947 | -0.20034 | 0.98884 | -0.2125 | 16.6709
68 | 0.092995 | 0.023782 | -0.092972 | -0.023768 | 2.2789e-05 | 1.359e-05 | 0.14002 | 0.14002 | 0.14002 | 0.98947 | -0.20034 | 0.9892 | -0.20541 | 7.6935
69 | 0.038948 | 0.0098201 | -0.038909 | -0.0097957 | 3.8791e-05 | 2.4441e-05 | 0.05863 | 0.058631 | 0.058631 | 0.98884 | -0.2125 | 0.98776 | -0.23333 | 16.1073
70 | 0.092377 | 0.023619 | -0.092319 | -0.023583 | 5.7384e-05 | 3.632e-05 | 0.13913 | 0.13913 | 0.13913 | 0.9892 | -0.20541 | 0.98853 | -0.21825 | 19.1107
71 | 0.038175 | 0.0096117 | -0.038149 | -0.0095951 | 2.6513e-05 | 1.6695e-05 | 0.057525 | 0.057525 | 0.057525 | 0.98776 | -0.23333 | 0.98701 | -0.24787 | 15.8035
72 | 0.091622 | 0.023408 | -0.091529 | -0.023349 | 9.266e-05 | 5.9136e-05 | 0.13808 | 0.13808 | 0.13808 | 0.98853 | -0.21825 | 0.98744 | -0.23919 | 37.933
73 | -0.0084886 | -0.0021277 | 0.0084904 | 0.0021285 | 1.8388e-06 | 7.9684e-07 | 0.012821 | 0.01282 | 0.012821 | 0.98523 | -0.28253 | 0.98547 | -0.27798 | 3.5221
74 | -0.0094145 | -0.0023601 | 0.0094168 | 0.0023612 | 2.2273e-06 | 1.0509e-06 | 0.014216 | 0.014216 | 0.014216 | 0.98547 | -0.27798 | 0.98572 | -0.27302 | 3.9054
75 | -0.037256 | -0.0093542 | 0.037272 | 0.0093639 | 1.5334e-05 | 9.649e-06 | 0.056247 | 0.056247 | 0.056247 | 0.98572 | -0.27302 | 0.98616 | -0.26439 | 15.4525
76 | 0.024976 | 0.0062772 | -0.024951 | -0.0062616 | 2.5185e-05 | 1.5517e-05 | 0.03771 | 0.03771 | 0.03771 | 0.98572 | -0.27302 | 0.98463 | -0.29416 | 10.3599
77 | 0.0028632 | 0.00071589 | -0.0028623 | -0.00071697 | 9.1294e-07 | -1.0766e-06 | 0.0043216 | 0.0043222 | 0.0043222 | 0.98572 | -0.27302 | 0.98538 | -0.27972 | 1.1874
78 | -0.038119 | -0.0095761 | 0.038149 | 0.0095951 | 3.0079e-05 | 1.8941e-05 | 0.057525 | 0.057525 | 0.057525 | 0.98616 | -0.26439 | 0.98701 | -0.24787 | 15.8036
79 | 0.0089341 | 0.00224 | -0.0089319 | -0.002239 | 2.2498e-06 | 1.0214e-06 | 0.013502 | 0.013502 | 0.013502 | 0.98463 | -0.29416 | 0.98436 | -0.29945 | 3.7094
80 | 0.016017 | 0.0040216 | -0.016008 | -0.0040162 | 9.3592e-06 | 5.4486e-06 | 0.024208 | 0.024208 | 0.024208 | 0.98463 | -0.29416 | 0.98401 | -0.30642 | 6.6507
81 | 0.0028623 | 0.00071697 | -0.002862 | -0.00071729 | 2.683e-07 | -3.1608e-07 | 0.0043222 | 0.0043224 | 0.0043224 | 0.98538 | -0.27972 | 0.98528 | -0.28169 | 1.1875
82 | 0.090189 | 0.023013 | -0.090128 | -0.022974 | 6.1213e-05 | 3.9064e-05 | 0.13606 | 0.13606 | 0.13606 | 0.98744 | -0.23919 | 0.98671 | -0.25325 | 37.3781
83 | -0.0048033 | -0.0012038 | 0.0048035 | 0.0012038 | 1.9248e-07 | -8.8183e-12 | 0.0072693 | 0.0072693 | 0.0072693 | 0.98322 | -0.32183 | 0.98326 | -0.32099 | 1.9971
84 | 0.010504 | 0.0026333 | -0.010501 | -0.002632 | 2.6735e-06 | 1.3533e-06 | 0.015896 | 0.015896 | 0.015896 | 0.98326 | -0.32099 | 0.98299 | -0.32633 | 4.3671
85 | -0.015307 | -0.0038371 | 0.015309 | 0.0038383 | 1.9275e-06 | 1.1121e-06 | 0.023165 | 0.023165 | 0.023165 | 0.98326 | -0.32099 | 0.9834 | -0.31835 | 6.3641
86 | 0.0089319 | 0.002239 | -0.00893 | -0.0022381 | 1.8483e-06 | 8.3932e-07 | 0.013502 | 0.013502 | 0.013502 | 0.98436 | -0.29945 | 0.98414 | -0.30379 | 3.7094
87 | 0.015318 | 0.0038433 | -0.015309 | -0.0038383 | 8.7088e-06 | 5.0242e-06 | 0.023165 | 0.023165 | 0.023165 | 0.98401 | -0.30642 | 0.9834 | -0.31835 | 6.3641
88 | 0.0085856 | 0.0021519 | -0.0085847 | -0.0021515 | 8.9294e-07 | 3.928e-07 | 0.012997 | 0.012997 | 0.012997 | 0.98299 | -0.32633 | 0.98288 | -0.32852 | 3.5705
89 | 0.00893 | 0.0022381 | -0.0089293 | -0.0022378 | 7.2446e-07 | 3.2902e-07 | 0.013502 | 0.013502 | 0.013502 | 0.98414 | -0.30379 | 0.98405 | -0.30549 | 3.7094
90 | 0.0048767 | 0.0012221 | -0.0048763 | -0.0012221 | 3.2819e-07 | 5.591e-09 | 0.0073741 | 0.0073742 | 0.0073742 | 0.98405 | -0.30549 | 0.98398 | -0.30691 | 2.0259
91 | 0.090128 | 0.022974 | -0.090014 | -0.022902 | 0.00011312 | 7.2188e-05 | 0.13606 | 0.13606 | 0.13606 | 0.98671 | -0.25325 | 0.98535 | -0.27929 | 37.3782
92 | 0.0883 | 0.022472 | -0.088067 | -0.022324 | 0.00023285 | 0.00014858 | 0.13347 | 0.13347 | 0.13347 | 0.98535 | -0.27929 | 0.98252 | -0.33415 | 36.667
93 | -0.0019747 | -0.0004949 | 0.0019748 | 0.00049464 | 8.8783e-08 | -2.6431e-07 | 0.003023 | 0.0030229 | 0.003023 | 0.97199 | -0.54036 | 0.97204 | -0.53941 | 0.8305
94 | -0.0019748 | -0.00049464 | 0.0019749 | 0.00049434 | 9.7696e-08 | -2.9091e-07 | 0.0030229 | 0.0030228 | 0.0030229 | 0.97204 | -0.53941 | 0.97209 | -0.53837 | 0.83047
95 | 0.086839 | 0.022016 | -0.086819 | -0.022003 | 1.908e-05 | 1.2174e-05 | 0.13161 | 0.13161 | 0.13161 | 0.98252 | -0.33415 | 0.98228 | -0.33872 | 36.1558
96 | -0.0019749 | -0.00049434 | 0.001975 | 0.00049408 | 8.9779e-08 | -2.674e-07 | 0.0030228 | 0.0030227 | 0.0030228 | 0.97209 | -0.53837 | 0.97214 | -0.53742 | 0.83043
97 | -0.005943 | -0.0014886 | 0.0059441 | 0.0014888 | 1.0953e-06 | 2.6326e-07 | 0.0090965 | 0.0090963 | 0.0090965 | 0.97214 | -0.53742 | 0.97233 | -0.53355 | 2.499
98 | -0.008264 | -0.0020702 | 0.0082659 | 0.0020711 | 1.8973e-06 | 8.218e-07 | 0.012646 | 0.012646 | 0.012646 | 0.97233 | -0.53355 | 0.97258 | -0.52873 | 3.4743
99 | 0.076786 | 0.01935 | -0.07678 | -0.019346 | 6.7133e-06 | 4.2801e-06 | 0.11692 | 0.11692 | 0.11692 | 0.97759 | -0.43011 | 0.9775 | -0.43194 | 32.1199
100 | -0.079399 | -0.020005 | 0.079504 | 0.020072 | 0.00010503 | 6.6979e-05 | 0.12089 | 0.12089 | 0.12089 | 0.97759 | -0.43011 | 0.979 | -0.40249 | 33.2123
101 | 0.071094 | 0.017921 | -0.071063 | -0.017902 | 3.072e-05 | 1.9573e-05 | 0.10826 | 0.10826 | 0.10826 | 0.9775 | -0.43194 | 0.97704 | -0.44097 | 29.7421
102 | -0.080013 | -0.0202 | 0.080078 | 0.020241 | 6.4362e-05 | 4.1046e-05 | 0.12167 | 0.12167 | 0.12167 | 0.979 | -0.40249 | 0.97986 | -0.38572 | 33.4251
103 | 0.066637 | 0.016792 | -0.066598 | -0.016768 | 3.8525e-05 | 2.4531e-05 | 0.10152 | 0.10152 | 0.10152 | 0.97704 | -0.44097 | 0.97642 | -0.45307 | 27.8901
104 | -0.081309 | -0.02055 | 0.081382 | 0.020596 | 7.3046e-05 | 4.6589e-05 | 0.12354 | 0.12354 | 0.12354 | 0.97986 | -0.38572 | 0.98082 | -0.367 | 33.9388
105 | 0.064378 | 0.016211 | -0.064303 | -0.016164 | 7.4568e-05 | 4.7465e-05 | 0.098136 | 0.098136 | 0.098136 | 0.97642 | -0.45307 | 0.97519 | -0.47732 | 26.9606
106 | -0.084772 | -0.021446 | 0.084887 | 0.021519 | 0.00011518 | 7.3483e-05 | 0.12868 | 0.12868 | 0.12868 | 0.98082 | -0.367 | 0.98228 | -0.33872 | 35.3516
107 | 0.056361 | 0.014173 | -0.05636 | -0.014173 | 4.0096e-07 | 2.5481e-07 | 0.086017 | 0.086017 | 0.086017 | 0.97519 | -0.47732 | 0.97518 | -0.47747 | 23.631
108 | 0.0078225 | 0.0019606 | -0.0078208 | -0.0019599 | 1.7044e-06 | 6.9966e-07 | 0.011987 | 0.011987 | 0.011987 | 0.97103 | -0.55929 | 0.9708 | -0.56387 | 3.2932
109 | -0.011568 | -0.0028992 | 0.011574 | 0.0029024 | 5.9019e-06 | 3.1573e-06 | 0.017726 | 0.017726 | 0.017726 | 0.97103 | -0.55929 | 0.97157 | -0.54859 | 4.8699
110 | 0.0048032 | 0.0012036 | -0.0048025 | -0.0012036 | 7.3156e-07 | 2.3269e-08 | 0.0073622 | 0.0073624 | 0.0073624 | 0.9708 | -0.56387 | 0.97064 | -0.56706 | 2.0226
111 | -0.013684 | -0.0034313 | 0.013688 | 0.0034335 | 3.869e-06 | 2.1852e-06 | 0.020958 | 0.020958 | 0.020958 | 0.97157 | -0.54859 | 0.97187 | -0.54266 | 5.7578
112 | -0.01445 | -0.0036246 | 0.014451 | 0.0036251 | 9.5365e-07 | 5.4596e-07 | 0.022126 | 0.022126 | 0.022126 | 0.97187 | -0.54266 | 0.97194 | -0.54127 | 6.0785
113 | -0.021311 | -0.0053443 | 0.021317 | 0.0053477 | 5.6134e-06 | 3.4183e-06 | 0.032628 | 0.032628 | 0.032628 | 0.97194 | -0.54127 | 0.97222 | -0.53575 | 8.9636
114 | 0.0068597 | 0.0017192 | -0.0068588 | -0.0017189 | 9.0772e-07 | 3.0899e-07 | 0.010502 | 0.010502 | 0.010502 | 0.97194 | -0.54127 | 0.9718 | -0.54405 | 2.8852
115 | -0.022337 | -0.0056034 | 0.022338 | 0.0056039 | 8.3186e-07 | 5.0886e-07 | 0.034189 | 0.034189 | 0.034189 | 0.97222 | -0.53575 | 0.97226 | -0.53497 | 9.3926
116 | 0.0057432 | 0.0014393 | -0.0057431 | -0.0014393 | 4.0413e-08 | 8.5984e-09 | 0.0087939 | 0.0087939 | 0.0087939 | 0.9718 | -0.54405 | 0.97179 | -0.5442 | 2.4159
117 | 0.048956 | 0.012317 | -0.048946 | -0.012311 | 1.0551e-05 | 6.6897e-06 | 0.074719 | 0.074719 | 0.074719 | 0.97518 | -0.47747 | 0.97495 | -0.48198 | 20.5273
118 | 0.04748 | 0.011943 | -0.047438 | -0.011917 | 4.2459e-05 | 2.6905e-05 | 0.072483 | 0.072483 | 0.072483 | 0.97495 | -0.48198 | 0.974 | -0.50072 | 19.9129
119 | 0.045286 | 0.011377 | -0.045271 | -0.011368 | 1.4628e-05 | 9.2602e-06 | 0.069195 | 0.069195 | 0.069195 | 0.974 | -0.50072 | 0.97365 | -0.50749 | 19.0095
120 | 0.04315 | 0.010836 | -0.043149 | -0.010836 | 6.1116e-07 | 3.8648e-07 | 0.065953 | 0.065953 | 0.065953 | 0.97365 | -0.50749 | 0.97364 | -0.50779 | 18.119
121 | 0.040802 | 0.010248 | -0.04079 | -0.01024 | 1.2177e-05 | 7.6894e-06 | 0.062366 | 0.062366 | 0.062366 | 0.97364 | -0.50779 | 0.97332 | -0.51404 | 17.1335
122 | 0.038777 | 0.0097355 | -0.038777 | -0.009735 | 6.8783e-07 | 4.3372e-07 | 0.059289 | 0.059289 | 0.059289 | 0.97332 | -0.51404 | 0.9733 | -0.51441 | 16.2881
123 | 0.036969 | 0.009282 | -0.036963 | -0.0092781 | 6.1339e-06 | 3.8621e-06 | 0.056525 | 0.056525 | 0.056525 | 0.9733 | -0.51441 | 0.97313 | -0.51789 | 15.5289
124 | 0.034683 | 0.0087068 | -0.034667 | -0.0086969 | 1.5807e-05 | 9.9306e-06 | 0.053039 | 0.05304 | 0.05304 | 0.97313 | -0.51789 | 0.97264 | -0.52745 | 14.5713
125 | 0.0093683 | 0.0023475 | -0.0093677 | -0.0023472 | 5.6958e-07 | 2.7276e-07 | 0.014332 | 0.014332 | 0.014332 | 0.97264 | -0.52745 | 0.97258 | -0.52873 | 3.9374
126 | 0.025299 | 0.0063494 | -0.025295 | -0.0063467 | 4.3722e-06 | 2.7016e-06 | 0.038707 | 0.038707 | 0.038707 | 0.97264 | -0.52745 | 0.97246 | -0.53108 | 10.6339
127 | 0.0046236 | 0.0011587 | -0.0046235 | -0.0011587 | 2.2301e-08 | -4.2795e-10 | 0.0070796 | 0.0070796 | 0.0070796 | 0.97179 | -0.5442 | 0.97179 | -0.5443 | 1.9449
128 | 0.0035811 | 0.0008974 | -0.0035809 | -0.00089747 | 1.519e-07 | -6.9685e-08 | 0.0054834 | 0.0054834 | 0.0054834 | 0.97179 | -0.5443 | 0.97174 | -0.54519 | 1.5064
129 | -0.024316 | -0.0060999 | 0.024321 | 0.0061026 | 4.5101e-06 | 2.7788e-06 | 0.037218 | 0.037218 | 0.037218 | 0.97226 | -0.53497 | 0.97246 | -0.53108 | 10.2246

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.51784 | 0.13226

## res_load
| p_mw | q_mvar
0 | 0.016076 | 0.0040289
1 | 0.015409 | 0.003862
2 | 0.0027588 | 0.00069141
3 | 0.0012217 | 0.0003062
4 | 0.0013959 | 0.00034984
5 | 0.0011103 | 0.00027827
6 | 0.015654 | 0.0039233
7 | 0.018811 | 0.0047146
8 | 0.0018482 | 0.00046319
9 | 0.018934 | 0.0047453
10 | 0.018576 | 0.0046555
11 | 0.0023184 | 0.00058104
12 | 0.0035886 | 0.00089939
13 | 0.0024631 | 0.00061731
14 | 0.0018315 | 0.00045902
15 | 0.0071993 | 0.0018043
16 | 0.010133 | 0.0025396
17 | 0.011352 | 0.002845
18 | 0.0084044 | 0.0021063
19 | 0.0078024 | 0.0019555
20 | 0.0075081 | 0.0018817
21 | 0.001847 | 0.00046289
22 | 0.0039285 | 0.00098457
23 | 0.0050398 | 0.0012631
24 | 0.0027669 | 0.00069346
25 | 0.0093807 | 0.002351
26 | 0.011907 | 0.0029842
27 | 0.007926 | 0.0019864
28 | 0.005455 | 0.0013671
29 | 0.00554 | 0.0013885
30 | 0.011112 | 0.0027849
31 | 0.013982 | 0.0035042
32 | 0.0099313 | 0.002489
33 | 0.0050155 | 0.001257
34 | 0.0024811 | 0.00062183
35 | 0.0045438 | 0.0011388
36 | 0.0063833 | 0.0015998
37 | 0.014118 | 0.0035383
38 | 0.0065541 | 0.0016426
39 | 0.0079809 | 0.0020002
40 | 0.0084664 | 0.0021219
41 | 0.012565 | 0.0031492
42 | 0.0060801 | 0.0015238
43 | 0.0019693 | 0.00049357
44 | 0.0019847 | 0.0004974
45 | 0.0035382 | 0.00088675
46 | 0.0045915 | 0.0011507
47 | 0.0060046 | 0.0015049
48 | 0.0042777 | 0.0010721
49 | 0.011979 | 0.0030022
50 | 0.0014935 | 0.00037429
51 | 0.00076565 | 0.00019189
52 | 0.0013634 | 0.00034171
53 | 0.00059529 | 0.00014919
54 | 0.00073399 | 0.00018396
55 | 0.00069754 | 0.00017482
56 | 0.0006785 | 0.00017005
57 | 0.0009241 | 0.0002316
58 | 0.0008469 | 0.00021225
59 | 0.0013402 | 0.0003359
60 | 0.0048033 | 0.0012038
61 | 0.00068991 | 0.00017291
62 | 0.002862 | 0.00071729
63 | 0.0019154 | 0.00048005
64 | 0.0040527 | 0.0010157
65 | 0.0017142 | 0.00042962
66 | 0.0019747 | 0.0004949
67 | 0.0012288 | 0.00030797
68 | 0.0052461 | 0.0013148
69 | 0.0048763 | 0.0012221
70 | 0.0085847 | 0.0021515
71 | 0.0039681 | 0.0009945
72 | 0.0023198 | 0.0005814
73 | 0.0026123 | 0.0006547
74 | 0.0056858 | 0.001425
75 | 0.00050987 | 0.00012779
76 | 0.0044263 | 0.0011093
77 | 0.0012312 | 0.00030858
78 | 0.0022203 | 0.00055645
79 | 0.0033898 | 0.00084957
80 | 0.0079428 | 0.0019906
81 | 0.0019324 | 0.0004843
82 | 0.0037452 | 0.00093864
83 | 0.0030175 | 0.00075627
84 | 0.0021104 | 0.00052892
85 | 0.0048025 | 0.0012036
86 | 0.00076234 | 0.00019106
87 | 0.0010203 | 0.00025572
88 | 0.0011157 | 0.00027961
89 | 0.0074038 | 0.0018556
90 | 0.0014655 | 0.00036728
91 | 0.0021523 | 0.00053942
92 | 0.0021211 | 0.0005316
93 | 0.0023471 | 0.00058824
94 | 0.0020128 | 0.00050446
95 | 0.0018077 | 0.00045305
96 | 0.0022796 | 0.00057132
97 | 0.0011196 | 0.00028059
98 | 0.0010425 | 0.00026126
99 | 0.0035809 | 0.00089747
100 | 0.0019787 | 0.00049592
101 | 0.0011018 | 0.00027615
102 | 0.00097368 | 0.00024403
103 | 0.0052632 | 0.0013191

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1