## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_118-3_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_118-3_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_118-3_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_118-3_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_118-3_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_118-3_0_3_node_9 | 0.4 | n |  | TRUE
6 | bus_LV_118-3_0_3_node_18 | 0.4 | n |  | TRUE
7 | bus_LV_118-3_0_3_node_25 | 0.4 | n |  | TRUE
8 | bus_LV_118-3_0_3_node_26 | 0.4 | n |  | TRUE
9 | bus_LV_118-3_0_3_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_118-3_0_3_node_27 | 0.4 | n |  | TRUE
11 | bus_LV_118-3_0_3_node_16 | 0.4 | n |  | TRUE
12 | bus_LV_118-3_0_3_node_23 | 0.4 | n |  | TRUE
13 | bus_LV_118-3_0_3_node_5 | 0.4 | n |  | TRUE
14 | bus_LV_118-3_0_3_node_6 | 0.4 | n |  | TRUE
15 | bus_LV_118-3_0_3_node_7 | 0.4 | n |  | TRUE
16 | bus_LV_118-3_0_3_node_57 | 0.4 | n |  | TRUE
17 | bus_LV_118-3_0_3_node_55 | 0.4 | n |  | TRUE
18 | bus_LV_118-3_0_3_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_118-3_0_3_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_118-3_0_3_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_118-3_0_3_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_118-3_0_3_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_118-3_0_3_node_109 | 0.4 | n |  | TRUE
24 | bus_LV_118-3_0_3_node_108 | 0.4 | n |  | TRUE
25 | bus_LV_118-3_0_3_node_40 | 0.4 | n |  | TRUE
26 | bus_LV_118-3_0_3_node_110 | 0.4 | n |  | TRUE
27 | bus_LV_118-3_0_3_node_32 | 0.4 | n |  | TRUE
28 | bus_LV_118-3_0_3_node_33 | 0.4 | n |  | TRUE
29 | bus_LV_118-3_0_3_node_96 | 0.4 | n |  | TRUE
30 | bus_LV_118-3_0_3_node_34 | 0.4 | n |  | TRUE
31 | bus_LV_118-3_0_3_node_39 | 0.4 | n |  | TRUE
32 | bus_LV_118-3_0_3_node_115 | 0.4 | n |  | TRUE
33 | bus_LV_118-3_0_3_node_35 | 0.4 | n |  | TRUE
34 | bus_LV_118-3_0_3_node_116 | 0.4 | n |  | TRUE
35 | bus_LV_118-3_0_3_node_38 | 0.4 | n |  | TRUE
36 | bus_LV_118-3_0_3_node_111 | 0.4 | n |  | TRUE
37 | bus_LV_118-3_0_3_node_113 | 0.4 | n |  | TRUE
38 | bus_LV_118-3_0_3_node_19 | 0.4 | n |  | TRUE
39 | bus_LV_118-3_0_3_node_17 | 0.4 | n |  | TRUE
40 | bus_LV_118-3_0_3_node_29 | 0.4 | n |  | TRUE
41 | bus_LV_118-3_0_3_node_42 | 0.4 | n |  | TRUE
42 | bus_LV_118-3_0_3_node_67 | 0.4 | n |  | TRUE
43 | bus_LV_118-3_0_3_node_31 | 0.4 | n |  | TRUE
44 | bus_LV_118-3_0_3_node_66 | 0.4 | n |  | TRUE
45 | bus_LV_118-3_0_3_node_65 | 0.4 | n |  | TRUE
46 | bus_LV_118-3_0_3_node_36 | 0.4 | n |  | TRUE
47 | bus_LV_118-3_0_3_node_82 | 0.4 | n |  | TRUE
48 | bus_LV_118-3_0_3_node_71 | 0.4 | n |  | TRUE
49 | bus_LV_118-3_0_3_node_72 | 0.4 | n |  | TRUE
50 | bus_LV_118-3_0_3_node_73 | 0.4 | n |  | TRUE
51 | bus_LV_118-3_0_3_node_15 | 0.4 | n |  | TRUE
52 | bus_LV_118-3_0_3_node_20 | 0.4 | n |  | TRUE
53 | bus_LV_118-3_0_3_node_105 | 0.4 | n |  | TRUE
54 | bus_LV_118-3_0_3_node_103 | 0.4 | n |  | TRUE
55 | bus_LV_118-3_0_3_node_21 | 0.4 | n |  | TRUE
56 | bus_LV_118-3_0_3_node_22 | 0.4 | n |  | TRUE
57 | bus_LV_118-3_0_3_node_24 | 0.4 | n |  | TRUE
58 | bus_LV_118-3_0_3_node_86 | 0.4 | n |  | TRUE
59 | bus_LV_118-3_0_3_node_54 | 0.4 | n |  | TRUE
60 | bus_LV_118-3_0_3_node_68 | 0.4 | n |  | TRUE
61 | bus_LV_118-3_0_3_node_126 | 0.4 | n |  | TRUE
62 | bus_LV_118-3_0_3_node_127 | 0.4 | n |  | TRUE
63 | bus_LV_118-3_0_3_node_102 | 0.4 | n |  | TRUE
64 | bus_LV_118-3_0_3_node_101 | 0.4 | n |  | TRUE
65 | bus_LV_118-3_0_3_node_95 | 0.4 | n |  | TRUE
66 | bus_LV_118-3_0_3_node_80 | 0.4 | n |  | TRUE
67 | bus_LV_118-3_0_3_node_112 | 0.4 | n |  | TRUE
68 | bus_LV_118-3_0_3_node_114 | 0.4 | n |  | TRUE
69 | bus_LV_118-3_0_3_node_88 | 0.4 | n |  | TRUE
70 | bus_LV_118-3_0_3_node_69 | 0.4 | n |  | TRUE
71 | bus_LV_118-3_0_3_node_74 | 0.4 | n |  | TRUE
72 | bus_LV_118-3_0_3_node_43 | 0.4 | n |  | TRUE
73 | bus_LV_118-3_0_3_node_44 | 0.4 | n |  | TRUE
74 | bus_LV_118-3_0_3_node_45 | 0.4 | n |  | TRUE
75 | bus_LV_118-3_0_3_node_46 | 0.4 | n |  | TRUE
76 | bus_LV_118-3_0_3_node_47 | 0.4 | n |  | TRUE
77 | bus_LV_118-3_0_3_node_63 | 0.4 | n |  | TRUE
78 | bus_LV_118-3_0_3_node_52 | 0.4 | n |  | TRUE
79 | bus_LV_118-3_0_3_node_62 | 0.4 | n |  | TRUE
80 | bus_LV_118-3_0_3_node_87 | 0.4 | n |  | TRUE
81 | bus_LV_118-3_0_3_node_77 | 0.4 | n |  | TRUE
82 | bus_LV_118-3_0_3_node_85 | 0.4 | n |  | TRUE
83 | bus_LV_118-3_0_3_node_50 | 0.4 | n |  | TRUE
84 | bus_LV_118-3_0_3_node_60 | 0.4 | n |  | TRUE
85 | bus_LV_118-3_0_3_node_48 | 0.4 | n |  | TRUE
86 | bus_LV_118-3_0_3_node_49 | 0.4 | n |  | TRUE
87 | bus_LV_118-3_0_3_node_51 | 0.4 | n |  | TRUE
88 | bus_LV_118-3_0_3_node_53 | 0.4 | n |  | TRUE
89 | bus_LV_118-3_0_3_node_56 | 0.4 | n |  | TRUE
90 | bus_LV_118-3_0_3_node_58 | 0.4 | n |  | TRUE
91 | bus_LV_118-3_0_3_node_59 | 0.4 | n |  | TRUE
92 | bus_LV_118-3_0_3_node_61 | 0.4 | n |  | TRUE
93 | bus_LV_118-3_0_3_node_64 | 0.4 | n |  | TRUE
94 | bus_LV_118-3_0_3_node_84 | 0.4 | n |  | TRUE
95 | bus_LV_118-3_0_3_node_76 | 0.4 | n |  | TRUE
96 | bus_LV_118-3_0_3_node_121 | 0.4 | n |  | TRUE
97 | bus_LV_118-3_0_3_node_70 | 0.4 | n |  | TRUE
98 | bus_LV_118-3_0_3_node_89 | 0.4 | n |  | TRUE
99 | bus_LV_118-3_0_3_node_75 | 0.4 | n |  | TRUE
100 | bus_LV_118-3_0_3_node_83 | 0.4 | n |  | TRUE
101 | bus_LV_118-3_0_3_node_78 | 0.4 | n |  | TRUE
102 | bus_LV_118-3_0_3_node_79 | 0.4 | n |  | TRUE
103 | bus_LV_118-3_0_3_node_81 | 0.4 | n |  | TRUE
104 | bus_LV_118-3_0_3_node_90 | 0.4 | n |  | TRUE
105 | bus_LV_118-3_0_3_node_91 | 0.4 | n |  | TRUE
106 | bus_LV_118-3_0_3_node_92 | 0.4 | n |  | TRUE
107 | bus_LV_118-3_0_3_node_93 | 0.4 | n |  | TRUE
108 | bus_LV_118-3_0_3_node_94 | 0.4 | n |  | TRUE
109 | bus_LV_118-3_0_3_node_97 | 0.4 | n |  | TRUE
110 | bus_LV_118-3_0_3_node_98 | 0.4 | n |  | TRUE
111 | bus_LV_118-3_0_3_node_99 | 0.4 | n |  | TRUE
112 | bus_LV_118-3_0_3_node_100 | 0.4 | n |  | TRUE
113 | bus_LV_118-3_0_3_node_119 | 0.4 | n |  | TRUE
114 | bus_LV_118-3_0_3_node_104 | 0.4 | n |  | TRUE
115 | bus_LV_118-3_0_3_node_106 | 0.4 | n |  | TRUE
116 | bus_LV_118-3_0_3_node_107 | 0.4 | n |  | TRUE
117 | bus_LV_118-3_0_3_node_117 | 0.4 | n |  | TRUE
118 | bus_LV_118-3_0_3_node_118 | 0.4 | n |  | TRUE
119 | bus_LV_118-3_0_3_node_120 | 0.4 | n |  | TRUE
120 | bus_LV_118-3_0_3_node_122 | 0.4 | n |  | TRUE
121 | bus_LV_118-3_0_3_node_123 | 0.4 | n |  | TRUE
122 | bus_LV_118-3_0_3_node_124 | 0.4 | n |  | TRUE
123 | bus_LV_118-3_0_3_node_125 | 0.4 | n |  | TRUE
124 | bus_MV_9_2_node_150 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_118-3_0_3_load_0 | 0 | 0.0031004 | 0.00077703 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_118-3_0_3_load_1 | 1 | 0.00085011 | 0.00021306 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_118-3_0_3_load_3 | 3 | 0.0034424 | 0.00086274 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_118-3_0_3_load_25 | 7 | 0.003542 | 0.00088771 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_118-3_0_3_load_8 | 9 | 0.0019388 | 0.0004859 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_118-3_0_3_load_27 | 10 | 0.00508 | 0.0012732 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_118-3_0_3_load_16 | 11 | 0.0045651 | 0.0011441 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_118-3_0_3_load_23 | 12 | 0.0027989 | 0.00070147 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_118-3_0_3_load_5 | 13 | 0.0020876 | 0.00052321 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_118-3_0_3_load_6 | 14 | 0.0025071 | 0.00062833 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_118-3_0_3_load_7 | 15 | 0.0048314 | 0.0012109 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_118-3_0_3_load_57 | 16 | 0.003834 | 0.00096089 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_118-3_0_3_load_55 | 17 | 0.0013711 | 0.00034364 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_118-3_0_3_load_10 | 18 | 0.0048007 | 0.0012032 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_118-3_0_3_load_11 | 19 | 0.00092823 | 0.00023264 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_118-3_0_3_load_12 | 20 | 0.002956 | 0.00074084 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_118-3_0_3_load_109 | 23 | 0.0018571 | 0.00046544 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_118-3_0_3_load_108 | 24 | 0.00092844 | 0.00023269 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_118-3_0_3_load_110 | 26 | 0.008025 | 0.0020112 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_118-3_0_3_load_96 | 29 | 0.0020317 | 0.00050919 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_118-3_0_3_load_115 | 32 | 0.0073091 | 0.0018318 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_118-3_0_3_load_116 | 34 | 0.0078236 | 0.0019608 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_118-3_0_3_load_113 | 37 | 0.0079622 | 0.0019955 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_118-3_0_3_load_67 | 42 | 0.0012561 | 0.00031482 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_118-3_0_3_load_65 | 45 | 0.0055263 | 0.001385 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_118-3_0_3_load_82 | 47 | 0.0035146 | 0.00088085 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_118-3_0_3_load_71 | 48 | 0.0074926 | 0.0018778 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_118-3_0_3_load_72 | 49 | 0.0109 | 0.0027318 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_118-3_0_3_load_73 | 50 | 0.0015485 | 0.0003881 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_118-3_0_3_load_15 | 51 | 0.0014273 | 0.00035771 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_118-3_0_3_load_20 | 52 | 0.0027593 | 0.00069154 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_118-3_0_3_load_103 | 54 | 0.0012937 | 0.00032423 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_118-3_0_3_load_21 | 55 | 0.0026301 | 0.00065917 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_118-3_0_3_load_22 | 56 | 0.001688 | 0.00042305 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_118-3_0_3_load_24 | 57 | 0.006786 | 0.0017007 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_118-3_0_3_load_86 | 58 | 0.0014672 | 0.00036772 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_118-3_0_3_load_54 | 59 | 0.0010597 | 0.00026559 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_118-3_0_3_load_126 | 61 | 0.021756 | 0.0054525 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_118-3_0_3_load_127 | 62 | 0.0075443 | 0.0018908 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_118-3_0_3_load_102 | 63 | 0.0065084 | 0.0016312 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_118-3_0_3_load_101 | 64 | 0.0081468 | 0.0020418 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_118-3_0_3_load_95 | 65 | 0.00037207 | 9.3249e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_118-3_0_3_load_112 | 67 | 0.011263 | 0.0028227 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_118-3_0_3_load_114 | 68 | 0.011203 | 0.0028077 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_118-3_0_3_load_88 | 69 | 0.0096656 | 0.0024224 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_118-3_0_3_load_74 | 71 | 0.00090701 | 0.00022732 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_118-3_0_3_load_43 | 72 | 0.0030013 | 0.00075219 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_118-3_0_3_load_44 | 73 | 0.0025304 | 0.00063419 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_118-3_0_3_load_45 | 74 | 0.0025039 | 0.00062755 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_118-3_0_3_load_47 | 76 | 0.0031498 | 0.00078941 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_118-3_0_3_load_52 | 78 | 0.0013617 | 0.00034129 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_118-3_0_3_load_62 | 79 | 0.0025324 | 0.00063468 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_118-3_0_3_load_87 | 80 | 0.004306 | 0.0010792 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_118-3_0_3_load_85 | 82 | 0.00090413 | 0.0002266 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_118-3_0_3_load_50 | 83 | 0.0017353 | 0.0004349 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_118-3_0_3_load_60 | 84 | 0.0020728 | 0.00051948 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_118-3_0_3_load_48 | 85 | 0.0069426 | 0.00174 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_118-3_0_3_load_49 | 86 | 0.0063113 | 0.0015818 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_118-3_0_3_load_51 | 87 | 0.00099337 | 0.00024896 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_118-3_0_3_load_53 | 88 | 0.0025102 | 0.00062912 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_118-3_0_3_load_56 | 89 | 0.0013319 | 0.00033382 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_118-3_0_3_load_58 | 90 | 0.0023503 | 0.00058905 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_118-3_0_3_load_59 | 91 | 0.0019124 | 0.0004793 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_118-3_0_3_load_61 | 92 | 0.00082503 | 0.00020677 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_118-3_0_3_load_64 | 93 | 0.0054368 | 0.0013626 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_118-3_0_3_load_84 | 94 | 0.0077536 | 0.0019432 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_118-3_0_3_load_76 | 95 | 0.0010403 | 0.00026073 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_118-3_0_3_load_121 | 96 | 0.001487 | 0.00037267 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_118-3_0_3_load_70 | 97 | 0.0014164 | 0.00035497 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_118-3_0_3_load_89 | 98 | 0.002464 | 0.00061753 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_118-3_0_3_load_75 | 99 | 0.0010165 | 0.00025476 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_118-3_0_3_load_83 | 100 | 0.0016752 | 0.00041984 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_118-3_0_3_load_78 | 101 | 0.00089584 | 0.00022452 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_118-3_0_3_load_79 | 102 | 0.0040333 | 0.0010108 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_118-3_0_3_load_81 | 103 | 0.0019927 | 0.00049942 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_118-3_0_3_load_90 | 104 | 0.00033343 | 8.3565e-05 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_118-3_0_3_load_91 | 105 | 0.0018515 | 0.00046402 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_118-3_0_3_load_92 | 106 | 0.0020031 | 0.00050202 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_118-3_0_3_load_93 | 107 | 0.0023022 | 0.00057698 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_118-3_0_3_load_94 | 108 | 0.00051451 | 0.00012895 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_118-3_0_3_load_97 | 109 | 0.004111 | 0.0010303 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_118-3_0_3_load_98 | 110 | 0.0032305 | 0.00080965 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_118-3_0_3_load_100 | 112 | 0.00091911 | 0.00023035 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_118-3_0_3_load_119 | 113 | 0.0067143 | 0.0016828 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_118-3_0_3_load_104 | 114 | 0.0012937 | 0.00032423 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_118-3_0_3_load_106 | 115 | 0.0012938 | 0.00032427 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_118-3_0_3_load_107 | 116 | 0.0012932 | 0.00032411 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_118-3_0_3_load_117 | 117 | 0.00096575 | 0.00024204 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_118-3_0_3_load_118 | 118 | 0.0010222 | 0.00025619 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_118-3_0_3_load_120 | 119 | 0.00112 | 0.0002807 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_118-3_0_3_load_122 | 120 | 0.0011028 | 0.0002764 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_118-3_0_3_load_123 | 121 | 0.0011539 | 0.00028919 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_118-3_0_3_load_124 | 122 | 0.0011406 | 0.00028586 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_118-3_0_3_load_125 | 123 | 0.0012574 | 0.00031514 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 57 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_118-3_0_3_line_0 |  | 0 | 1 | 0.0037854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_118-3_0_3_line_1 |  | 1 | 2 | 0.015591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_118-3_0_3_line_2 |  | 2 | 3 | 0.030622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_118-3_0_3_line_3 |  | 2 | 4 | 0.014936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_118-3_0_3_line_4 |  | 3 | 5 | 0.0020967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_118-3_0_3_line_5 |  | 4 | 6 | 0.012261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
6 | LV_118-3_0_3_line_6 |  | 4 | 7 | 0.021069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_118-3_0_3_line_7 |  | 5 | 8 | 0.018707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_118-3_0_3_line_8 |  | 5 | 9 | 0.01702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_118-3_0_3_line_9 |  | 6 | 10 | 0.012943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_118-3_0_3_line_10 |  | 6 | 11 | 0.020665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_118-3_0_3_line_11 |  | 7 | 12 | 0.0041505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_118-3_0_3_line_12 |  | 8 | 16 | 0.017229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_118-3_0_3_line_13 |  | 8 | 17 | 0.02115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_118-3_0_3_line_14 |  | 9 | 14 | 0.019675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_118-3_0_3_line_15 |  | 11 | 51 | 0.022287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_118-3_0_3_line_16 |  | 12 | 55 | 0.039263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_118-3_0_3_line_17 |  | 13 | 14 | 0.024685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_118-3_0_3_line_18 |  | 13 | 15 | 0.0075018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_118-3_0_3_line_19 |  | 16 | 58 | 0.0019834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_118-3_0_3_line_20 |  | 17 | 59 | 0.030263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_118-3_0_3_line_21 |  | 18 | 19 | 0.025683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_118-3_0_3_line_22 |  | 18 | 20 | 0.028657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
23 | LV_118-3_0_3_line_23 |  | 19 | 21 | 0.011705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
24 | LV_118-3_0_3_line_24 |  | 20 | 22 | 0.019386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
25 | LV_118-3_0_3_line_25 |  | 21 | 23 | 0.004471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_118-3_0_3_line_26 |  | 21 | 24 | 0.013468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_118-3_0_3_line_27 |  | 22 | 25 | 0.01758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
28 | LV_118-3_0_3_line_28 |  | 22 | 26 | 0.022097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_118-3_0_3_line_29 |  | 24 | 38 | 0.019623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
30 | LV_118-3_0_3_line_30 |  | 25 | 45 | 0.032442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_118-3_0_3_line_31 |  | 25 | 30 | 0.012366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_118-3_0_3_line_32 |  | 26 | 36 | 0.0019904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_118-3_0_3_line_33 |  | 27 | 28 | 0.099155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_118-3_0_3_line_34 |  | 27 | 29 | 0.045926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_118-3_0_3_line_35 |  | 28 | 46 | 0.064014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_118-3_0_3_line_36 |  | 28 | 47 | 0.017714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_118-3_0_3_line_37 |  | 29 | 65 | 0.0099069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_118-3_0_3_line_38 |  | 30 | 31 | 0.015885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_118-3_0_3_line_39 |  | 30 | 32 | 0.016917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_118-3_0_3_line_40 |  | 31 | 49 | 0.0039149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_118-3_0_3_line_41 |  | 31 | 48 | 0.026901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_118-3_0_3_line_42 |  | 32 | 33 | 0.060913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_118-3_0_3_line_43 |  | 33 | 34 | 0.020871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_118-3_0_3_line_44 |  | 34 | 62 | 0.041041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_118-3_0_3_line_45 |  | 35 | 36 | 0.00833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_118-3_0_3_line_46 |  | 35 | 37 | 0.017463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_118-3_0_3_line_47 |  | 36 | 67 | 0.027487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_118-3_0_3_line_48 |  | 37 | 68 | 0.026073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_118-3_0_3_line_49 |  | 38 | 39 | 0.040402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
50 | LV_118-3_0_3_line_50 |  | 39 | 52 | 0.032648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_118-3_0_3_line_51 |  | 39 | 51 | 0.014204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
52 | LV_118-3_0_3_line_52 |  | 40 | 41 | 0.064638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_118-3_0_3_line_53 |  | 40 | 42 | 0.06139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_118-3_0_3_line_54 |  | 41 | 50 | 0.035549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_118-3_0_3_line_55 |  | 42 | 60 | 0.01403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_118-3_0_3_line_56 |  | 43 | 44 | 0.023879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_118-3_0_3_line_57 |  | 43 | 45 | 0.016701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_118-3_0_3_line_58 |  | 44 | 63 | 0.012596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_118-3_0_3_line_59 |  | 44 | 64 | 0.0053165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_118-3_0_3_line_60 |  | 46 | 48 | 0.0032595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_118-3_0_3_line_61 |  | 47 | 66 | 0.030837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_118-3_0_3_line_62 |  | 50 | 71 | 0.032252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_118-3_0_3_line_63 |  | 52 | 53 | 0.01876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_118-3_0_3_line_64 |  | 53 | 54 | 0.0061152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_118-3_0_3_line_65 |  | 54 | 114 | 0.0058588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_118-3_0_3_line_66 |  | 55 | 56 | 0.0052779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
67 | LV_118-3_0_3_line_67 |  | 56 | 57 | 0.0030058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
68 | LV_118-3_0_3_line_68 |  | 58 | 82 | 0.029332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_118-3_0_3_line_69 |  | 59 | 89 | 0.0087509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_118-3_0_3_line_70 |  | 60 | 70 | 0.023863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_118-3_0_3_line_71 |  | 60 | 97 | 0.034937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_118-3_0_3_line_72 |  | 61 | 62 | 0.054954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_118-3_0_3_line_73 |  | 63 | 96 | 0.0068688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_118-3_0_3_line_74 |  | 65 | 108 | 0.013911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_118-3_0_3_line_75 |  | 66 | 103 | 0.046713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_118-3_0_3_line_76 |  | 66 | 102 | 0.014055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_118-3_0_3_line_77 |  | 67 | 94 | 0.039414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_118-3_0_3_line_78 |  | 69 | 70 | 0.032001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_118-3_0_3_line_79 |  | 70 | 98 | 0.004157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_118-3_0_3_line_80 |  | 71 | 99 | 0.0058784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_118-3_0_3_line_81 |  | 72 | 73 | 0.012309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_118-3_0_3_line_82 |  | 72 | 74 | 0.0086614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_118-3_0_3_line_83 |  | 73 | 75 | 0.032643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_118-3_0_3_line_84 |  | 74 | 76 | 0.0046526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_118-3_0_3_line_85 |  | 75 | 77 | 0.015583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_118-3_0_3_line_86 |  | 75 | 78 | 0.0034497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_118-3_0_3_line_87 |  | 76 | 79 | 0.004146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_118-3_0_3_line_88 |  | 77 | 80 | 0.042875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_118-3_0_3_line_89 |  | 77 | 81 | 0.024417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_118-3_0_3_line_90 |  | 77 | 82 | 0.019619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_118-3_0_3_line_91 |  | 78 | 83 | 0.0098824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_118-3_0_3_line_92 |  | 79 | 84 | 0.020222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_118-3_0_3_line_93 |  | 81 | 95 | 0.0053847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_118-3_0_3_line_94 |  | 83 | 85 | 0.014776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_118-3_0_3_line_95 |  | 84 | 90 | 0.0025076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_118-3_0_3_line_96 |  | 85 | 86 | 0.0047448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_118-3_0_3_line_97 |  | 86 | 87 | 0.0053436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_118-3_0_3_line_98 |  | 87 | 88 | 0.11339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_118-3_0_3_line_99 |  | 90 | 91 | 0.0045517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_118-3_0_3_line_100 |  | 91 | 92 | 0.024698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_118-3_0_3_line_101 |  | 93 | 94 | 0.029087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_118-3_0_3_line_102 |  | 95 | 97 | 0.012762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_118-3_0_3_line_103 |  | 96 | 113 | 0.0013442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_118-3_0_3_line_104 |  | 99 | 100 | 0.036885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_118-3_0_3_line_105 |  | 100 | 101 | 0.0034679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_118-3_0_3_line_106 |  | 104 | 105 | 0.034897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_118-3_0_3_line_107 |  | 104 | 106 | 0.0037462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_118-3_0_3_line_108 |  | 105 | 107 | 0.0039905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_118-3_0_3_line_109 |  | 106 | 108 | 0.013341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_118-3_0_3_line_110 |  | 107 | 109 | 0.042339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_118-3_0_3_line_111 |  | 109 | 110 | 0.00031494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_118-3_0_3_line_112 |  | 110 | 111 | 0.040255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_118-3_0_3_line_113 |  | 111 | 112 | 0.007267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_118-3_0_3_line_114 |  | 113 | 117 | 0.017535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_118-3_0_3_line_115 |  | 114 | 115 | 0.010046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_118-3_0_3_line_116 |  | 115 | 116 | 0.0058586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_118-3_0_3_line_117 |  | 117 | 118 | 0.0045031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_118-3_0_3_line_118 |  | 118 | 119 | 0.0046757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_118-3_0_3_line_119 |  | 119 | 120 | 0.004677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_118-3_0_3_line_120 |  | 120 | 121 | 0.0047875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_118-3_0_3_line_121 |  | 121 | 122 | 0.0048014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_118-3_0_3_line_122 |  | 122 | 123 | 0.0044677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_118-3_0_3_trafo_24 | 0.63 MVA 20/0.4 kV | 124 | 57 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2707193.3853 | 1234295.16 | 2707197.1088 | 1234294.4778
1 | 2707212.4448 | 1234291.6678 | 2707197.1088 | 1234294.4778
2 | 2707212.4448 | 1234291.6678 | 2707209.8139 | 1234261.1588
3 | 2707213.0386 | 1234306.5899 | 2707212.4448 | 1234291.6678
4 | 2707209.6338 | 1234259.0699 | 2707209.8139 | 1234261.1588
5 | 2707219.4213 | 1234317.0687 | 2707213.0386 | 1234306.5899
6 | 2707213.0386 | 1234306.5899 | 2707192.1829 | 1234309.5843
7 | 2707207.2051 | 1234240.523 | 2707209.6338 | 1234259.0699
8 | 2707209.6338 | 1234259.0699 | 2707193.3496 | 1234264.0195
9 | 2707219.4213 | 1234317.0687 | 2707225.8192 | 1234313.7038 | 2707231.4684 | 1234312.8445
10 | 2707219.4213 | 1234317.0687 | 2707217.3987 | 1234319.2227 | 2707213.637 | 1234325.026 | 2707211.0175 | 1234335.4979 | 2707211.0175 | 1234335.4979
11 | 2707188.0746 | 1234310.1741 | 2707192.1829 | 1234309.5843
12 | 2707207.2051 | 1234240.523 | 2707204.3778 | 1234223.5278
13 | 2707207.2051 | 1234240.523 | 2707200.8802 | 1234237.7401 | 2707186.6948 | 1234238.9831
14 | 2707193.3496 | 1234264.0195 | 2707191.8495 | 1234264.4755 | 2707176.8299 | 1234274.5892
15 | 2707214.006 | 1234357.5835 | 2707211.0175 | 1234335.4979
16 | 2707188.0746 | 1234310.1741 | 2707187.9959 | 1234310.1854 | 2707178.7983 | 1234313.4554 | 2707156.6014 | 1234317.1135 | 2707153.3467 | 1234323.2272
17 | 2707156.3543 | 1234288.3768 | 2707176.8299 | 1234274.5892
18 | 2707150.1317 | 1234292.5669 | 2707156.3543 | 1234288.3768
19 | 2707204.0523 | 1234221.5713 | 2707204.3778 | 1234223.5278
20 | 2707157.6631 | 1234247.4523 | 2707185.6224 | 1234239.077 | 2707186.6948 | 1234238.9831
21 | 2707145.4869 | 1234418.6837 | 2707147.7444 | 1234418.9985 | 2707155.8795 | 1234419.6345 | 2707165.3267 | 1234419.7272 | 2707171.0949 | 1234419.1624
22 | 2707145.4869 | 1234418.6837 | 2707139.3162 | 1234417.8234 | 2707129.5724 | 1234415.2903 | 2707119.931 | 1234412.114 | 2707117.89 | 1234411.2717
23 | 2707182.6745 | 1234417.505 | 2707175.7782 | 1234418.7038 | 2707171.0949 | 1234419.1624
24 | 2707100.6769 | 1234402.493 | 2707104.9414 | 1234405.3276 | 2707109.7028 | 1234407.8931 | 2707117.89 | 1234411.2717
25 | 2707182.6745 | 1234417.505 | 2707181.9136 | 1234413.099
26 | 2707182.6745 | 1234417.505 | 2707185.5226 | 1234417.0115 | 2707191.4847 | 1234415.9738 | 2707195.8564 | 1234414.8024
27 | 2707096.2891 | 1234419.5158 | 2707098.5731 | 1234410.4167 | 2707100.6769 | 1234402.493
28 | 2707100.6769 | 1234402.493 | 2707095.9254 | 1234398.5376 | 2707092.1101 | 1234393.8876 | 2707089.7331 | 1234388.8297 | 2707088.6793 | 1234384.6496
29 | 2707214.8107 | 1234409.7232 | 2707195.8564 | 1234414.8024
30 | 2707096.2891 | 1234419.5158 | 2707128.2966 | 1234424.805
31 | 2707085.218 | 1234425.0873 | 2707096.2891 | 1234419.5158
32 | 2707088.1928 | 1234382.7195 | 2707088.6793 | 1234384.6496
33 | 2706991.4976 | 1234295.9115 | 2706975.4338 | 1234315.9487 | 2706972.0353 | 1234321.3584 | 2706969.2346 | 1234327.2013 | 2706967.7167 | 1234332.8672 | 2706966.5366 | 1234339.54 | 2706976.3632 | 1234344.2093 | 2707000.2118 | 1234355.6029 | 2707009.7572 | 1234360.334
34 | 2706991.4976 | 1234295.9115 | 2707000.583 | 1234285 | 2707002.9481 | 1234284.8425 | 2707003.8667 | 1234284.7034 | 2707004.6433 | 1234284.4616 | 2707005.3634 | 1234283.9964 | 2707022.2071 | 1234263.9733 | 2707022.5726 | 1234263.5081
35 | 2707009.7572 | 1234360.334 | 2707009.3506 | 1234365.2526 | 2707040.5352 | 1234379.1805 | 2707041.8358 | 1234387.2545 | 2707044.7289 | 1234390.1422 | 2707055.1615 | 1234397.3134
36 | 2707009.7572 | 1234360.334 | 2707010.5915 | 1234342.6394
37 | 2707028.6931 | 1234255.718 | 2707022.5726 | 1234263.5081
38 | 2707069.4063 | 1234423.579 | 2707077.7828 | 1234424.2638 | 2707085.218 | 1234425.0873
39 | 2707085.218 | 1234425.0873 | 2707082.5582 | 1234441.7937
40 | 2707069.4063 | 1234423.579 | 2707069.4452 | 1234427.4937
41 | 2707069.4063 | 1234423.579 | 2707064.7695 | 1234410.7412 | 2707057.0582 | 1234399.9642
42 | 2707073.0044 | 1234501.5813 | 2707073.2888 | 1234498.4062 | 2707073.7333 | 1234493.4883 | 2707074.376 | 1234486.3944 | 2707074.8768 | 1234480.877 | 2707078.6109 | 1234470.7143 | 2707081.9034 | 1234451.4477 | 2707081.5551 | 1234448.0944 | 2707082.5582 | 1234441.7937
43 | 2707073.0044 | 1234501.5813 | 2707090.4775 | 1234512.9955
44 | 2707114.6084 | 1234542.024 | 2707112.3569 | 1234527.288 | 2707090.4775 | 1234512.9955
45 | 2707079.9324 | 1234381.4697 | 2707088.1928 | 1234382.7195
46 | 2707079.9324 | 1234381.4697 | 2707079.8158 | 1234364.0066
47 | 2707088.1928 | 1234382.7195 | 2707087.2353 | 1234375.7747 | 2707085.8648 | 1234360.2493 | 2707085.5838 | 1234355.3666
48 | 2707079.8158 | 1234364.0066 | 2707079.7033 | 1234347.1504 | 2707080.1064 | 1234337.9429
49 | 2707214.8107 | 1234409.7232 | 2707219.2969 | 1234404.8893 | 2707220.642 | 1234399.9987 | 2707220.402 | 1234397.359 | 2707216.5376 | 1234374.8832 | 2707215.9144 | 1234371.6583
50 | 2707215.9144 | 1234371.6583 | 2707183.5708 | 1234376.1025
51 | 2707215.9144 | 1234371.6583 | 2707214.5846 | 1234361.8602 | 2707214.006 | 1234357.5835
52 | 2707353.0873 | 1234179.9878 | 2707362.5391 | 1234181.9378 | 2707367.9222 | 1234177.3426 | 2707366.0014 | 1234129.4712
53 | 2707353.0873 | 1234179.9878 | 2707328.4431 | 1234174.9054 | 2707300.9908 | 1234172.708 | 2707292.3798 | 1234173.8536
54 | 2707366.0014 | 1234129.4712 | 2707330.4732 | 1234128.2494
55 | 2707278.472 | 1234175.7038 | 2707292.3798 | 1234173.8536
56 | 2707144.7573 | 1234427.6179 | 2707147.7733 | 1234443.4177 | 2707149.187 | 1234451.0824
57 | 2707144.7573 | 1234427.6179 | 2707142.7435 | 1234427.1924 | 2707128.2966 | 1234424.805
58 | 2707149.187 | 1234451.0824 | 2707145.6448 | 1234456.4782 | 2707147.0678 | 1234462.452
59 | 2707149.187 | 1234451.0824 | 2707150.4338 | 1234456.2507
60 | 2707055.1615 | 1234397.3134 | 2707057.0582 | 1234399.9642
61 | 2707023.1889 | 1234315.3636 | 2707010.9704 | 1234334.6028 | 2707010.5915 | 1234342.6394
62 | 2707330.4732 | 1234128.2494 | 2707313.5253 | 1234127.6665 | 2707298.3523 | 1234125.7462
63 | 2707164.9852 | 1234378.6562 | 2707183.5708 | 1234376.1025
64 | 2707164.9852 | 1234378.6562 | 2707164.4788 | 1234374.4105 | 2707162.6601 | 1234374.6857
65 | 2707162.6601 | 1234374.6857 | 2707156.8672 | 1234375.5622
66 | 2707153.3467 | 1234323.2272 | 2707150.8666 | 1234327.886
67 | 2707149.4541 | 1234330.5393 | 2707150.8666 | 1234327.886
68 | 2707200.1139 | 1234192.5913 | 2707199.8762 | 1234196.4682 | 2707204.0523 | 1234221.5713
69 | 2707149.2802 | 1234249.9634 | 2707157.6631 | 1234247.4523
70 | 2707278.472 | 1234175.7038 | 2707275.8479 | 1234199.4191
71 | 2707278.472 | 1234175.7038 | 2707262.2832 | 1234177.8577 | 2707243.6904 | 1234177.156
72 | 2707111.1455 | 1234596.3848 | 2707111.6922 | 1234592.2591 | 2707116.9006 | 1234557.026 | 2707114.6084 | 1234542.024
73 | 2707147.0678 | 1234462.452 | 2707148.6594 | 1234469.1338
74 | 2707028.6931 | 1234255.718 | 2707032.5444 | 1234250.8161 | 2707037.1231 | 1234244.6535
75 | 2707023.1889 | 1234315.3636 | 2707022.4448 | 1234311.2804 | 2707032.6484 | 1234293.773 | 2707047.0547 | 1234276.7531
76 | 2707023.1889 | 1234315.3636 | 2707037.2318 | 1234314.7764
77 | 2707085.5838 | 1234355.3666 | 2707085.0347 | 1234345.8232 | 2707085.0472 | 1234333.3695 | 2707085.6034 | 1234322.2599 | 2707086.2238 | 1234316.0133
78 | 2707275.8479 | 1234199.4191 | 2707272.3307 | 1234231.2263
79 | 2707275.8479 | 1234199.4191 | 2707271.6888 | 1234199.1327
80 | 2707292.5205 | 1234125.0082 | 2707298.3523 | 1234125.7462
81 | 2707174.8443 | 1234172.7857 | 2707172.7923 | 1234173.8624 | 2707164.8866 | 1234179.9721
82 | 2707158.0333 | 1234185.2685 | 2707164.8866 | 1234179.9721
83 | 2707203.75 | 1234157.6194 | 2707174.8443 | 1234172.7857
84 | 2707154.3519 | 1234188.1135 | 2707158.0333 | 1234185.2685
85 | 2707203.75 | 1234157.6194 | 2707201.3143 | 1234173.0095
86 | 2707203.75 | 1234157.6194 | 2707203.3357 | 1234154.1947
87 | 2707151.0714 | 1234190.6488 | 2707154.3519 | 1234188.1135
88 | 2707168.1393 | 1234189.6128 | 2707168.5596 | 1234183.1043 | 2707172.7265 | 1234177.5084 | 2707179.2829 | 1234174.1797 | 2707189.0497 | 1234172.9438 | 2707201.3143 | 1234173.0095
89 | 2707201.3143 | 1234173.0095 | 2707225.5562 | 1234176.4717
90 | 2707201.3143 | 1234173.0095 | 2707200.1139 | 1234192.5913
91 | 2707202.1487 | 1234144.3839 | 2707203.3357 | 1234154.1947
92 | 2707151.0714 | 1234190.6488 | 2707135.0707 | 1234203.0144
93 | 2707225.5562 | 1234176.4717 | 2707230.9371 | 1234176.6747
94 | 2707200.374 | 1234129.7149 | 2707202.1487 | 1234144.3839
95 | 2707133.0866 | 1234204.5478 | 2707133.0866 | 1234204.5478 | 2707135.0707 | 1234203.0144
96 | 2707200.374 | 1234129.7149 | 2707199.8041 | 1234125.0044
97 | 2707199.8041 | 1234125.0044 | 2707199.1623 | 1234119.6995
98 | 2707199.1623 | 1234119.6995 | 2707198.2222 | 1234111.9292 | 2707198.2601 | 1234101.0215 | 2707209.5554 | 1234089.7833 | 2707276.7264 | 1234076.5964 | 2707285.7419 | 1234071.6714
99 | 2707133.0866 | 1234204.5478 | 2707130.2697 | 1234208.1232
100 | 2707130.2697 | 1234208.1232 | 2707120.5877 | 1234220.4124 | 2707114.4556 | 1234227.0724
101 | 2707092.0034 | 1234287.552 | 2707088.9371 | 1234299.4581 | 2707086.7598 | 1234310.6163 | 2707086.2238 | 1234316.0133
102 | 2707230.9371 | 1234176.6747 | 2707243.6904 | 1234177.156
103 | 2707148.9709 | 1234470.4414 | 2707148.6594 | 1234469.1338
104 | 2707292.5205 | 1234125.0082 | 2707263.3045 | 1234121.3106 | 2707255.9011 | 1234120.6121
105 | 2707252.4485 | 1234120.2864 | 2707255.9011 | 1234120.6121
106 | 2707045.2945 | 1234229.7259 | 2707046.2224 | 1234227.489 | 2707048.4546 | 1234221.6803 | 2707050.3433 | 1234214.3532 | 2707051.2066 | 1234210.1433 | 2707052.0257 | 1234204.1868 | 2707052.5552 | 1234197.9138 | 2707052.4118 | 1234195.8379
107 | 2707045.2945 | 1234229.7259 | 2707043.8591 | 1234233.1862
108 | 2707052.4118 | 1234195.8379 | 2707052.1368 | 1234191.8569
109 | 2707043.8591 | 1234233.1862 | 2707043.5074 | 1234234.034 | 2707041.1743 | 1234238.7178 | 2707038.8219 | 1234242.3671 | 2707037.1231 | 1234244.6535
110 | 2707048.9764 | 1234149.6437 | 2707049.4629 | 1234153.146 | 2707052.1368 | 1234191.8569
111 | 2707048.9331 | 1234149.3318 | 2707048.9764 | 1234149.6437
112 | 2707043.9824 | 1234109.3916 | 2707044.6282 | 1234116.4086 | 2707045.1737 | 1234122.2674 | 2707048.9331 | 1234149.3318
113 | 2707043.9824 | 1234109.3916 | 2707041.8726 | 1234113.4456 | 2707041.5181 | 1234114.629 | 2707041.3405 | 1234116.0825
114 | 2707153.3721 | 1234487.4138 | 2707153.0786 | 1234486.324 | 2707150.2336 | 1234475.7424 | 2707148.9709 | 1234470.4414
115 | 2707156.8672 | 1234375.5622 | 2707146.9344 | 1234377.0652
116 | 2707141.1417 | 1234377.9417 | 2707146.9344 | 1234377.0652
117 | 2707153.3721 | 1234487.4138 | 2707154.543 | 1234491.7621
118 | 2707154.543 | 1234491.7621 | 2707155.7588 | 1234496.277
119 | 2707155.7588 | 1234496.277 | 2707156.975 | 1234500.7931
120 | 2707156.975 | 1234500.7931 | 2707158.2198 | 1234505.4159
121 | 2707158.2198 | 1234505.4159 | 2707159.4683 | 1234510.0522
122 | 2707159.4683 | 1234510.0522 | 2707159.7556 | 1234511.119 | 2707160.7796 | 1234514.3222

## bus_geodata
| x | y | coords
0 | 2707193.3853 | 1234295.16
1 | 2707197.1088 | 1234294.4778
2 | 2707212.4448 | 1234291.6678
3 | 2707209.8139 | 1234261.1588
4 | 2707213.0386 | 1234306.5899
5 | 2707209.6338 | 1234259.0699
6 | 2707219.4213 | 1234317.0687
7 | 2707192.1829 | 1234309.5843
8 | 2707207.2051 | 1234240.523
9 | 2707193.3496 | 1234264.0195
10 | 2707231.4684 | 1234312.8445
11 | 2707211.0175 | 1234335.4979
12 | 2707188.0746 | 1234310.1741
13 | 2707156.3543 | 1234288.3768
14 | 2707176.8299 | 1234274.5892
15 | 2707150.1317 | 1234292.5669
16 | 2707204.3778 | 1234223.5278
17 | 2707186.6948 | 1234238.9831
18 | 2707145.4869 | 1234418.6837
19 | 2707171.0949 | 1234419.1624
20 | 2707117.89 | 1234411.2717
21 | 2707182.6745 | 1234417.505
22 | 2707100.6769 | 1234402.493
23 | 2707181.9136 | 1234413.099
24 | 2707195.8564 | 1234414.8024
25 | 2707096.2891 | 1234419.5158
26 | 2707088.6793 | 1234384.6496
27 | 2706991.4977 | 1234295.9115
28 | 2707009.7572 | 1234360.334
29 | 2707022.5726 | 1234263.5081
30 | 2707085.218 | 1234425.0873
31 | 2707069.4063 | 1234423.579
32 | 2707082.5582 | 1234441.7937
33 | 2707073.0044 | 1234501.5813
34 | 2707090.4775 | 1234512.9955
35 | 2707079.9324 | 1234381.4697
36 | 2707088.1928 | 1234382.7195
37 | 2707079.8158 | 1234364.0066
38 | 2707214.8107 | 1234409.7232
39 | 2707215.9144 | 1234371.6583
40 | 2707353.0873 | 1234179.9878
41 | 2707366.0014 | 1234129.4712
42 | 2707292.3798 | 1234173.8536
43 | 2707144.7573 | 1234427.6179
44 | 2707149.187 | 1234451.0824
45 | 2707128.2966 | 1234424.805
46 | 2707055.1615 | 1234397.3134
47 | 2707010.5915 | 1234342.6394
48 | 2707057.0582 | 1234399.9642
49 | 2707069.4452 | 1234427.4937
50 | 2707330.4732 | 1234128.2494
51 | 2707214.006 | 1234357.5835
52 | 2707183.5708 | 1234376.1025
53 | 2707164.9852 | 1234378.6562
54 | 2707162.6601 | 1234374.6857
55 | 2707153.3467 | 1234323.2272
56 | 2707150.8666 | 1234327.886
57 | 2707149.4541 | 1234330.5393
58 | 2707204.0523 | 1234221.5713
59 | 2707157.6631 | 1234247.4523
60 | 2707278.472 | 1234175.7038
61 | 2707111.1455 | 1234596.3848
62 | 2707114.6084 | 1234542.024
63 | 2707147.0678 | 1234462.452
64 | 2707150.4338 | 1234456.2507
65 | 2707028.6931 | 1234255.718
66 | 2707023.1889 | 1234315.3636
67 | 2707085.5838 | 1234355.3666
68 | 2707080.1064 | 1234337.9429
69 | 2707272.3307 | 1234231.2263
70 | 2707275.8479 | 1234199.4191
71 | 2707298.3523 | 1234125.7462
72 | 2707164.8866 | 1234179.9721
73 | 2707174.8443 | 1234172.7857
74 | 2707158.0333 | 1234185.2685
75 | 2707203.75 | 1234157.6194
76 | 2707154.3519 | 1234188.1135
77 | 2707201.3143 | 1234173.0095
78 | 2707203.3357 | 1234154.1947
79 | 2707151.0714 | 1234190.6488
80 | 2707168.1393 | 1234189.6128
81 | 2707225.5562 | 1234176.4717
82 | 2707200.1139 | 1234192.5913
83 | 2707202.1487 | 1234144.3839
84 | 2707135.0707 | 1234203.0144
85 | 2707200.374 | 1234129.7149
86 | 2707199.8041 | 1234125.0044
87 | 2707199.1623 | 1234119.6995
88 | 2707285.7419 | 1234071.6714
89 | 2707149.2802 | 1234249.9634
90 | 2707133.0866 | 1234204.5478
91 | 2707130.2697 | 1234208.1232
92 | 2707114.4556 | 1234227.0724
93 | 2707092.0034 | 1234287.552
94 | 2707086.2238 | 1234316.0133
95 | 2707230.9371 | 1234176.6747
96 | 2707148.6594 | 1234469.1338
97 | 2707243.6904 | 1234177.156
98 | 2707271.6888 | 1234199.1327
99 | 2707292.5205 | 1234125.0082
100 | 2707255.9011 | 1234120.6121
101 | 2707252.4485 | 1234120.2864
102 | 2707037.2318 | 1234314.7764
103 | 2707047.0547 | 1234276.7531
104 | 2707045.2945 | 1234229.7259
105 | 2707052.4118 | 1234195.8379
106 | 2707043.8591 | 1234233.1862
107 | 2707052.1368 | 1234191.8569
108 | 2707037.1231 | 1234244.6535
109 | 2707048.9764 | 1234149.6437
110 | 2707048.9331 | 1234149.3318
111 | 2707043.9824 | 1234109.3916
112 | 2707041.3405 | 1234116.0825
113 | 2707148.9709 | 1234470.4414
114 | 2707156.8672 | 1234375.5622
115 | 2707146.9344 | 1234377.0652
116 | 2707141.1417 | 1234377.9417
117 | 2707153.3721 | 1234487.4138
118 | 2707154.543 | 1234491.7621
119 | 2707155.7588 | 1234496.277
120 | 2707156.975 | 1234500.7931
121 | 2707158.2198 | 1234505.4159
122 | 2707159.4683 | 1234510.0522
123 | 2707160.7796 | 1234514.3222
124 | 2707213.0386 | 1234306.5899

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99167 | -0.15804 | 0.0031004 | 0.00077703
1 | 0.99168 | -0.15783 | 0.00085011 | 0.00021306
2 | 0.99174 | -0.15674 | 0 | 0
3 | 0.98915 | -0.20665 | 0.0034424 | 0.00086274
4 | 0.99306 | -0.13145 | 0 | 0
5 | 0.98898 | -0.20994 | 0 | 0
6 | 0.99227 | -0.14651 | 0 | 0
7 | 0.99504 | -0.09378 | 0.003542 | 0.00088771
8 | 0.98765 | -0.23562 | 0 | 0
9 | 0.9888 | -0.21339 | 0.0019388 | 0.0004859
10 | 0.99221 | -0.14767 | 0.00508 | 0.0012732
11 | 0.99096 | -0.17133 | 0.0045651 | 0.0011441
12 | 0.99543 | -0.086292 | 0.0027989 | 0.00070147
13 | 0.98847 | -0.21975 | 0.0020876 | 0.00052321
14 | 0.98863 | -0.2167 | 0.0025071 | 0.00062833
15 | 0.98844 | -0.22039 | 0.0048314 | 0.0012109
16 | 0.98649 | -0.25817 | 0.003834 | 0.00096089
17 | 0.98758 | -0.23704 | 0.0013711 | 0.00034364
18 | 0.98226 | -0.33896 | 0.0048007 | 0.0012032
19 | 0.98374 | -0.31029 | 0.00092823 | 0.00023264
20 | 0.98065 | -0.37021 | 0.002956 | 0.00074084
21 | 0.98441 | -0.29719 | 0 | 0
22 | 0.97958 | -0.39106 | 0 | 0
23 | 0.98441 | -0.29734 | 0.0018571 | 0.00046544
24 | 0.9852 | -0.28199 | 0.00092844 | 0.00023269
25 | 0.97855 | -0.41123 | 0 | 0
26 | 0.97853 | -0.41181 | 0.008025 | 0.0020112
27 | 0.97263 | -0.52764 | 0 | 0
28 | 0.97426 | -0.4954 | 0 | 0
29 | 0.97187 | -0.54261 | 0.0020317 | 0.00050919
30 | 0.97751 | -0.43153 | 0 | 0
31 | 0.97684 | -0.44475 | 0 | 0
32 | 0.97681 | -0.44525 | 0.0073091 | 0.0018318
33 | 0.97471 | -0.48665 | 0 | 0
34 | 0.97398 | -0.50087 | 0.0078236 | 0.0019608
35 | 0.9783 | -0.4163 | 0 | 0
36 | 0.97845 | -0.41339 | 0 | 0
37 | 0.97799 | -0.4224 | 0.0079622 | 0.0019955
38 | 0.98635 | -0.25978 | 0 | 0
39 | 0.98872 | -0.2142 | 0 | 0
40 | 0.9814 | -0.35742 | 0 | 0
41 | 0.98104 | -0.3645 | 0 | 0
42 | 0.98174 | -0.3507 | 0.0012561 | 0.00031482
43 | 0.97699 | -0.44194 | 0 | 0
44 | 0.97631 | -0.4553 | 0 | 0
45 | 0.97746 | -0.4326 | 0.0055263 | 0.001385
46 | 0.97589 | -0.46345 | 0 | 0
47 | 0.9741 | -0.4985 | 0.0035146 | 0.00088085
48 | 0.97597 | -0.46183 | 0.0074926 | 0.0018778
49 | 0.9768 | -0.44553 | 0.0109 | 0.0027318
50 | 0.98084 | -0.36839 | 0.0015485 | 0.0003881
51 | 0.98959 | -0.19757 | 0.0014273 | 0.00035771
52 | 0.98849 | -0.21882 | 0.0027593 | 0.00069154
53 | 0.9884 | -0.22056 | 0 | 0
54 | 0.98837 | -0.22112 | 0.0012937 | 0.00032423
55 | 0.9992 | -0.015106 | 0.0026301 | 0.00065917
56 | 0.99971 | -0.0054975 | 0.001688 | 0.00042305
57 | 1 | 0 | -0.32221 | -0.08262
58 | 0.98636 | -0.26063 | 0.0014672 | 0.00036772
59 | 0.98751 | -0.23834 | 0.0010597 | 0.00026559
60 | 0.98183 | -0.34885 | 0 | 0
61 | 0.97175 | -0.54504 | 0.021756 | 0.0054525
62 | 0.97286 | -0.523 | 0.0075443 | 0.0018908
63 | 0.97605 | -0.46048 | 0.0065084 | 0.0016312
64 | 0.97627 | -0.45609 | 0.0081468 | 0.0020418
65 | 0.97172 | -0.54547 | 0.00037207 | 9.3249e-05
66 | 0.97393 | -0.50192 | 0 | 0
67 | 0.97782 | -0.42564 | 0.011263 | 0.0028227
68 | 0.97772 | -0.42772 | 0.011203 | 0.0028077
69 | 0.98128 | -0.35968 | 0.0096656 | 0.0024224
70 | 0.98157 | -0.35408 | 0 | 0
71 | 0.9807 | -0.37102 | 0.00090701 | 0.00022732
72 | 0.98189 | -0.34784 | 0.0030013 | 0.00075219
73 | 0.98209 | -0.34376 | 0.0025304 | 0.00063419
74 | 0.98176 | -0.35025 | 0.0025039 | 0.00062755
75 | 0.98272 | -0.33145 | 0 | 0
76 | 0.98171 | -0.35133 | 0.0031498 | 0.00078941
77 | 0.98331 | -0.32 | 0 | 0
78 | 0.98266 | -0.33269 | 0.0013617 | 0.00034129
79 | 0.98167 | -0.35205 | 0.0025324 | 0.00063468
80 | 0.98314 | -0.32333 | 0.004306 | 0.0010792
81 | 0.98282 | -0.32964 | 0 | 0
82 | 0.98452 | -0.29635 | 0.00090413 | 0.0002266
83 | 0.98249 | -0.33599 | 0.0017353 | 0.0004349
84 | 0.98154 | -0.35467 | 0.0020728 | 0.00051948
85 | 0.98226 | -0.34046 | 0.0069426 | 0.00174
86 | 0.98222 | -0.3413 | 0.0063113 | 0.0015818
87 | 0.9822 | -0.34164 | 0.00099337 | 0.00024896
88 | 0.98194 | -0.34679 | 0.0025102 | 0.00062912
89 | 0.9875 | -0.23855 | 0.0013319 | 0.00033382
90 | 0.98153 | -0.3549 | 0.0023503 | 0.00058905
91 | 0.98151 | -0.35513 | 0.0019124 | 0.0004793
92 | 0.98149 | -0.3555 | 0.00082503 | 0.00020677
93 | 0.97719 | -0.43801 | 0.0054368 | 0.0013626
94 | 0.97734 | -0.43512 | 0.0077536 | 0.0019432
95 | 0.98271 | -0.33177 | 0.0010403 | 0.00026073
96 | 0.97594 | -0.46248 | 0.001487 | 0.00037267
97 | 0.98246 | -0.33657 | 0.0014164 | 0.00035497
98 | 0.98156 | -0.35427 | 0.002464 | 0.00061753
99 | 0.98068 | -0.3714 | 0.0010165 | 0.00025476
100 | 0.9806 | -0.37312 | 0.0016752 | 0.00041984
101 | 0.98059 | -0.37317 | 0.00089584 | 0.00022452
102 | 0.97388 | -0.50296 | 0.0040333 | 0.0010108
103 | 0.97385 | -0.50363 | 0.0019927 | 0.00049942
104 | 0.9713 | -0.55391 | 0.00033343 | 8.3565e-05
105 | 0.97089 | -0.56192 | 0.0018515 | 0.00046402
106 | 0.97134 | -0.55302 | 0.0020031 | 0.00050202
107 | 0.97085 | -0.5627 | 0.0023022 | 0.00057698
108 | 0.97153 | -0.54939 | 0.00051451 | 0.00012895
109 | 0.97053 | -0.56917 | 0.004111 | 0.0010303
110 | 0.97052 | -0.56919 | 0.0032305 | 0.00080965
111 | 0.97049 | -0.56988 | 0 | 0
112 | 0.97048 | -0.57 | 0.00091911 | 0.00023035
113 | 0.97593 | -0.46284 | 0.0067143 | 0.0016828
114 | 0.98835 | -0.22153 | 0.0012937 | 0.00032423
115 | 0.98832 | -0.22199 | 0.0012938 | 0.00032427
116 | 0.98832 | -0.22213 | 0.0012932 | 0.00032411
117 | 0.9758 | -0.46533 | 0.00096575 | 0.00024204
118 | 0.97577 | -0.46589 | 0.0010222 | 0.00025619
119 | 0.97575 | -0.46639 | 0.00112 | 0.0002807
120 | 0.97573 | -0.46678 | 0.0011028 | 0.0002764
121 | 0.97571 | -0.4671 | 0.0011539 | 0.00028919
122 | 0.9757 | -0.46731 | 0.0011406 | 0.00028586
123 | 0.97569 | -0.46741 | 0.0012574 | 0.00031514
124 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0031004 | -0.00077703 | 0.0031004 | 0.000777 | 3.0723e-08 | -2.9176e-08 | 0.0046522 | 0.0046522 | 0.0046522 | 0.99167 | -0.15804 | 0.99168 | -0.15783 | 1.2781
1 | -0.0039505 | -0.00099006 | 0.0039507 | 0.00098999 | 2.0544e-07 | -6.9688e-08 | 0.0059278 | 0.0059277 | 0.0059278 | 0.99168 | -0.15783 | 0.99174 | -0.15674 | 1.6285
2 | 0.092406 | 0.023422 | -0.092185 | -0.023281 | 0.00022104 | 0.00014107 | 0.13874 | 0.13874 | 0.13874 | 0.99174 | -0.15674 | 0.98915 | -0.20665 | 38.1156
3 | -0.096357 | -0.024412 | 0.096474 | 0.024487 | 0.00011722 | 7.4829e-05 | 0.14467 | 0.14467 | 0.14467 | 0.99174 | -0.15674 | 0.99306 | -0.13145 | 39.744
4 | 0.088743 | 0.022418 | -0.088729 | -0.022409 | 1.4026e-05 | 8.9497e-06 | 0.13356 | 0.13356 | 0.13356 | 0.98915 | -0.20665 | 0.98898 | -0.20994 | 36.6929
5 | 0.21143 | 0.054184 | -0.21128 | -0.054086 | 0.00015424 | 9.8239e-05 | 0.31724 | 0.31724 | 0.31724 | 0.99306 | -0.13145 | 0.99227 | -0.14651 | 29.051
6 | -0.3079 | -0.078671 | 0.30847 | 0.07903 | 0.00056191 | 0.0003588 | 0.4619 | 0.4619 | 0.4619 | 0.99306 | -0.13145 | 0.99504 | -0.09378 | 42.2989
7 | 0.077359 | 0.019559 | -0.077264 | -0.019498 | 9.5138e-05 | 6.0649e-05 | 0.11646 | 0.11646 | 0.11646 | 0.98898 | -0.20994 | 0.98765 | -0.23562 | 31.9933
8 | 0.011369 | 0.0028503 | -0.011367 | -0.0028493 | 1.8677e-06 | 9.77e-07 | 0.017107 | 0.017107 | 0.017107 | 0.98898 | -0.20994 | 0.9888 | -0.21339 | 4.6996
9 | 0.0050802 | 0.0012732 | -0.00508 | -0.0012732 | 2.8171e-07 | 1.3115e-08 | 0.0076184 | 0.0076185 | 0.0076185 | 0.99227 | -0.14651 | 0.99221 | -0.14767 | 2.093
10 | 0.20619 | 0.052813 | -0.20595 | -0.052655 | 0.00024763 | 0.00015768 | 0.30962 | 0.30962 | 0.30962 | 0.99227 | -0.14651 | 0.99096 | -0.17133 | 28.3534
11 | -0.31201 | -0.079917 | 0.31212 | 0.07999 | 0.00011324 | 7.2314e-05 | 0.4672 | 0.4672 | 0.4672 | 0.99504 | -0.09378 | 0.99543 | -0.086292 | 42.784
12 | 0.073501 | 0.018556 | -0.073422 | -0.018505 | 7.9297e-05 | 5.053e-05 | 0.11079 | 0.11079 | 0.11079 | 0.98765 | -0.23562 | 0.98649 | -0.25817 | 30.4358
13 | 0.0037632 | 0.00094254 | -0.003763 | -0.00094265 | 2.5494e-07 | -1.0748e-07 | 0.0056695 | 0.0056696 | 0.0056696 | 0.98765 | -0.23562 | 0.98758 | -0.23704 | 1.5576
14 | 0.0094287 | 0.0023634 | -0.0094272 | -0.0023627 | 1.4855e-06 | 6.9837e-07 | 0.014189 | 0.014189 | 0.014189 | 0.9888 | -0.21339 | 0.98863 | -0.2167 | 3.8981
15 | 0.20138 | 0.051511 | -0.20113 | -0.051348 | 0.00025537 | 0.00016258 | 0.30276 | 0.30276 | 0.30276 | 0.99096 | -0.17133 | 0.98959 | -0.19757 | 27.7257
16 | -0.31492 | -0.080691 | 0.31601 | 0.081387 | 0.0010906 | 0.00069642 | 0.47138 | 0.47138 | 0.47138 | 0.99543 | -0.086292 | 0.9992 | -0.015106 | 43.1671
17 | -0.0069192 | -0.0017341 | 0.0069202 | 0.0017344 | 1.0043e-06 | 3.2626e-07 | 0.010416 | 0.010416 | 0.010416 | 0.98847 | -0.21975 | 0.98863 | -0.2167 | 2.8615
18 | 0.0048315 | 0.0012109 | -0.0048314 | -0.0012109 | 1.4882e-07 | -9.1644e-10 | 0.0072732 | 0.0072733 | 0.0072733 | 0.98847 | -0.21975 | 0.98844 | -0.22039 | 1.9981
19 | 0.069588 | 0.017544 | -0.069579 | -0.017539 | 8.2005e-06 | 5.223e-06 | 0.105 | 0.105 | 0.105 | 0.98649 | -0.25817 | 0.98636 | -0.26063 | 28.847
20 | 0.0023918 | 0.00059901 | -0.0023917 | -0.0005993 | 1.4739e-07 | -2.9288e-07 | 0.0036037 | 0.0036038 | 0.0036038 | 0.98758 | -0.23704 | 0.98751 | -0.23834 | 0.99006
21 | -0.18675 | -0.047243 | 0.18701 | 0.047407 | 0.00025723 | 0.00016365 | 0.28306 | 0.28306 | 0.28306 | 0.98226 | -0.33896 | 0.98374 | -0.31029 | 25.9215
22 | 0.18195 | 0.04604 | -0.18168 | -0.045867 | 0.00027246 | 0.00017329 | 0.27579 | 0.27579 | 0.27579 | 0.98226 | -0.33896 | 0.98065 | -0.37021 | 25.2555
23 | -0.18793 | -0.04764 | 0.18805 | 0.047715 | 0.0001184 | 7.5331e-05 | 0.28447 | 0.28447 | 0.28447 | 0.98374 | -0.31029 | 0.98441 | -0.29719 | 26.05
24 | 0.17872 | 0.045126 | -0.17854 | -0.045013 | 0.00017837 | 0.00011342 | 0.27131 | 0.27131 | 0.27131 | 0.98065 | -0.37021 | 0.97958 | -0.39106 | 24.8448
25 | 0.0018571 | 0.00046539 | -0.0018571 | -0.00046544 | 1.3212e-08 | -4.8386e-08 | 0.0028072 | 0.0028072 | 0.0028072 | 0.98441 | -0.29719 | 0.98441 | -0.29734 | 0.77121
26 | -0.18991 | -0.04818 | 0.19005 | 0.048269 | 0.00013893 | 8.8404e-05 | 0.28727 | 0.28727 | 0.28727 | 0.98441 | -0.29719 | 0.9852 | -0.28199 | 26.3071
27 | 0.12681 | 0.032016 | -0.12669 | -0.031938 | 0.00012242 | 7.7905e-05 | 0.19271 | 0.19272 | 0.19272 | 0.97958 | -0.39106 | 0.97855 | -0.41123 | 26.4719
28 | 0.05173 | 0.012996 | -0.051679 | -0.012964 | 5.118e-05 | 3.2477e-05 | 0.078591 | 0.078591 | 0.078591 | 0.97958 | -0.39106 | 0.97853 | -0.41181 | 21.5908
29 | -0.19098 | -0.048501 | 0.19118 | 0.048632 | 0.00020441 | 0.00013007 | 0.28868 | 0.28868 | 0.28868 | 0.9852 | -0.28199 | 0.98635 | -0.25978 | 26.4355
30 | 0.036225 | 0.0091077 | -0.036188 | -0.0090845 | 3.6928e-05 | 2.3227e-05 | 0.055095 | 0.055095 | 0.055095 | 0.97855 | -0.41123 | 0.97746 | -0.4326 | 15.136
31 | 0.090465 | 0.022831 | -0.090377 | -0.022775 | 8.7827e-05 | 5.6054e-05 | 0.13762 | 0.13762 | 0.13762 | 0.97855 | -0.41123 | 0.97751 | -0.43153 | 37.8078
32 | 0.043654 | 0.010953 | -0.04365 | -0.01095 | 3.2896e-06 | 2.0804e-06 | 0.066387 | 0.066387 | 0.066387 | 0.97853 | -0.41181 | 0.97845 | -0.41339 | 18.2383
33 | -0.017697 | -0.0044438 | 0.017725 | 0.00446 | 2.7264e-05 | 1.6216e-05 | 0.027078 | 0.027078 | 0.027078 | 0.97263 | -0.52764 | 0.97426 | -0.4954 | 7.4391
34 | 0.017697 | 0.0044438 | -0.017685 | -0.0044363 | 1.2628e-05 | 7.5124e-06 | 0.027078 | 0.027079 | 0.027079 | 0.97263 | -0.52764 | 0.97187 | -0.54261 | 7.4392
35 | -0.027268 | -0.0068515 | 0.02731 | 0.0068774 | 4.165e-05 | 2.5857e-05 | 0.041654 | 0.041653 | 0.041654 | 0.97426 | -0.4954 | 0.97589 | -0.46345 | 11.4433
36 | 0.0095434 | 0.0023915 | -0.009542 | -0.0023908 | 1.4113e-06 | 6.8268e-07 | 0.014576 | 0.014576 | 0.014576 | 0.97426 | -0.4954 | 0.9741 | -0.4985 | 4.0044
37 | 0.015653 | 0.0039271 | -0.015651 | -0.0039259 | 2.1342e-06 | 1.2431e-06 | 0.023968 | 0.023968 | 0.023968 | 0.97187 | -0.54261 | 0.97172 | -0.54547 | 6.5846
38 | 0.045762 | 0.011525 | -0.045733 | -0.011506 | 2.8924e-05 | 1.8312e-05 | 0.069681 | 0.069681 | 0.069681 | 0.97751 | -0.43153 | 0.97684 | -0.44475 | 19.1432
39 | 0.044615 | 0.01125 | -0.044585 | -0.011231 | 2.9281e-05 | 1.8528e-05 | 0.067939 | 0.067939 | 0.067939 | 0.97751 | -0.43153 | 0.97681 | -0.44525 | 18.6646
40 | 0.0109 | 0.002732 | -0.0109 | -0.0027318 | 4.0477e-07 | 2.1005e-07 | 0.016605 | 0.016605 | 0.016605 | 0.97684 | -0.44475 | 0.9768 | -0.44553 | 4.5617
41 | 0.034833 | 0.0087744 | -0.034804 | -0.0087565 | 2.8419e-05 | 1.7852e-05 | 0.053077 | 0.053077 | 0.053077 | 0.97684 | -0.44475 | 0.97597 | -0.46183 | 14.5816
42 | 0.037276 | 0.0093996 | -0.037203 | -0.0093532 | 7.3708e-05 | 4.6413e-05 | 0.056805 | 0.056805 | 0.056805 | 0.97681 | -0.44525 | 0.97471 | -0.48665 | 15.6058
43 | 0.037203 | 0.0093532 | -0.037177 | -0.0093373 | 2.5255e-05 | 1.5903e-05 | 0.056805 | 0.056805 | 0.056805 | 0.97471 | -0.48665 | 0.97398 | -0.50087 | 15.6059
44 | 0.029354 | 0.0073765 | -0.029323 | -0.0073572 | 3.0962e-05 | 1.9306e-05 | 0.044853 | 0.044853 | 0.044853 | 0.97398 | -0.50087 | 0.97286 | -0.523 | 12.3222
45 | -0.019174 | -0.0048081 | 0.019176 | 0.0048097 | 2.6569e-06 | 1.5958e-06 | 0.029164 | 0.029164 | 0.029164 | 0.9783 | -0.4163 | 0.97845 | -0.41339 | 8.0122
46 | 0.019174 | 0.0048081 | -0.019168 | -0.0048047 | 5.5702e-06 | 3.3457e-06 | 0.029164 | 0.029165 | 0.029165 | 0.9783 | -0.4163 | 0.97799 | -0.4224 | 8.0122
47 | 0.024474 | 0.0061408 | -0.02446 | -0.006132 | 1.4282e-05 | 8.7953e-06 | 0.037223 | 0.037223 | 0.037223 | 0.97845 | -0.41339 | 0.97782 | -0.42564 | 10.2261
48 | 0.011206 | 0.0028092 | -0.011203 | -0.0028077 | 2.8423e-06 | 1.492e-06 | 0.01705 | 0.01705 | 0.01705 | 0.97799 | -0.4224 | 0.97772 | -0.42772 | 4.6841
49 | -0.19118 | -0.048632 | 0.1916 | 0.048899 | 0.00042085 | 0.0002678 | 0.28868 | 0.28867 | 0.28868 | 0.98635 | -0.25978 | 0.98872 | -0.2142 | 26.4355
50 | 0.0079362 | 0.0019889 | -0.0079344 | -0.0019882 | 1.7465e-06 | 6.9917e-07 | 0.011944 | 0.011944 | 0.011944 | 0.98872 | -0.2142 | 0.98849 | -0.21882 | 3.2813
51 | -0.19954 | -0.050888 | 0.1997 | 0.05099 | 0.00016045 | 0.00010214 | 0.30062 | 0.30062 | 0.30062 | 0.98872 | -0.2142 | 0.98959 | -0.19757 | 27.5292
52 | 0.006047 | 0.0015148 | -0.006045 | -0.0015143 | 2.0376e-06 | 4.8763e-07 | 0.0091684 | 0.0091687 | 0.0091687 | 0.9814 | -0.35742 | 0.98104 | -0.3645 | 2.5189
53 | -0.006047 | -0.0015148 | 0.006049 | 0.0015153 | 1.9351e-06 | 4.6249e-07 | 0.0091684 | 0.0091681 | 0.0091684 | 0.9814 | -0.35742 | 0.98174 | -0.3507 | 2.5188
54 | 0.006045 | 0.0015143 | -0.0060439 | -0.0015141 | 1.1207e-06 | 2.6847e-07 | 0.0091687 | 0.0091689 | 0.0091689 | 0.98104 | -0.3645 | 0.98084 | -0.36839 | 2.5189
55 | -0.0073051 | -0.0018301 | 0.0073058 | 0.0018304 | 6.4499e-07 | 2.3537e-07 | 0.011072 | 0.011072 | 0.011072 | 0.98174 | -0.3507 | 0.98183 | -0.34885 | 3.0418
56 | 0.030648 | 0.007691 | -0.030628 | -0.0076788 | 1.9514e-05 | 1.219e-05 | 0.046682 | 0.046682 | 0.046682 | 0.97699 | -0.44194 | 0.97631 | -0.4553 | 12.8248
57 | -0.030648 | -0.007691 | 0.030661 | 0.0076995 | 1.3648e-05 | 8.5257e-06 | 0.046682 | 0.046682 | 0.046682 | 0.97699 | -0.44194 | 0.97746 | -0.4326 | 12.8248
58 | 0.022481 | 0.0056369 | -0.022476 | -0.0056335 | 5.5456e-06 | 3.3917e-06 | 0.034265 | 0.034265 | 0.034265 | 0.97631 | -0.4553 | 0.97605 | -0.46048 | 9.4135
59 | 0.0081471 | 0.0020419 | -0.0081468 | -0.0020418 | 3.074e-07 | 1.3026e-07 | 0.012417 | 0.012417 | 0.012417 | 0.97631 | -0.4553 | 0.97627 | -0.45609 | 3.4113
60 | -0.02731 | -0.0068774 | 0.027312 | 0.0068787 | 2.1207e-06 | 1.3165e-06 | 0.041653 | 0.041653 | 0.041653 | 0.97589 | -0.46345 | 0.97597 | -0.46183 | 11.4432
61 | 0.0060274 | 0.00151 | -0.0060264 | -0.0015097 | 9.8026e-07 | 2.4356e-07 | 0.009207 | 0.0092071 | 0.0092071 | 0.9741 | -0.4985 | 0.97393 | -0.50192 | 2.5294
62 | 0.0044953 | 0.001126 | -0.0044948 | -0.001126 | 5.6249e-07 | -4.7013e-08 | 0.0068196 | 0.0068197 | 0.0068197 | 0.98084 | -0.36839 | 0.9807 | -0.37102 | 1.8736
63 | 0.0051752 | 0.0012967 | -0.0051747 | -0.0012967 | 4.2696e-07 | 3.2788e-08 | 0.0077903 | 0.0077904 | 0.0077904 | 0.98849 | -0.21882 | 0.9884 | -0.22056 | 2.1402
64 | 0.0051747 | 0.0012967 | -0.0051746 | -0.0012967 | 1.3918e-07 | 1.0698e-08 | 0.0077904 | 0.0077904 | 0.0077904 | 0.9884 | -0.22056 | 0.98837 | -0.22112 | 2.1402
65 | 0.0038809 | 0.00097242 | -0.0038808 | -0.00097245 | 7.5002e-08 | -2.7083e-08 | 0.0058427 | 0.0058428 | 0.0058428 | 0.98837 | -0.22112 | 0.98835 | -0.22153 | 1.6052
66 | -0.31864 | -0.082047 | 0.31879 | 0.082142 | 0.00014904 | 9.5179e-05 | 0.4753 | 0.4753 | 0.4753 | 0.9992 | -0.015106 | 0.99971 | -0.0054975 | 43.5257
67 | -0.32048 | -0.082565 | 0.32056 | 0.08262 | 8.5781e-05 | 5.4782e-05 | 0.47781 | 0.47781 | 0.47781 | 0.99971 | -0.0054975 | 1 | 0 | 43.7558
68 | 0.068112 | 0.017171 | -0.067996 | -0.017097 | 0.00011622 | 7.4006e-05 | 0.10279 | 0.10279 | 0.10279 | 0.98636 | -0.26063 | 0.98452 | -0.29635 | 28.2389
69 | 0.001332 | 0.00033371 | -0.0013319 | -0.00033382 | 1.3219e-08 | -1.035e-07 | 0.002007 | 0.002007 | 0.002007 | 0.98751 | -0.23834 | 0.9875 | -0.23855 | 0.55138
70 | 0.012135 | 0.0030428 | -0.012132 | -0.0030412 | 3.027e-06 | 1.6356e-06 | 0.018392 | 0.018392 | 0.018392 | 0.98183 | -0.34885 | 0.98157 | -0.35408 | 5.0528
71 | -0.019441 | -0.0048731 | 0.019452 | 0.00488 | 1.1374e-05 | 6.837e-06 | 0.029464 | 0.029464 | 0.029464 | 0.98183 | -0.34885 | 0.98246 | -0.33657 | 8.0945
72 | -0.021756 | -0.0054525 | 0.021778 | 0.0054664 | 2.2871e-05 | 1.3956e-05 | 0.033314 | 0.033314 | 0.033314 | 0.97175 | -0.54504 | 0.97286 | -0.523 | 9.1522
73 | 0.015967 | 0.0040023 | -0.015966 | -0.0040014 | 1.5263e-06 | 8.9102e-07 | 0.024343 | 0.024343 | 0.024343 | 0.97605 | -0.46048 | 0.97594 | -0.46248 | 6.6876
74 | 0.015279 | 0.0038326 | -0.015276 | -0.003831 | 2.856e-06 | 1.6556e-06 | 0.023398 | 0.023398 | 0.023398 | 0.97172 | -0.54547 | 0.97153 | -0.54939 | 6.4281
75 | 0.0019929 | 0.00049895 | -0.0019927 | -0.00049942 | 1.6239e-07 | -4.7732e-07 | 0.0030446 | 0.0030448 | 0.0030448 | 0.97393 | -0.50192 | 0.97385 | -0.50363 | 0.83649
76 | 0.0040335 | 0.0010108 | -0.0040333 | -0.0010108 | 2.0017e-07 | -4.6791e-08 | 0.0061625 | 0.0061626 | 0.0061626 | 0.97393 | -0.50192 | 0.97388 | -0.50296 | 1.693
77 | 0.013197 | 0.0033093 | -0.013191 | -0.0033059 | 5.9616e-06 | 3.3213e-06 | 0.020084 | 0.020084 | 0.020084 | 0.97782 | -0.42564 | 0.97734 | -0.43512 | 5.5175
78 | -0.0096656 | -0.0024224 | 0.0096681 | 0.0024237 | 2.578e-06 | 1.2455e-06 | 0.014657 | 0.014657 | 0.014657 | 0.98128 | -0.35968 | 0.98157 | -0.35408 | 4.0266
79 | 0.002464 | 0.00061749 | -0.002464 | -0.00061753 | 2.175e-08 | -3.8624e-08 | 0.0037353 | 0.0037353 | 0.0037353 | 0.98157 | -0.35408 | 0.98156 | -0.35427 | 1.0262
80 | 0.0035878 | 0.00089871 | -0.0035877 | -0.00089874 | 6.5321e-08 | -3.2365e-08 | 0.0054435 | 0.0054436 | 0.0054436 | 0.9807 | -0.37102 | 0.98068 | -0.3714 | 1.4955
81 | -0.018352 | -0.0045999 | 0.018355 | 0.0046021 | 3.5702e-06 | 2.1292e-06 | 0.027812 | 0.027812 | 0.027812 | 0.98189 | -0.34784 | 0.98209 | -0.34376 | 7.6405
82 | 0.01535 | 0.0038478 | -0.015349 | -0.0038467 | 1.7578e-06 | 1.0154e-06 | 0.023263 | 0.023263 | 0.023263 | 0.98189 | -0.34784 | 0.98176 | -0.35025 | 6.391
83 | -0.020886 | -0.0052363 | 0.020898 | 0.0052437 | 1.2259e-05 | 7.4322e-06 | 0.031645 | 0.031645 | 0.031645 | 0.98209 | -0.34376 | 0.98272 | -0.33145 | 8.6938
84 | 0.012845 | 0.0032192 | -0.012844 | -0.0032188 | 6.6127e-07 | 3.6438e-07 | 0.019468 | 0.019468 | 0.019468 | 0.98176 | -0.35025 | 0.98171 | -0.35133 | 5.3484
85 | -0.040761 | -0.010223 | 0.040783 | 0.010237 | 2.2262e-05 | 1.405e-05 | 0.061722 | 0.061722 | 0.061722 | 0.98272 | -0.33145 | 0.98331 | -0.32 | 16.9566
86 | 0.019863 | 0.0049797 | -0.019862 | -0.0049789 | 1.1702e-06 | 7.0525e-07 | 0.030077 | 0.030077 | 0.030077 | 0.98272 | -0.33145 | 0.98266 | -0.33269 | 8.2629
87 | 0.0096943 | 0.0024294 | -0.0096939 | -0.0024293 | 3.3569e-07 | 1.6242e-07 | 0.014694 | 0.014694 | 0.014694 | 0.98171 | -0.35133 | 0.98167 | -0.35205 | 4.0368
88 | 0.0043067 | 0.0010791 | -0.004306 | -0.0010792 | 6.829e-07 | -1.0672e-07 | 0.0065171 | 0.0065173 | 0.0065173 | 0.98331 | -0.32 | 0.98314 | -0.32333 | 1.7905
89 | 0.021926 | 0.0055061 | -0.021916 | -0.0054999 | 1.0083e-05 | 6.1435e-06 | 0.033184 | 0.033184 | 0.033184 | 0.98331 | -0.32 | 0.98282 | -0.32964 | 9.1165
90 | -0.067016 | -0.016823 | 0.067092 | 0.016871 | 7.5679e-05 | 4.8185e-05 | 0.10142 | 0.10142 | 0.10142 | 0.98331 | -0.32 | 0.98452 | -0.29635 | 27.8635
91 | 0.0185 | 0.0046377 | -0.018497 | -0.0046359 | 2.9085e-06 | 1.7363e-06 | 0.028015 | 0.028015 | 0.028015 | 0.98266 | -0.33269 | 0.98249 | -0.33599 | 7.6964
92 | 0.0071615 | 0.0017946 | -0.0071606 | -0.0017943 | 8.9361e-07 | 3.1628e-07 | 0.010855 | 0.010855 | 0.010855 | 0.98167 | -0.35205 | 0.98154 | -0.35467 | 2.9823
93 | 0.021916 | 0.0054999 | -0.021914 | -0.0054986 | 2.2236e-06 | 1.3549e-06 | 0.033184 | 0.033184 | 0.033184 | 0.98282 | -0.32964 | 0.98271 | -0.33177 | 9.1165
94 | 0.016762 | 0.004201 | -0.016758 | -0.0041989 | 3.5711e-06 | 2.0984e-06 | 0.025387 | 0.025387 | 0.025387 | 0.98249 | -0.33599 | 0.98226 | -0.34046 | 6.9744
95 | 0.0050879 | 0.0012748 | -0.0050878 | -0.0012748 | 5.5944e-08 | 4.1101e-09 | 0.0077131 | 0.0077131 | 0.0077131 | 0.98154 | -0.35467 | 0.98153 | -0.3549 | 2.119
96 | 0.0098159 | 0.002459 | -0.0098155 | -0.0024588 | 3.9341e-07 | 1.9173e-07 | 0.01487 | 0.01487 | 0.01487 | 0.98226 | -0.34046 | 0.98222 | -0.3413 | 4.0851
97 | 0.0035043 | 0.00087701 | -0.0035042 | -0.00087704 | 5.6465e-08 | -3.1494e-08 | 0.0053083 | 0.0053084 | 0.0053084 | 0.98222 | -0.3413 | 0.9822 | -0.34164 | 1.4583
98 | 0.0025108 | 0.00062808 | -0.0025102 | -0.00062912 | 6.1522e-07 | -1.041e-06 | 0.0038034 | 0.0038039 | 0.0038039 | 0.9822 | -0.34164 | 0.98194 | -0.34679 | 1.045
99 | 0.0027375 | 0.00068572 | -0.0027375 | -0.00068576 | 2.9397e-08 | -3.8715e-08 | 0.00415 | 0.00415 | 0.00415 | 0.98153 | -0.3549 | 0.98151 | -0.35513 | 1.1401
100 | 0.00082504 | 0.00020647 | -0.00082503 | -0.00020677 | 1.4489e-08 | -3.0287e-07 | 0.0012507 | 0.0012508 | 0.0012508 | 0.98151 | -0.35513 | 0.98149 | -0.3555 | 0.34363
101 | -0.0054368 | -0.0013626 | 0.0054376 | 0.0013627 | 7.476e-07 | 1.1402e-07 | 0.0082789 | 0.0082788 | 0.0082789 | 0.97719 | -0.43801 | 0.97734 | -0.43512 | 2.2744
102 | 0.020873 | 0.0052379 | -0.020869 | -0.005235 | 4.7817e-06 | 2.8987e-06 | 0.031609 | 0.031609 | 0.031609 | 0.98271 | -0.33177 | 0.98246 | -0.33657 | 8.6838
103 | 0.014479 | 0.0036288 | -0.014478 | -0.0036286 | 2.4565e-07 | 1.4042e-07 | 0.022076 | 0.022076 | 0.022076 | 0.97594 | -0.46248 | 0.97593 | -0.46284 | 6.0647
104 | 0.0025712 | 0.00064398 | -0.002571 | -0.00064431 | 2.1053e-07 | -3.3062e-07 | 0.0039012 | 0.0039014 | 0.0039014 | 0.98068 | -0.3714 | 0.9806 | -0.37312 | 1.0718
105 | 0.00089584 | 0.00022448 | -0.00089584 | -0.00022452 | 2.4032e-09 | -4.221e-08 | 0.0013594 | 0.0013594 | 0.0013594 | 0.9806 | -0.37312 | 0.98059 | -0.37317 | 0.37346
106 | 0.012422 | 0.0031147 | -0.012417 | -0.0031121 | 4.7396e-06 | 2.6016e-06 | 0.019031 | 0.019031 | 0.019031 | 0.9713 | -0.55391 | 0.97089 | -0.56192 | 5.2283
107 | -0.012755 | -0.0031982 | 0.012756 | 0.0031985 | 5.3648e-07 | 2.9698e-07 | 0.019542 | 0.019542 | 0.019542 | 0.9713 | -0.55391 | 0.97134 | -0.55302 | 5.3686
108 | 0.010566 | 0.002648 | -0.010565 | -0.0026478 | 3.9241e-07 | 2.0179e-07 | 0.016193 | 0.016193 | 0.016193 | 0.97089 | -0.56192 | 0.97085 | -0.5627 | 4.4488
109 | -0.014759 | -0.0037005 | 0.014762 | 0.003702 | 2.5575e-06 | 1.4716e-06 | 0.02261 | 0.02261 | 0.02261 | 0.97134 | -0.55302 | 0.97153 | -0.54939 | 6.2116
110 | 0.0082632 | 0.0020709 | -0.0082607 | -0.0020697 | 2.5467e-06 | 1.1065e-06 | 0.012665 | 0.012665 | 0.012665 | 0.97085 | -0.5627 | 0.97053 | -0.56917 | 3.4794
111 | 0.0041497 | 0.0010394 | -0.0041497 | -0.0010394 | 4.7806e-09 | -8.3252e-10 | 0.0063621 | 0.0063621 | 0.0063621 | 0.97053 | -0.56917 | 0.97052 | -0.56919 | 1.7478
112 | 0.00091915 | 0.00022979 | -0.00091912 | -0.00023026 | 2.9974e-08 | -4.7824e-07 | 0.001409 | 0.0014092 | 0.0014092 | 0.97052 | -0.56919 | 0.97049 | -0.56988 | 0.38715
113 | 0.00091912 | 0.00023026 | -0.00091911 | -0.00023035 | 5.4119e-09 | -8.633e-08 | 0.0014092 | 0.0014092 | 0.0014092 | 0.97049 | -0.56988 | 0.97048 | -0.57 | 0.38716
114 | 0.0077641 | 0.0019458 | -0.0077632 | -0.0019455 | 9.2153e-07 | 3.707e-07 | 0.011838 | 0.011838 | 0.011838 | 0.97593 | -0.46284 | 0.9758 | -0.46533 | 3.2522
115 | 0.0025871 | 0.00064822 | -0.0025871 | -0.00064831 | 5.7155e-08 | -9.216e-08 | 0.003895 | 0.0038951 | 0.0038951 | 0.98835 | -0.22153 | 0.98832 | -0.22199 | 1.0701
116 | 0.0012932 | 0.00032404 | -0.0012932 | -0.00032411 | 8.3291e-09 | -6.9745e-08 | 0.0019471 | 0.0019471 | 0.0019471 | 0.98832 | -0.22199 | 0.98832 | -0.22213 | 0.53492
117 | 0.0067974 | 0.0017034 | -0.0067972 | -0.0017034 | 1.8144e-07 | 5.9868e-08 | 0.010365 | 0.010365 | 0.010365 | 0.9758 | -0.46533 | 0.97577 | -0.46589 | 2.8477
118 | 0.005775 | 0.0014472 | -0.0057749 | -0.0014472 | 1.3599e-07 | 2.8629e-08 | 0.0088067 | 0.0088067 | 0.0088067 | 0.97577 | -0.46589 | 0.97575 | -0.46639 | 2.4194
119 | 0.0046549 | 0.0011665 | -0.0046548 | -0.0011665 | 8.838e-08 | -1.854e-09 | 0.0070987 | 0.0070987 | 0.0070987 | 0.97575 | -0.46639 | 0.97573 | -0.46678 | 1.9502
120 | 0.003552 | 0.00089006 | -0.0035519 | -0.00089009 | 5.2678e-08 | -2.6081e-08 | 0.0054168 | 0.0054168 | 0.0054168 | 0.97573 | -0.46678 | 0.97571 | -0.4671 | 1.4881
121 | 0.002398 | 0.0006009 | -0.002398 | -0.00060094 | 2.4081e-08 | -4.4556e-08 | 0.0036571 | 0.0036571 | 0.0036571 | 0.97571 | -0.4671 | 0.9757 | -0.46731 | 1.0047
122 | 0.0012574 | 0.00031508 | -0.0012574 | -0.00031514 | 6.1609e-09 | -5.1855e-08 | 0.0019176 | 0.0019177 | 0.0019177 | 0.9757 | -0.46731 | 0.97569 | -0.46741 | 0.52683

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.329 | 0.08432

## res_load
| p_mw | q_mvar
0 | 0.0031004 | 0.00077703
1 | 0.00085011 | 0.00021306
2 | 0.0034424 | 0.00086274
3 | 0.003542 | 0.00088771
4 | 0.0019388 | 0.0004859
5 | 0.00508 | 0.0012732
6 | 0.0045651 | 0.0011441
7 | 0.0027989 | 0.00070147
8 | 0.0020876 | 0.00052321
9 | 0.0025071 | 0.00062833
10 | 0.0048314 | 0.0012109
11 | 0.003834 | 0.00096089
12 | 0.0013711 | 0.00034364
13 | 0.0048007 | 0.0012032
14 | 0.00092823 | 0.00023264
15 | 0.002956 | 0.00074084
16 | 0.0018571 | 0.00046544
17 | 0.00092844 | 0.00023269
18 | 0.008025 | 0.0020112
19 | 0.0020317 | 0.00050919
20 | 0.0073091 | 0.0018318
21 | 0.0078236 | 0.0019608
22 | 0.0079622 | 0.0019955
23 | 0.0012561 | 0.00031482
24 | 0.0055263 | 0.001385
25 | 0.0035146 | 0.00088085
26 | 0.0074926 | 0.0018778
27 | 0.0109 | 0.0027318
28 | 0.0015485 | 0.0003881
29 | 0.0014273 | 0.00035771
30 | 0.0027593 | 0.00069154
31 | 0.0012937 | 0.00032423
32 | 0.0026301 | 0.00065917
33 | 0.001688 | 0.00042305
34 | 0.006786 | 0.0017007
35 | 0.0014672 | 0.00036772
36 | 0.0010597 | 0.00026559
37 | 0.021756 | 0.0054525
38 | 0.0075443 | 0.0018908
39 | 0.0065084 | 0.0016312
40 | 0.0081468 | 0.0020418
41 | 0.00037207 | 9.3249e-05
42 | 0.011263 | 0.0028227
43 | 0.011203 | 0.0028077
44 | 0.0096656 | 0.0024224
45 | 0.00090701 | 0.00022732
46 | 0.0030013 | 0.00075219
47 | 0.0025304 | 0.00063419
48 | 0.0025039 | 0.00062755
49 | 0.0031498 | 0.00078941
50 | 0.0013617 | 0.00034129
51 | 0.0025324 | 0.00063468
52 | 0.004306 | 0.0010792
53 | 0.00090413 | 0.0002266
54 | 0.0017353 | 0.0004349
55 | 0.0020728 | 0.00051948
56 | 0.0069426 | 0.00174
57 | 0.0063113 | 0.0015818
58 | 0.00099337 | 0.00024896
59 | 0.0025102 | 0.00062912
60 | 0.0013319 | 0.00033382
61 | 0.0023503 | 0.00058905
62 | 0.0019124 | 0.0004793
63 | 0.00082503 | 0.00020677
64 | 0.0054368 | 0.0013626
65 | 0.0077536 | 0.0019432
66 | 0.0010403 | 0.00026073
67 | 0.001487 | 0.00037267
68 | 0.0014164 | 0.00035497
69 | 0.002464 | 0.00061753
70 | 0.0010165 | 0.00025476
71 | 0.0016752 | 0.00041984
72 | 0.00089584 | 0.00022452
73 | 0.0040333 | 0.0010108
74 | 0.0019927 | 0.00049942
75 | 0.00033343 | 8.3565e-05
76 | 0.0018515 | 0.00046402
77 | 0.0020031 | 0.00050202
78 | 0.0023022 | 0.00057698
79 | 0.00051451 | 0.00012895
80 | 0.004111 | 0.0010303
81 | 0.0032305 | 0.00080965
82 | 0.00091911 | 0.00023035
83 | 0.0067143 | 0.0016828
84 | 0.0012937 | 0.00032423
85 | 0.0012938 | 0.00032427
86 | 0.0012932 | 0.00032411
87 | 0.00096575 | 0.00024204
88 | 0.0010222 | 0.00025619
89 | 0.00112 | 0.0002807
90 | 0.0011028 | 0.0002764
91 | 0.0011539 | 0.00028919
92 | 0.0011406 | 0.00028586
93 | 0.0012574 | 0.00031514

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1