## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_121-13_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_121-13_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_121-13_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_121-13_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_121-13_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_121-13_0_4_node_91 | 0.4 | n |  | TRUE
6 | bus_LV_121-13_0_4_node_97 | 0.4 | n |  | TRUE
7 | bus_LV_121-13_0_4_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_121-13_0_4_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_121-13_0_4_node_30 | 0.4 | n |  | TRUE
10 | bus_LV_121-13_0_4_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_121-13_0_4_node_36 | 0.4 | n |  | TRUE
12 | bus_LV_121-13_0_4_node_120 | 0.4 | n |  | TRUE
13 | bus_LV_121-13_0_4_node_39 | 0.4 | n |  | TRUE
14 | bus_LV_121-13_0_4_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_121-13_0_4_node_38 | 0.4 | n |  | TRUE
16 | bus_LV_121-13_0_4_node_90 | 0.4 | n |  | TRUE
17 | bus_LV_121-13_0_4_node_92 | 0.4 | n |  | TRUE
18 | bus_LV_121-13_0_4_node_40 | 0.4 | n |  | TRUE
19 | bus_LV_121-13_0_4_node_100 | 0.4 | n |  | TRUE
20 | bus_LV_121-13_0_4_node_114 | 0.4 | n |  | TRUE
21 | bus_LV_121-13_0_4_node_21 | 0.4 | n |  | TRUE
22 | bus_LV_121-13_0_4_node_32 | 0.4 | n |  | TRUE
23 | bus_LV_121-13_0_4_node_20 | 0.4 | n |  | TRUE
24 | bus_LV_121-13_0_4_node_29 | 0.4 | n |  | TRUE
25 | bus_LV_121-13_0_4_node_94 | 0.4 | n |  | TRUE
26 | bus_LV_121-13_0_4_node_46 | 0.4 | n |  | TRUE
27 | bus_LV_121-13_0_4_node_34 | 0.4 | n |  | TRUE
28 | bus_LV_121-13_0_4_node_59 | 0.4 | n |  | TRUE
29 | bus_LV_121-13_0_4_node_58 | 0.4 | n |  | TRUE
30 | bus_LV_121-13_0_4_node_67 | 0.4 | n |  | TRUE
31 | bus_LV_121-13_0_4_node_37 | 0.4 | n |  | TRUE
32 | bus_LV_121-13_0_4_node_80 | 0.4 | n |  | TRUE
33 | bus_LV_121-13_0_4_node_88 | 0.4 | n |  | TRUE
34 | bus_LV_121-13_0_4_node_10 | 0.4 | n |  | TRUE
35 | bus_LV_121-13_0_4_node_11 | 0.4 | n |  | TRUE
36 | bus_LV_121-13_0_4_node_12 | 0.4 | n |  | TRUE
37 | bus_LV_121-13_0_4_node_13 | 0.4 | n |  | TRUE
38 | bus_LV_121-13_0_4_node_22 | 0.4 | n |  | TRUE
39 | bus_LV_121-13_0_4_node_19 | 0.4 | n |  | TRUE
40 | bus_LV_121-13_0_4_node_25 | 0.4 | n |  | TRUE
41 | bus_LV_121-13_0_4_node_14 | 0.4 | n |  | TRUE
42 | bus_LV_121-13_0_4_node_15 | 0.4 | n |  | TRUE
43 | bus_LV_121-13_0_4_node_16 | 0.4 | n |  | TRUE
44 | bus_LV_121-13_0_4_node_17 | 0.4 | n |  | TRUE
45 | bus_LV_121-13_0_4_node_18 | 0.4 | n |  | TRUE
46 | bus_LV_121-13_0_4_node_96 | 0.4 | n |  | TRUE
47 | bus_LV_121-13_0_4_node_26 | 0.4 | n |  | TRUE
48 | bus_LV_121-13_0_4_node_93 | 0.4 | n |  | TRUE
49 | bus_LV_121-13_0_4_node_28 | 0.4 | n |  | TRUE
50 | bus_LV_121-13_0_4_node_31 | 0.4 | n |  | TRUE
51 | bus_LV_121-13_0_4_node_24 | 0.4 | n |  | TRUE
52 | bus_LV_121-13_0_4_node_23 | 0.4 | n |  | TRUE
53 | bus_LV_121-13_0_4_node_27 | 0.4 | n |  | TRUE
54 | bus_LV_121-13_0_4_node_89 | 0.4 | n |  | TRUE
55 | bus_LV_121-13_0_4_node_95 | 0.4 | n |  | TRUE
56 | bus_LV_121-13_0_4_node_33 | 0.4 | n |  | TRUE
57 | bus_LV_121-13_0_4_node_35 | 0.4 | n |  | TRUE
58 | bus_LV_121-13_0_4_node_65 | 0.4 | n |  | TRUE
59 | bus_LV_121-13_0_4_node_117 | 0.4 | n |  | TRUE
60 | bus_LV_121-13_0_4_node_56 | 0.4 | n |  | TRUE
61 | bus_LV_121-13_0_4_node_115 | 0.4 | n |  | TRUE
62 | bus_LV_121-13_0_4_node_41 | 0.4 | n |  | TRUE
63 | bus_LV_121-13_0_4_node_42 | 0.4 | n |  | TRUE
64 | bus_LV_121-13_0_4_node_43 | 0.4 | n |  | TRUE
65 | bus_LV_121-13_0_4_node_44 | 0.4 | n |  | TRUE
66 | bus_LV_121-13_0_4_node_45 | 0.4 | n |  | TRUE
67 | bus_LV_121-13_0_4_node_47 | 0.4 | n |  | TRUE
68 | bus_LV_121-13_0_4_node_70 | 0.4 | n |  | TRUE
69 | bus_LV_121-13_0_4_node_81 | 0.4 | n |  | TRUE
70 | bus_LV_121-13_0_4_node_78 | 0.4 | n |  | TRUE
71 | bus_LV_121-13_0_4_node_66 | 0.4 | n |  | TRUE
72 | bus_LV_121-13_0_4_node_68 | 0.4 | n |  | TRUE
73 | bus_LV_121-13_0_4_node_64 | 0.4 | n |  | TRUE
74 | bus_LV_121-13_0_4_node_99 | 0.4 | n |  | TRUE
75 | bus_LV_121-13_0_4_node_79 | 0.4 | n |  | TRUE
76 | bus_LV_121-13_0_4_node_48 | 0.4 | n |  | TRUE
77 | bus_LV_121-13_0_4_node_49 | 0.4 | n |  | TRUE
78 | bus_LV_121-13_0_4_node_50 | 0.4 | n |  | TRUE
79 | bus_LV_121-13_0_4_node_51 | 0.4 | n |  | TRUE
80 | bus_LV_121-13_0_4_node_52 | 0.4 | n |  | TRUE
81 | bus_LV_121-13_0_4_node_63 | 0.4 | n |  | TRUE
82 | bus_LV_121-13_0_4_node_62 | 0.4 | n |  | TRUE
83 | bus_LV_121-13_0_4_node_98 | 0.4 | n |  | TRUE
84 | bus_LV_121-13_0_4_node_54 | 0.4 | n |  | TRUE
85 | bus_LV_121-13_0_4_node_53 | 0.4 | n |  | TRUE
86 | bus_LV_121-13_0_4_node_55 | 0.4 | n |  | TRUE
87 | bus_LV_121-13_0_4_node_57 | 0.4 | n |  | TRUE
88 | bus_LV_121-13_0_4_node_71 | 0.4 | n |  | TRUE
89 | bus_LV_121-13_0_4_node_123 | 0.4 | n |  | TRUE
90 | bus_LV_121-13_0_4_node_101 | 0.4 | n |  | TRUE
91 | bus_LV_121-13_0_4_node_72 | 0.4 | n |  | TRUE
92 | bus_LV_121-13_0_4_node_60 | 0.4 | n |  | TRUE
93 | bus_LV_121-13_0_4_node_61 | 0.4 | n |  | TRUE
94 | bus_LV_121-13_0_4_node_69 | 0.4 | n |  | TRUE
95 | bus_LV_121-13_0_4_node_121 | 0.4 | n |  | TRUE
96 | bus_LV_121-13_0_4_node_122 | 0.4 | n |  | TRUE
97 | bus_LV_121-13_0_4_node_76 | 0.4 | n |  | TRUE
98 | bus_LV_121-13_0_4_node_74 | 0.4 | n |  | TRUE
99 | bus_LV_121-13_0_4_node_73 | 0.4 | n |  | TRUE
100 | bus_LV_121-13_0_4_node_75 | 0.4 | n |  | TRUE
101 | bus_LV_121-13_0_4_node_77 | 0.4 | n |  | TRUE
102 | bus_LV_121-13_0_4_node_102 | 0.4 | n |  | TRUE
103 | bus_LV_121-13_0_4_node_103 | 0.4 | n |  | TRUE
104 | bus_LV_121-13_0_4_node_82 | 0.4 | n |  | TRUE
105 | bus_LV_121-13_0_4_node_83 | 0.4 | n |  | TRUE
106 | bus_LV_121-13_0_4_node_84 | 0.4 | n |  | TRUE
107 | bus_LV_121-13_0_4_node_85 | 0.4 | n |  | TRUE
108 | bus_LV_121-13_0_4_node_86 | 0.4 | n |  | TRUE
109 | bus_LV_121-13_0_4_node_87 | 0.4 | n |  | TRUE
110 | bus_LV_121-13_0_4_node_104 | 0.4 | n |  | TRUE
111 | bus_LV_121-13_0_4_node_108 | 0.4 | n |  | TRUE
112 | bus_LV_121-13_0_4_node_106 | 0.4 | n |  | TRUE
113 | bus_LV_121-13_0_4_node_118 | 0.4 | n |  | TRUE
114 | bus_LV_121-13_0_4_node_105 | 0.4 | n |  | TRUE
115 | bus_LV_121-13_0_4_node_107 | 0.4 | n |  | TRUE
116 | bus_LV_121-13_0_4_node_109 | 0.4 | n |  | TRUE
117 | bus_LV_121-13_0_4_node_113 | 0.4 | n |  | TRUE
118 | bus_LV_121-13_0_4_node_111 | 0.4 | n |  | TRUE
119 | bus_LV_121-13_0_4_node_112 | 0.4 | n |  | TRUE
120 | bus_LV_121-13_0_4_node_116 | 0.4 | n |  | TRUE
121 | bus_LV_121-13_0_4_node_119 | 0.4 | n |  | TRUE
122 | bus_MV_357_0_node_29 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_121-13_0_4_load_0 | 0 | 0.0018529 | 0.00046437 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_121-13_0_4_load_1 | 1 | 0.001715 | 0.00042983 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_121-13_0_4_load_3 | 3 | 0.0019922 | 0.0004993 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_121-13_0_4_load_91 | 5 | 0.0068546 | 0.0017179 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_121-13_0_4_load_97 | 6 | 0.0041244 | 0.0010337 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_121-13_0_4_load_30 | 9 | 0.0055928 | 0.0014017 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_121-13_0_4_load_120 | 12 | 0.0055888 | 0.0014007 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_121-13_0_4_load_39 | 13 | 0.0041925 | 0.0010507 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_121-13_0_4_load_38 | 15 | 0.0049431 | 0.0012389 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_121-13_0_4_load_92 | 17 | 0.00207 | 0.00051879 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_121-13_0_4_load_114 | 20 | 0.0026912 | 0.00067448 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_121-13_0_4_load_20 | 23 | 0.011749 | 0.0029445 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_121-13_0_4_load_29 | 24 | 0.0079228 | 0.0019856 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_121-13_0_4_load_94 | 25 | 0.010968 | 0.0027488 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_121-13_0_4_load_46 | 26 | 0.0060616 | 0.0015192 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_121-13_0_4_load_34 | 27 | 0.0067229 | 0.0016849 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_121-13_0_4_load_59 | 28 | 0.002245 | 0.00056266 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_121-13_0_4_load_58 | 29 | 0.002951 | 0.00073959 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_121-13_0_4_load_67 | 30 | 0.0053902 | 0.0013509 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_121-13_0_4_load_37 | 31 | 0.0048175 | 0.0012074 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_121-13_0_4_load_88 | 33 | 0.0081923 | 0.0020532 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_121-13_0_4_load_10 | 34 | 0.0020228 | 0.00050697 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_121-13_0_4_load_11 | 35 | 0.0019515 | 0.0004891 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_121-13_0_4_load_12 | 36 | 0.0015542 | 0.00038951 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_121-13_0_4_load_22 | 38 | 0.0085326 | 0.0021385 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_121-13_0_4_load_19 | 39 | 0.0028121 | 0.00070479 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_121-13_0_4_load_14 | 41 | 0.0026217 | 0.00065707 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_121-13_0_4_load_15 | 42 | 0.0025216 | 0.00063197 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_121-13_0_4_load_16 | 43 | 0.0040759 | 0.0010215 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_121-13_0_4_load_17 | 44 | 0.0019027 | 0.00047687 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_121-13_0_4_load_18 | 45 | 0.0033265 | 0.0008337 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_121-13_0_4_load_26 | 47 | 0.0019835 | 0.00049711 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_121-13_0_4_load_93 | 48 | 0.0018494 | 0.00046351 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_121-13_0_4_load_28 | 49 | 0.0019274 | 0.00048305 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_121-13_0_4_load_31 | 50 | 0.0069802 | 0.0017494 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_121-13_0_4_load_24 | 51 | 0.0017142 | 0.00042963 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_121-13_0_4_load_23 | 52 | 0.0082845 | 0.0020763 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_121-13_0_4_load_27 | 53 | 0.0047926 | 0.0012012 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_121-13_0_4_load_89 | 54 | 0.0021481 | 0.00053836 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_121-13_0_4_load_95 | 55 | 0.0017743 | 0.00044468 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_121-13_0_4_load_33 | 56 | 0.006036 | 0.0015128 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_121-13_0_4_load_35 | 57 | 0.0020097 | 0.00050368 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_121-13_0_4_load_117 | 59 | 0.00062389 | 0.00015636 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_121-13_0_4_load_115 | 61 | 0.0026161 | 0.00065565 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_121-13_0_4_load_41 | 62 | 0.0016654 | 0.00041739 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_121-13_0_4_load_42 | 63 | 0.0020369 | 0.0005105 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_121-13_0_4_load_43 | 64 | 0.0012428 | 0.00031148 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_121-13_0_4_load_44 | 65 | 0.0016834 | 0.0004219 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_121-13_0_4_load_45 | 66 | 0.001292 | 0.00032381 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_121-13_0_4_load_70 | 68 | 0.001411 | 0.00035362 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_121-13_0_4_load_81 | 69 | 0.00021257 | 5.3276e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_121-13_0_4_load_78 | 70 | 0.0020192 | 0.00050606 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_121-13_0_4_load_68 | 72 | 0.0075065 | 0.0018813 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_121-13_0_4_load_64 | 73 | 0.0039551 | 0.00099123 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_121-13_0_4_load_79 | 75 | 0.0022624 | 0.00056701 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_121-13_0_4_load_48 | 76 | 0.0011791 | 0.00029551 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_121-13_0_4_load_49 | 77 | 0.0012577 | 0.00031521 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_121-13_0_4_load_50 | 78 | 0.0014623 | 0.00036649 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_121-13_0_4_load_51 | 79 | 0.0010646 | 0.00026681 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_121-13_0_4_load_52 | 80 | 0.001368 | 0.00034285 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_121-13_0_4_load_63 | 81 | 0.0019067 | 0.00047787 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_121-13_0_4_load_62 | 82 | 0.0021755 | 0.00054524 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_121-13_0_4_load_54 | 84 | 0.0011791 | 0.00029552 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_121-13_0_4_load_53 | 85 | 0.0012022 | 0.0003013 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_121-13_0_4_load_55 | 86 | 0.0011937 | 0.00029916 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_121-13_0_4_load_57 | 87 | 0.0034101 | 0.00085466 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_121-13_0_4_load_71 | 88 | 0.001259 | 0.00031554 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_121-13_0_4_load_123 | 89 | 0.0010202 | 0.00025568 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_121-13_0_4_load_101 | 90 | 0.0010884 | 0.00027279 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_121-13_0_4_load_72 | 91 | 0.0012573 | 0.00031512 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_121-13_0_4_load_60 | 92 | 0.0019008 | 0.00047639 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_121-13_0_4_load_61 | 93 | 0.00196 | 0.00049122 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_121-13_0_4_load_121 | 95 | 0.0037476 | 0.00093923 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_121-13_0_4_load_122 | 96 | 0.0025264 | 0.00063319 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_121-13_0_4_load_76 | 97 | 0.0011144 | 0.0002793 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_121-13_0_4_load_74 | 98 | 0.0011922 | 0.0002988 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_121-13_0_4_load_73 | 99 | 0.0012314 | 0.00030861 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_121-13_0_4_load_75 | 100 | 0.0012189 | 0.00030547 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_121-13_0_4_load_77 | 101 | 0.0038922 | 0.00097547 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_121-13_0_4_load_102 | 102 | 0.000203 | 5.0878e-05 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_121-13_0_4_load_103 | 103 | 0.0029933 | 0.0007502 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_121-13_0_4_load_82 | 104 | 0.0030772 | 0.00077122 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_121-13_0_4_load_83 | 105 | 0.0033773 | 0.00084643 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_121-13_0_4_load_85 | 107 | 0.0047998 | 0.0012029 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_121-13_0_4_load_104 | 110 | 0.0010407 | 0.00026081 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_121-13_0_4_load_106 | 112 | 0.0057649 | 0.0014448 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_121-13_0_4_load_118 | 113 | 0.0044318 | 0.0011107 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_121-13_0_4_load_105 | 114 | 0.027623 | 0.0069229 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_121-13_0_4_load_107 | 115 | 0.029589 | 0.0074157 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_121-13_0_4_load_113 | 117 | 0.024996 | 0.0062645 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_121-13_0_4_load_111 | 118 | 0.04342 | 0.010882 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_121-13_0_4_load_112 | 119 | 0.016613 | 0.0041635 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_121-13_0_4_load_116 | 120 | 0.00064189 | 0.00016087 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_121-13_0_4_load_119 | 121 | 0.00060808 | 0.0001524 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 54 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_121-13_0_4_line_0 |  | 0 | 1 | 0.0059958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_121-13_0_4_line_1 |  | 0 | 2 | 0.10062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_121-13_0_4_line_2 |  | 1 | 3 | 0.010561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_121-13_0_4_line_3 |  | 2 | 4 | 0.02119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_121-13_0_4_line_4 |  | 3 | 5 | 0.0023409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_121-13_0_4_line_5 |  | 4 | 6 | 0.03124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_121-13_0_4_line_6 |  | 5 | 17 | 0.0038465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_121-13_0_4_line_7 |  | 7 | 8 | 0.087779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_121-13_0_4_line_8 |  | 7 | 9 | 0.048784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_121-13_0_4_line_9 |  | 8 | 13 | 0.012699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_121-13_0_4_line_10 |  | 9 | 24 | 0.0363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_121-13_0_4_line_11 |  | 10 | 11 | 0.008464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_121-13_0_4_line_12 |  | 10 | 12 | 0.039393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_121-13_0_4_line_13 |  | 11 | 26 | 0.013947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_121-13_0_4_line_14 |  | 11 | 27 | 0.023256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_121-13_0_4_line_15 |  | 13 | 30 | 0.017415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_121-13_0_4_line_16 |  | 14 | 15 | 0.013018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_121-13_0_4_line_17 |  | 14 | 16 | 0.02399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_121-13_0_4_line_18 |  | 15 | 31 | 0.01807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_121-13_0_4_line_19 |  | 16 | 32 | 0.034664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
20 | LV_121-13_0_4_line_20 |  | 16 | 33 | 0.031765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_121-13_0_4_line_21 |  | 17 | 48 | 0.011209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_121-13_0_4_line_22 |  | 18 | 19 | 0.044272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_121-13_0_4_line_23 |  | 18 | 20 | 0.013791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_121-13_0_4_line_24 |  | 19 | 59 | 0.01308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_121-13_0_4_line_25 |  | 19 | 60 | 0.082897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_121-13_0_4_line_26 |  | 20 | 61 | 9.7197e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_121-13_0_4_line_27 |  | 21 | 22 | 0.019912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
28 | LV_121-13_0_4_line_28 |  | 21 | 23 | 0.022421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
29 | LV_121-13_0_4_line_29 |  | 22 | 25 | 0.026791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
30 | LV_121-13_0_4_line_30 |  | 23 | 39 | 0.022397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_121-13_0_4_line_31 |  | 24 | 50 | 0.024928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_121-13_0_4_line_32 |  | 25 | 55 | 0.042902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
33 | LV_121-13_0_4_line_33 |  | 26 | 58 | 0.025034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_121-13_0_4_line_34 |  | 27 | 56 | 0.017561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_121-13_0_4_line_35 |  | 28 | 29 | 0.025695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_121-13_0_4_line_36 |  | 29 | 92 | 0.00096633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_121-13_0_4_line_37 |  | 30 | 58 | 0.038043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_121-13_0_4_line_38 |  | 32 | 102 | 0.020069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_121-13_0_4_line_39 |  | 32 | 75 | 0.0017266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
40 | LV_121-13_0_4_line_40 |  | 33 | 54 | 0.0034605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
41 | LV_121-13_0_4_line_41 |  | 34 | 35 | 0.004875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_121-13_0_4_line_42 |  | 34 | 36 | 0.021323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_121-13_0_4_line_43 |  | 35 | 37 | 0.021027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_121-13_0_4_line_44 |  | 37 | 38 | 0.019403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_121-13_0_4_line_45 |  | 37 | 39 | 0.0013946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
46 | LV_121-13_0_4_line_46 |  | 38 | 40 | 0.02338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
47 | LV_121-13_0_4_line_47 |  | 40 | 51 | 0.012798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_121-13_0_4_line_48 |  | 40 | 46 | 0.006961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_121-13_0_4_line_49 |  | 41 | 42 | 0.009045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_121-13_0_4_line_50 |  | 41 | 43 | 0.0032689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_121-13_0_4_line_51 |  | 42 | 44 | 0.022213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_121-13_0_4_line_52 |  | 43 | 45 | 0.022755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_121-13_0_4_line_53 |  | 44 | 46 | 0.024482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_121-13_0_4_line_54 |  | 45 | 47 | 0.0090103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_121-13_0_4_line_55 |  | 46 | 48 | 0.0023588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_121-13_0_4_line_56 |  | 47 | 49 | 0.009741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_121-13_0_4_line_57 |  | 49 | 53 | 0.011503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_121-13_0_4_line_58 |  | 51 | 52 | 0.023841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_121-13_0_4_line_59 |  | 55 | 109 | 0.020915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
60 | LV_121-13_0_4_line_60 |  | 56 | 57 | 0.0093773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_121-13_0_4_line_61 |  | 58 | 72 | 0.018041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_121-13_0_4_line_62 |  | 58 | 73 | 0.020753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_121-13_0_4_line_63 |  | 59 | 113 | 0.004622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_121-13_0_4_line_64 |  | 60 | 83 | 0.072532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_121-13_0_4_line_65 |  | 60 | 84 | 0.029699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_121-13_0_4_line_66 |  | 60 | 80 | 0.012383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_121-13_0_4_line_67 |  | 61 | 120 | 0.010764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_121-13_0_4_line_68 |  | 62 | 63 | 0.022392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_121-13_0_4_line_69 |  | 62 | 64 | 0.016834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_121-13_0_4_line_70 |  | 63 | 65 | 0.011342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_121-13_0_4_line_71 |  | 64 | 66 | 0.0033641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_121-13_0_4_line_72 |  | 65 | 67 | 0.004356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_121-13_0_4_line_73 |  | 66 | 68 | 0.0055629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_121-13_0_4_line_74 |  | 67 | 69 | 0.019378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
75 | LV_121-13_0_4_line_75 |  | 67 | 70 | 0.036616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
76 | LV_121-13_0_4_line_76 |  | 68 | 71 | 0.013167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_121-13_0_4_line_77 |  | 69 | 74 | 0.044263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
78 | LV_121-13_0_4_line_78 |  | 70 | 75 | 0.0047305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
79 | LV_121-13_0_4_line_79 |  | 71 | 94 | 0.022094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_121-13_0_4_line_80 |  | 71 | 73 | 0.011416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_121-13_0_4_line_81 |  | 74 | 90 | 0.022487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
82 | LV_121-13_0_4_line_82 |  | 74 | 83 | 0.044397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_121-13_0_4_line_83 |  | 76 | 77 | 0.00017983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_121-13_0_4_line_84 |  | 76 | 78 | 0.034016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_121-13_0_4_line_85 |  | 77 | 79 | 0.0010135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_121-13_0_4_line_86 |  | 78 | 80 | 0.00015127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_121-13_0_4_line_87 |  | 79 | 81 | 0.023971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_121-13_0_4_line_88 |  | 81 | 82 | 0.010657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_121-13_0_4_line_89 |  | 82 | 93 | 0.010797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_121-13_0_4_line_90 |  | 83 | 89 | 0.007755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_121-13_0_4_line_91 |  | 84 | 85 | 0.017054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_121-13_0_4_line_92 |  | 85 | 86 | 0.0061421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_121-13_0_4_line_93 |  | 86 | 87 | 0.012252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_121-13_0_4_line_94 |  | 87 | 88 | 0.025504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_121-13_0_4_line_95 |  | 88 | 91 | 0.0013367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_121-13_0_4_line_96 |  | 90 | 108 | 0.050154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
97 | LV_121-13_0_4_line_97 |  | 91 | 97 | 0.00036702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_121-13_0_4_line_98 |  | 92 | 93 | 0.024668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_121-13_0_4_line_99 |  | 94 | 95 | 0.002816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_121-13_0_4_line_100 |  | 94 | 96 | 0.022607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_121-13_0_4_line_101 |  | 97 | 98 | 0.031532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_121-13_0_4_line_102 |  | 98 | 99 | 0.00088309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_121-13_0_4_line_103 |  | 99 | 100 | 0.00040659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_121-13_0_4_line_104 |  | 100 | 101 | 0.0028319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_121-13_0_4_line_105 |  | 102 | 103 | 0.012072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_121-13_0_4_line_106 |  | 104 | 105 | 0.0016323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_121-13_0_4_line_107 |  | 104 | 106 | 0.016818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_121-13_0_4_line_108 |  | 105 | 107 | 0.022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_121-13_0_4_line_109 |  | 106 | 108 | 0.023679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
110 | LV_121-13_0_4_line_110 |  | 106 | 109 | 0.03995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
111 | LV_121-13_0_4_line_111 |  | 108 | 110 | 0.013813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_121-13_0_4_line_112 |  | 109 | 111 | 0.041806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
113 | LV_121-13_0_4_line_113 |  | 111 | 112 | 0.032078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
114 | LV_121-13_0_4_line_114 |  | 112 | 114 | 0.0015497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
115 | LV_121-13_0_4_line_115 |  | 113 | 121 | 0.0095013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_121-13_0_4_line_116 |  | 114 | 115 | 0.00085126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
117 | LV_121-13_0_4_line_117 |  | 115 | 116 | 0.021063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
118 | LV_121-13_0_4_line_118 |  | 116 | 117 | 0.029022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_121-13_0_4_line_119 |  | 116 | 118 | 0.0092915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_121-13_0_4_line_120 |  | 118 | 119 | 0.014573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_121-13_0_4_trafo_89 | 0.63 MVA 20/0.4 kV | 122 | 54 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2702358.7669 | 1241069.5401 | 2702359.5019 | 1241063.5895
1 | 2702337.715 | 1241167.777 | 2702341.0997 | 1241147.3641 | 2702346.1479 | 1241125.2118 | 2702356.6957 | 1241086.3082 | 2702358.7669 | 1241069.5401
2 | 2702359.5019 | 1241063.5895 | 2702360.7965 | 1241053.1086
3 | 2702337.715 | 1241167.777 | 2702349.1916 | 1241162.6931 | 2702353.1063 | 1241154.9547
4 | 2702361.0835 | 1241050.7853 | 2702360.7965 | 1241053.1086
5 | 2702353.1063 | 1241154.9547 | 2702360.0708 | 1241124.5004
6 | 2702361.0835 | 1241050.7853 | 2702361.555 | 1241046.9679
7 | 2702410.0481 | 1241169.1365 | 2702418.0035 | 1241168.2731 | 2702417.2409 | 1241152.8703 | 2702418.4911 | 1241130.3968 | 2702422.5597 | 1241095.796 | 2702425.7375 | 1241096.14 | 2702429.5268 | 1241096.5501
8 | 2702410.0481 | 1241169.1365 | 2702409.7881 | 1241165.7961 | 2702409.5435 | 1241161.5665 | 2702410.3266 | 1241153.4404 | 2702410.9388 | 1241146.4567 | 2702414.4822 | 1241120.6765
9 | 2702429.5268 | 1241096.5501 | 2702436.4638 | 1241097.2926 | 2702437.7419 | 1241098.6045 | 2702441.5746 | 1241099.2743
10 | 2702414.4822 | 1241120.6765 | 2702414.6058 | 1241119.7772 | 2702418.7559 | 1241084.6288
11 | 2702477.3488 | 1241149.683 | 2702472.8612 | 1241156.8666
12 | 2702472.8612 | 1241156.8666 | 2702443.68 | 1241141.8625 | 2702437.1358 | 1241141.1723
13 | 2702477.3488 | 1241149.683 | 2702483.2289 | 1241137.0364
14 | 2702477.3488 | 1241149.683 | 2702496.0509 | 1241161.0368 | 2702496.7328 | 1241159.8406
15 | 2702441.5746 | 1241099.2743 | 2702456.3121 | 1241101.8497 | 2702458.7007 | 1241102.4145
16 | 2702457.4651 | 1241035.9745 | 2702456.7187 | 1241041.5326 | 2702453.2102 | 1241045.008 | 2702452.8684 | 1241047.4558
17 | 2702460.6588 | 1241012.2002 | 2702457.4651 | 1241035.9745
18 | 2702450.319 | 1241065.3438 | 2702450.4745 | 1241064.5981 | 2702452.8684 | 1241047.4558
19 | 2702460.6588 | 1241012.2002 | 2702477.5788 | 1241005.0424 | 2702493.8224 | 1241002.8989
20 | 2702460.6588 | 1241012.2002 | 2702456.3106 | 1241009.9902 | 2702454.8369 | 1241007.3071 | 2702466.6483 | 1240986.6144
21 | 2702361.555 | 1241046.9679 | 2702362.9291 | 1241035.8433
22 | 2702581.2389 | 1241132.731 | 2702583.2139 | 1241129.1624 | 2702603.6344 | 1241094.5108
23 | 2702581.2389 | 1241132.731 | 2702593.3122 | 1241139.3969
24 | 2702603.6344 | 1241094.5108 | 2702614.9418 | 1241101.0848
25 | 2702619.5806 | 1241056.2125 | 2702619.9619 | 1241054.718 | 2702620.5905 | 1241051.1705 | 2702622.7789 | 1241038.3318 | 2702626.7964 | 1241039.1019 | 2702626.0776 | 1241042.1807 | 2702622.3322 | 1241059.3403 | 2702619.7701 | 1241066.2457 | 2702612.5474 | 1241078.9529 | 2702603.6344 | 1241094.5108
26 | 2702593.3973 | 1241139.4439 | 2702593.3122 | 1241139.3969
27 | 2702401.6106 | 1240957.4282 | 2702406.7463 | 1240951.2564 | 2702414.9489 | 1240942.658
28 | 2702401.6106 | 1240957.4282 | 2702397.783 | 1240962.2992 | 2702385.1738 | 1240972.5118
29 | 2702414.9489 | 1240942.658 | 2702423.7447 | 1240933.436 | 2702432.9366 | 1240922.8146
30 | 2702365.6761 | 1240983.5329 | 2702385.1738 | 1240972.5118
31 | 2702421.6789 | 1241059.8726 | 2702418.7559 | 1241084.6288
32 | 2702432.9366 | 1240922.8146 | 2702461.0115 | 1240890.3738
33 | 2702493.3519 | 1241114.1653 | 2702492.1305 | 1241117.8915 | 2702483.2289 | 1241137.0364
34 | 2702505.4293 | 1241144.5845 | 2702496.7328 | 1241159.8406
35 | 2702561.7819 | 1241159.8317 | 2702548.9086 | 1241182.0688
36 | 2702562.266 | 1241158.9954 | 2702561.7819 | 1241159.8317
37 | 2702493.3519 | 1241114.1653 | 2702469.0272 | 1241108.263 | 2702467.2707 | 1241104.4409 | 2702458.7007 | 1241102.4145
38 | 2702493.8224 | 1241002.8989 | 2702494.5676 | 1240995.6618 | 2702500.8065 | 1240984.4928
39 | 2702493.8224 | 1241002.8989 | 2702495.5485 | 1241002.9417
40 | 2702466.6483 | 1240986.6144 | 2702468.3637 | 1240983.6091
41 | 2702339.9277 | 1240992.4812 | 2702344.449 | 1240990.6582
42 | 2702339.9277 | 1240992.4812 | 2702333.1067 | 1240995.2315 | 2702321.6359 | 1241003.203
43 | 2702364.462 | 1240984.2192 | 2702345.6951 | 1240990.1557 | 2702344.449 | 1240990.6582
44 | 2702364.462 | 1240984.2192 | 2702367.2161 | 1241003.4259
45 | 2702364.462 | 1240984.2192 | 2702365.6761 | 1240983.5329
46 | 2702364.1315 | 1241026.6016 | 2702367.2161 | 1241003.4259
47 | 2702364.1315 | 1241026.6016 | 2702375.6366 | 1241020.9963
48 | 2702363.2183 | 1241033.5023 | 2702364.1315 | 1241026.6016
49 | 2702309.7804 | 1241036.7291 | 2702315.1549 | 1241032.3951 | 2702317.2506 | 1241031.9579
50 | 2702309.7804 | 1241036.7291 | 2702307.2358 | 1241038.7811
51 | 2702339.0467 | 1241029.6167 | 2702333.0745 | 1241028.6566 | 2702317.2506 | 1241031.9579
52 | 2702289.7314 | 1241053.3038 | 2702292.6766 | 1241050.5216 | 2702307.2358 | 1241038.7811
53 | 2702363.2183 | 1241033.5023 | 2702339.0467 | 1241029.6167
54 | 2702283.1814 | 1241059.491 | 2702289.7314 | 1241053.3038
55 | 2702363.2183 | 1241033.5023 | 2702362.9291 | 1241035.8433
56 | 2702283.1814 | 1241059.491 | 2702276.1002 | 1241066.1801
57 | 2702276.1002 | 1241066.1801 | 2702271.2202 | 1241070.7898 | 2702267.4079 | 1241073.6903
58 | 2702397.0696 | 1241010.5541 | 2702375.6366 | 1241020.9963
59 | 2702474.698 | 1240874.559 | 2702461.0115 | 1240890.3738
60 | 2702510.0732 | 1241136.4378 | 2702505.4293 | 1241144.5845
61 | 2702493.3519 | 1241114.1653 | 2702500.7869 | 1241115.8505 | 2702508.7492 | 1241117.656 | 2702509.418 | 1241119.8079
62 | 2702493.3519 | 1241114.1653 | 2702498.2398 | 1241099.1381 | 2702499.4278 | 1241094.3314
63 | 2702614.9418 | 1241101.0848 | 2702618.9375 | 1241103.4079
64 | 2702601.6018 | 1240992.9753 | 2702622.028 | 1241014.4116 | 2702624.4264 | 1241018.723 | 2702624.9639 | 1241022.1905 | 2702624.6808 | 1241027.1895 | 2702622.7789 | 1241038.3318 | 2702620.5905 | 1241051.1705 | 2702619.9619 | 1241054.718 | 2702619.5806 | 1241056.2125
65 | 2702619.5806 | 1241056.2125 | 2702617.4812 | 1241053.4185 | 2702616.4547 | 1241048.497 | 2702612.7443 | 1241040.9048 | 2702607.8698 | 1241035.0271 | 2702603.7004 | 1241032.1077
66 | 2702619.5806 | 1241056.2125 | 2702619.0622 | 1241058.2051 | 2702617.504 | 1241062.5927 | 2702615.5027 | 1241066.8057 | 2702615.0037 | 1241067.677
67 | 2702602.8201 | 1241144.6464 | 2702593.3973 | 1241139.4439
68 | 2702515.2676 | 1241046.9999 | 2702526.5935 | 1241027.6832
69 | 2702515.2676 | 1241046.9999 | 2702510.0119 | 1241055.9637 | 2702507.3092 | 1241061.8127
70 | 2702526.5935 | 1241027.6832 | 2702530.3496 | 1241021.2771 | 2702532.2951 | 1241017.8786
71 | 2702506.1331 | 1241064.9506 | 2702506.4844 | 1241063.5976 | 2702507.3092 | 1241061.8127
72 | 2702534.4591 | 1241014.0982 | 2702532.2951 | 1241017.8786
73 | 2702506.1331 | 1241064.9506 | 2702504.7912 | 1241070.1178 | 2702504.7473 | 1241070.3377
74 | 2702534.4591 | 1241014.0982 | 2702546.5293 | 1240998.9389
75 | 2702534.4591 | 1241014.0982 | 2702522.0607 | 1241006.8562 | 2702508.6236 | 1241003.2659 | 2702500.2775 | 1241003.0589
76 | 2702502.167 | 1241083.2492 | 2702504.7473 | 1241070.3377
77 | 2702574.1008 | 1240964.3113 | 2702546.5293 | 1240998.9389
78 | 2702500.2775 | 1241003.0589 | 2702495.5485 | 1241002.9417
79 | 2702502.167 | 1241083.2492 | 2702504.3891 | 1241084.6331 | 2702521.3977 | 1241094.2231
80 | 2702502.167 | 1241083.2492 | 2702499.4278 | 1241094.3314
81 | 2702574.1008 | 1240964.3113 | 2702557.2807 | 1240953.4235 | 2702555.1591 | 1240952.1971
82 | 2702601.6018 | 1240992.9753 | 2702604.6579 | 1240990.3039 | 2702592.3865 | 1240977.9045 | 2702583.8012 | 1240970.139 | 2702574.1008 | 1240964.3113
83 | 2702597.981 | 1241097.3017 | 2702597.8909 | 1241097.4574
84 | 2702597.981 | 1241097.3017 | 2702603.0338 | 1241088.5736 | 2702614.9285 | 1241067.8082
85 | 2702597.3831 | 1241098.3345 | 2702597.8909 | 1241097.4574
86 | 2702615.0037 | 1241067.677 | 2702614.9285 | 1241067.8082
87 | 2702597.3831 | 1241098.3345 | 2702585.3733 | 1241119.08
88 | 2702580.0342 | 1241128.3028 | 2702585.3733 | 1241119.08
89 | 2702574.6249 | 1241137.6467 | 2702580.0342 | 1241128.3028
90 | 2702595.7359 | 1240998.0667 | 2702601.6018 | 1240992.9753
91 | 2702589.7301 | 1241022.3258 | 2702603.7004 | 1241032.1077
92 | 2702589.7301 | 1241022.3258 | 2702584.6988 | 1241018.8029
93 | 2702575.6333 | 1241016.708 | 2702577.5183 | 1241013.7751 | 2702584.6988 | 1241018.8029
94 | 2702575.6333 | 1241016.708 | 2702561.8441 | 1241038.1629
95 | 2702561.8441 | 1241038.1629 | 2702561.1214 | 1241039.2874
96 | 2702512.8955 | 1240925.4242 | 2702522.5971 | 1240933.3756 | 2702555.1591 | 1240952.1971
97 | 2702560.9229 | 1241039.5961 | 2702561.1214 | 1241039.2874
98 | 2702574.6249 | 1241137.6467 | 2702562.266 | 1241158.9954
99 | 2702522.2382 | 1241091.5356 | 2702521.3977 | 1241094.2231
100 | 2702541.8112 | 1241102.3931 | 2702536.4662 | 1241102.7344 | 2702521.3977 | 1241094.2231
101 | 2702543.8746 | 1241066.1218 | 2702560.9229 | 1241039.5961
102 | 2702543.3971 | 1241066.8647 | 2702543.8746 | 1241066.1218
103 | 2702543.1773 | 1241067.2068 | 2702543.3971 | 1241066.8647
104 | 2702541.6462 | 1241069.589 | 2702543.1773 | 1241067.2068
105 | 2702500.8065 | 1240984.4928 | 2702506.6937 | 1240973.9535
106 | 2702485.3828 | 1240918.0546 | 2702484.1516 | 1240919.1263
107 | 2702498.0657 | 1240907.0095 | 2702492.522 | 1240911.8398 | 2702485.3828 | 1240918.0546
108 | 2702472.3872 | 1240937.4007 | 2702480.26 | 1240922.5141 | 2702484.1516 | 1240919.1263
109 | 2702498.0657 | 1240907.0095 | 2702504.8984 | 1240916.8684 | 2702512.8955 | 1240925.4242
110 | 2702474.698 | 1240874.559 | 2702498.0657 | 1240907.0095
111 | 2702504.3298 | 1240936.2068 | 2702506.7738 | 1240932.1904 | 2702512.8955 | 1240925.4242
112 | 2702474.698 | 1240874.559 | 2702480.563 | 1240866.454 | 2702487.8964 | 1240858.2743 | 2702502.7446 | 1240843.6861
113 | 2702502.7446 | 1240843.6861 | 2702480.4474 | 1240820.6241
114 | 2702479.3702 | 1240819.51 | 2702480.4474 | 1240820.6241
115 | 2702627.1515 | 1241108.1834 | 2702618.9375 | 1241103.4079
116 | 2702478.7785 | 1240818.898 | 2702479.3702 | 1240819.51
117 | 2702464.1382 | 1240803.7556 | 2702478.7785 | 1240818.898
118 | 2702464.1382 | 1240803.7556 | 2702441.5905 | 1240822.0274
119 | 2702464.1382 | 1240803.7556 | 2702457.5286 | 1240797.2253
120 | 2702447.162 | 1240786.9831 | 2702457.5286 | 1240797.2253

## bus_geodata
| x | y | coords
0 | 2702358.7669 | 1241069.5401
1 | 2702359.5019 | 1241063.5895
2 | 2702337.715 | 1241167.777
3 | 2702360.7965 | 1241053.1086
4 | 2702353.1063 | 1241154.9547
5 | 2702361.0835 | 1241050.7853
6 | 2702360.0708 | 1241124.5004
7 | 2702410.0481 | 1241169.1365
8 | 2702429.5268 | 1241096.5501
9 | 2702414.4822 | 1241120.6765
10 | 2702472.8612 | 1241156.8666
11 | 2702477.3488 | 1241149.683
12 | 2702437.1358 | 1241141.1723
13 | 2702441.5746 | 1241099.2743
14 | 2702457.4651 | 1241035.9745
15 | 2702452.8684 | 1241047.4558
16 | 2702460.6588 | 1241012.2002
17 | 2702361.555 | 1241046.9679
18 | 2702581.2389 | 1241132.731
19 | 2702603.6344 | 1241094.5108
20 | 2702593.3122 | 1241139.3969
21 | 2702401.6106 | 1240957.4282
22 | 2702414.9489 | 1240942.658
23 | 2702385.1738 | 1240972.5118
24 | 2702418.7559 | 1241084.6288
25 | 2702432.9366 | 1240922.8146
26 | 2702483.2289 | 1241137.0364
27 | 2702496.7328 | 1241159.8406
28 | 2702548.9086 | 1241182.0688
29 | 2702561.7819 | 1241159.8317
30 | 2702458.7007 | 1241102.4145
31 | 2702450.319 | 1241065.3438
32 | 2702493.8224 | 1241002.8989
33 | 2702466.6483 | 1240986.6144
34 | 2702339.9277 | 1240992.4812
35 | 2702344.449 | 1240990.6582
36 | 2702321.6359 | 1241003.203
37 | 2702364.462 | 1240984.2192
38 | 2702367.2161 | 1241003.4259
39 | 2702365.6761 | 1240983.5329
40 | 2702364.1315 | 1241026.6016
41 | 2702309.7804 | 1241036.7291
42 | 2702317.2506 | 1241031.9579
43 | 2702307.2358 | 1241038.7811
44 | 2702339.0467 | 1241029.6167
45 | 2702289.7314 | 1241053.3038
46 | 2702363.2183 | 1241033.5023
47 | 2702283.1814 | 1241059.491
48 | 2702362.9291 | 1241035.8433
49 | 2702276.1002 | 1241066.1801
50 | 2702421.6789 | 1241059.8726
51 | 2702375.6366 | 1241020.9963
52 | 2702397.0696 | 1241010.5541
53 | 2702267.4079 | 1241073.6903
54 | 2702468.3637 | 1240983.6091
55 | 2702461.0115 | 1240890.3738
56 | 2702505.4293 | 1241144.5845
57 | 2702510.0732 | 1241136.4378
58 | 2702493.3519 | 1241114.1653
59 | 2702614.9418 | 1241101.0848
60 | 2702619.5806 | 1241056.2125
61 | 2702593.3973 | 1241139.4439
62 | 2702515.2676 | 1241046.9999
63 | 2702526.5935 | 1241027.6832
64 | 2702507.3092 | 1241061.8127
65 | 2702532.2951 | 1241017.8786
66 | 2702506.1331 | 1241064.9506
67 | 2702534.4591 | 1241014.0982
68 | 2702504.7473 | 1241070.3377
69 | 2702546.5293 | 1240998.9389
70 | 2702500.2775 | 1241003.0589
71 | 2702502.167 | 1241083.2492
72 | 2702509.418 | 1241119.8079
73 | 2702499.4278 | 1241094.3314
74 | 2702574.1008 | 1240964.3113
75 | 2702495.5485 | 1241002.9417
76 | 2702597.981 | 1241097.3017
77 | 2702597.8909 | 1241097.4574
78 | 2702614.9285 | 1241067.8082
79 | 2702597.3831 | 1241098.3345
80 | 2702615.0037 | 1241067.677
81 | 2702585.3733 | 1241119.08
82 | 2702580.0342 | 1241128.3028
83 | 2702601.6018 | 1240992.9753
84 | 2702603.7004 | 1241032.1077
85 | 2702589.7301 | 1241022.3258
86 | 2702584.6988 | 1241018.8029
87 | 2702575.6333 | 1241016.708
88 | 2702561.8441 | 1241038.1629
89 | 2702595.7359 | 1240998.0667
90 | 2702555.1591 | 1240952.1971
91 | 2702561.1214 | 1241039.2874
92 | 2702562.266 | 1241158.9954
93 | 2702574.6249 | 1241137.6467
94 | 2702521.3977 | 1241094.2231
95 | 2702522.2382 | 1241091.5356
96 | 2702541.8112 | 1241102.3931
97 | 2702560.9229 | 1241039.5961
98 | 2702543.8746 | 1241066.1218
99 | 2702543.3971 | 1241066.8647
100 | 2702543.1773 | 1241067.2068
101 | 2702541.6462 | 1241069.589
102 | 2702500.8065 | 1240984.4928
103 | 2702506.6937 | 1240973.9535
104 | 2702485.3828 | 1240918.0546
105 | 2702484.1516 | 1240919.1263
106 | 2702498.0657 | 1240907.0095
107 | 2702472.3872 | 1240937.4007
108 | 2702512.8955 | 1240925.4242
109 | 2702474.698 | 1240874.559
110 | 2702504.3298 | 1240936.2068
111 | 2702502.7446 | 1240843.6861
112 | 2702480.4474 | 1240820.6241
113 | 2702618.9375 | 1241103.4079
114 | 2702479.3702 | 1240819.51
115 | 2702478.7785 | 1240818.898
116 | 2702464.1382 | 1240803.7556
117 | 2702441.5905 | 1240822.0274
118 | 2702457.5286 | 1240797.2253
119 | 2702447.162 | 1240786.9831
120 | 2702602.8201 | 1241144.6464
121 | 2702627.1515 | 1241108.1834
122 | 2702460.6588 | 1241012.2002

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97231 | -0.53314 | 0.0018529 | 0.00046437
1 | 0.97234 | -0.53248 | 0.001715 | 0.00042983
2 | 0.97192 | -0.5408 | 0 | 0
3 | 0.97242 | -0.53098 | 0.0019922 | 0.0004993
4 | 0.97184 | -0.54241 | 0 | 0
5 | 0.97244 | -0.53056 | 0.0068546 | 0.0017179
6 | 0.97172 | -0.54479 | 0.0041244 | 0.0010337
7 | 0.97861 | -0.41055 | 0 | 0
8 | 0.98028 | -0.37785 | 0 | 0
9 | 0.97768 | -0.42876 | 0.0055928 | 0.0014017
10 | 0.98106 | -0.36259 | 0 | 0
11 | 0.98111 | -0.36173 | 0 | 0
12 | 0.98086 | -0.36658 | 0.0055888 | 0.0014007
13 | 0.98052 | -0.37313 | 0.0041925 | 0.0010507
14 | 0.99644 | -0.067032 | 0 | 0
15 | 0.99633 | -0.069263 | 0.0049431 | 0.0012389
16 | 0.99665 | -0.062921 | 0 | 0
17 | 0.9725 | -0.52939 | 0.00207 | 0.00051879
18 | 0.97847 | -0.41269 | 0 | 0
19 | 0.97871 | -0.4079 | 0 | 0
20 | 0.97839 | -0.41419 | 0.0026912 | 0.00067448
21 | 0.9747 | -0.48584 | 0 | 0
22 | 0.97509 | -0.47833 | 0 | 0
23 | 0.97428 | -0.4943 | 0.011749 | 0.0029445
24 | 0.97718 | -0.43863 | 0.0079228 | 0.0019856
25 | 0.9756 | -0.46824 | 0.010968 | 0.0027488
26 | 0.98137 | -0.35659 | 0.0060616 | 0.0015192
27 | 0.98079 | -0.36795 | 0.0067229 | 0.0016849
28 | 0.97813 | -0.41945 | 0.002245 | 0.00056266
29 | 0.97818 | -0.4184 | 0.002951 | 0.00073959
30 | 0.98092 | -0.36534 | 0.0053902 | 0.0013509
31 | 0.99625 | -0.070791 | 0.0048175 | 0.0012074
32 | 0.99345 | -0.12364 | 0 | 0
33 | 0.99967 | -0.0062741 | 0.0081923 | 0.0020532
34 | 0.97376 | -0.50445 | 0.0020228 | 0.00050697
35 | 0.97378 | -0.50413 | 0.0019515 | 0.0004891
36 | 0.97373 | -0.50506 | 0.0015542 | 0.00038951
37 | 0.97389 | -0.50199 | 0 | 0
38 | 0.9736 | -0.50753 | 0.0085326 | 0.0021385
39 | 0.97391 | -0.50155 | 0.0028121 | 0.00070479
40 | 0.97302 | -0.51906 | 0 | 0
41 | 0.97161 | -0.54694 | 0.0026217 | 0.00065707
42 | 0.97177 | -0.54381 | 0.0025216 | 0.00063197
43 | 0.97156 | -0.54791 | 0.0040759 | 0.0010215
44 | 0.97221 | -0.5351 | 0.0019027 | 0.00047687
45 | 0.9713 | -0.55297 | 0.0033265 | 0.0008337
46 | 0.97274 | -0.52465 | 0 | 0
47 | 0.97123 | -0.55442 | 0.0019835 | 0.00049711
48 | 0.97269 | -0.52554 | 0.0018494 | 0.00046351
49 | 0.97117 | -0.55563 | 0.0019274 | 0.00048305
50 | 0.97702 | -0.44181 | 0.0069802 | 0.0017494
51 | 0.9729 | -0.52142 | 0.0017142 | 0.00042963
52 | 0.97272 | -0.52506 | 0.0082845 | 0.0020763
53 | 0.97112 | -0.55665 | 0.0047926 | 0.0012012
54 | 1 | 0 | -0.42638 | -0.10986
55 | 0.97653 | -0.44994 | 0.0017743 | 0.00044468
56 | 0.98066 | -0.37051 | 0.006036 | 0.0015128
57 | 0.98064 | -0.37085 | 0.0020097 | 0.00050368
58 | 0.98198 | -0.34463 | 0 | 0
59 | 0.97865 | -0.40925 | 0.00062389 | 0.00015636
60 | 0.97961 | -0.39039 | 0 | 0
61 | 0.97839 | -0.41419 | 0.0026161 | 0.00065565
62 | 0.98668 | -0.25327 | 0.0016654 | 0.00041739
63 | 0.98833 | -0.22131 | 0.0020369 | 0.0005105
64 | 0.98546 | -0.27687 | 0.0012428 | 0.00031148
65 | 0.98919 | -0.20475 | 0.0016834 | 0.0004219
66 | 0.98522 | -0.28152 | 0.001292 | 0.00032381
67 | 0.98953 | -0.19827 | 0 | 0
68 | 0.98483 | -0.28908 | 0.001411 | 0.00035362
69 | 0.98814 | -0.22477 | 0.00021257 | 5.3276e-05
70 | 0.99285 | -0.13485 | 0.0020192 | 0.00050606
71 | 0.98393 | -0.30666 | 0 | 0
72 | 0.98186 | -0.34707 | 0.0075065 | 0.0018813
73 | 0.98321 | -0.32064 | 0.0039551 | 0.00099123
74 | 0.98498 | -0.28555 | 0 | 0
75 | 0.99329 | -0.12665 | 0.0022624 | 0.00056701
76 | 0.97886 | -0.40512 | 0.0011791 | 0.00029551
77 | 0.97885 | -0.40517 | 0.0012577 | 0.00031521
78 | 0.97938 | -0.39482 | 0.0014623 | 0.00036649
79 | 0.97884 | -0.40543 | 0.0010646 | 0.00026681
80 | 0.97938 | -0.39477 | 0.001368 | 0.00034285
81 | 0.97855 | -0.41116 | 0.0019067 | 0.00047787
82 | 0.97844 | -0.41334 | 0.0021755 | 0.00054524
83 | 0.98292 | -0.32573 | 0 | 0
84 | 0.97911 | -0.40019 | 0.0011791 | 0.00029552
85 | 0.97884 | -0.40545 | 0.0012022 | 0.0003013
86 | 0.97875 | -0.40722 | 0.0011937 | 0.00029916
87 | 0.97858 | -0.41047 | 0.0034101 | 0.00085466
88 | 0.97832 | -0.41565 | 0.001259 | 0.00031554
89 | 0.98291 | -0.32587 | 0.0010202 | 0.00025568
90 | 0.98364 | -0.31148 | 0.0010884 | 0.00027279
91 | 0.97831 | -0.41589 | 0.0012573 | 0.00031512
92 | 0.97818 | -0.41831 | 0.0019008 | 0.00047639
93 | 0.97835 | -0.41512 | 0.00196 | 0.00049122
94 | 0.9838 | -0.30916 | 0 | 0
95 | 0.98379 | -0.30935 | 0.0037476 | 0.00093923
96 | 0.98375 | -0.31019 | 0.0025264 | 0.00063319
97 | 0.9783 | -0.41595 | 0.0011144 | 0.0002793
98 | 0.97808 | -0.42028 | 0.0011922 | 0.0002988
99 | 0.97808 | -0.42038 | 0.0012314 | 0.00030861
100 | 0.97808 | -0.42042 | 0.0012189 | 0.00030547
101 | 0.97807 | -0.42062 | 0.0038922 | 0.00097547
102 | 0.99339 | -0.12477 | 0.000203 | 5.0878e-05
103 | 0.99335 | -0.12541 | 0.0029933 | 0.0007502
104 | 0.97908 | -0.40009 | 0.0030772 | 0.00077122
105 | 0.97907 | -0.40033 | 0.0033773 | 0.00084643
106 | 0.97926 | -0.39665 | 0 | 0
107 | 0.97897 | -0.40225 | 0.0047998 | 0.0012029
108 | 0.98066 | -0.36933 | 0 | 0
109 | 0.97699 | -0.44087 | 0 | 0
110 | 0.98064 | -0.36959 | 0.0010407 | 0.00026081
111 | 0.97555 | -0.46916 | 0 | 0
112 | 0.97445 | -0.49092 | 0.0057649 | 0.0014448
113 | 0.97862 | -0.40967 | 0.0044318 | 0.0011107
114 | 0.9744 | -0.49193 | 0.027623 | 0.0069229
115 | 0.97437 | -0.49238 | 0.029589 | 0.0074157
116 | 0.97354 | -0.50883 | 0 | 0
117 | 0.97286 | -0.52218 | 0.024996 | 0.0062645
118 | 0.97302 | -0.5191 | 0.04342 | 0.010882
119 | 0.97279 | -0.52356 | 0.016613 | 0.0041635
120 | 0.97839 | -0.41432 | 0.00064189 | 0.00016087
121 | 0.97862 | -0.40978 | 0.00060808 | 0.0001524
122 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0059796 | -0.0014976 | 0.0059798 | 0.0014977 | 1.8827e-07 | 4.6129e-08 | 0.0091508 | 0.0091507 | 0.0091508 | 0.97231 | -0.53314 | 0.97234 | -0.53248 | 2.5139
1 | 0.0041267 | 0.0010332 | -0.0041252 | -0.0010335 | 1.5049e-06 | -2.8431e-07 | 0.0063151 | 0.0063156 | 0.0063156 | 0.97231 | -0.53314 | 0.97192 | -0.5408 | 1.7351
2 | -0.0076948 | -0.0019275 | 0.0076954 | 0.0019277 | 5.4912e-07 | 2.2044e-07 | 0.011775 | 0.011775 | 0.011775 | 0.97234 | -0.53248 | 0.97242 | -0.53098 | 3.235
3 | 0.0041252 | 0.0010335 | -0.0041249 | -0.0010336 | 3.1695e-07 | -5.9732e-08 | 0.0063156 | 0.0063157 | 0.0063157 | 0.97192 | -0.5408 | 0.97184 | -0.54241 | 1.7351
4 | -0.0096876 | -0.002427 | 0.0096878 | 0.0024271 | 1.929e-07 | 9.4417e-08 | 0.014824 | 0.014824 | 0.014824 | 0.97242 | -0.53098 | 0.97244 | -0.53056 | 4.0725
5 | 0.0041249 | 0.0010336 | -0.0041244 | -0.0010337 | 4.673e-07 | -8.7971e-08 | 0.0063157 | 0.0063158 | 0.0063158 | 0.97184 | -0.54241 | 0.97172 | -0.54479 | 1.7351
6 | -0.016542 | -0.004145 | 0.016543 | 0.0041456 | 9.2422e-07 | 5.4378e-07 | 0.025313 | 0.025313 | 0.025313 | 0.97244 | -0.53056 | 0.9725 | -0.52939 | 6.954
7 | -0.020522 | -0.0051519 | 0.020554 | 0.0051713 | 3.2057e-05 | 1.9412e-05 | 0.031207 | 0.031207 | 0.031207 | 0.97861 | -0.41055 | 0.98028 | -0.37785 | 8.5733
8 | 0.020522 | 0.0051519 | -0.020504 | -0.0051411 | 1.7816e-05 | 1.079e-05 | 0.031207 | 0.031207 | 0.031207 | 0.97861 | -0.41055 | 0.97768 | -0.42876 | 8.5734
9 | -0.020554 | -0.0051713 | 0.020558 | 0.0051741 | 4.6376e-06 | 2.8079e-06 | 0.031207 | 0.031207 | 0.031207 | 0.98028 | -0.37785 | 0.98052 | -0.37313 | 8.5732
10 | 0.014911 | 0.0037394 | -0.014904 | -0.0037354 | 7.0115e-06 | 4.0324e-06 | 0.022695 | 0.022695 | 0.022695 | 0.97768 | -0.42876 | 0.97718 | -0.43863 | 6.235
11 | -0.0055899 | -0.0014009 | 0.0055901 | 0.0014009 | 2.2815e-07 | 3.9137e-08 | 0.0084783 | 0.0084783 | 0.0084783 | 0.98106 | -0.36259 | 0.98111 | -0.36173 | 2.3292
12 | 0.0055899 | 0.0014009 | -0.0055888 | -0.0014007 | 1.0619e-06 | 1.823e-07 | 0.0084783 | 0.0084785 | 0.0084785 | 0.98106 | -0.36259 | 0.98086 | -0.36658 | 2.3293
13 | -0.020364 | -0.0051051 | 0.020369 | 0.0051081 | 4.9892e-06 | 3.0169e-06 | 0.030886 | 0.030886 | 0.030886 | 0.98111 | -0.36173 | 0.98137 | -0.35659 | 8.4852
14 | 0.014774 | 0.0037042 | -0.01477 | -0.0037017 | 4.3789e-06 | 2.5089e-06 | 0.022408 | 0.022408 | 0.022408 | 0.98111 | -0.36173 | 0.98079 | -0.36795 | 6.156
15 | -0.024751 | -0.0062249 | 0.02476 | 0.0062305 | 9.2176e-06 | 5.6795e-06 | 0.037569 | 0.037569 | 0.037569 | 0.98052 | -0.37313 | 0.98092 | -0.36534 | 10.3211
16 | 0.009762 | 0.0024467 | -0.0097609 | -0.0024462 | 1.0375e-06 | 4.9442e-07 | 0.014578 | 0.014578 | 0.014578 | 0.99644 | -0.067032 | 0.99633 | -0.069263 | 4.0049
17 | -0.009762 | -0.0024467 | 0.0097639 | 0.0024476 | 1.9118e-06 | 9.1101e-07 | 0.014578 | 0.014578 | 0.014578 | 0.99644 | -0.067032 | 0.99665 | -0.062921 | 4.0049
18 | 0.0048178 | 0.0012074 | -0.0048175 | -0.0012074 | 3.5085e-07 | -1.077e-08 | 0.0071954 | 0.0071955 | 0.0071955 | 0.99633 | -0.069263 | 0.99625 | -0.070791 | 1.9768
19 | 0.40549 | 0.10454 | -0.4043 | -0.10378 | 0.0011952 | 0.00076312 | 0.60645 | 0.60645 | 0.60645 | 0.99665 | -0.062921 | 0.99345 | -0.12364 | 41.6516
20 | -0.41526 | -0.10699 | 0.41641 | 0.10773 | 0.0011485 | 0.00073339 | 0.62102 | 0.62102 | 0.62102 | 0.99665 | -0.062921 | 0.99967 | -0.0062741 | 42.6528
21 | -0.018613 | -0.0046644 | 0.018617 | 0.0046664 | 3.4094e-06 | 2.0429e-06 | 0.02848 | 0.02848 | 0.02848 | 0.9725 | -0.52939 | 0.97269 | -0.52554 | 7.8242
22 | -0.0059496 | -0.001491 | 0.005951 | 0.0014913 | 1.3591e-06 | 3.1359e-07 | 0.0090479 | 0.0090477 | 0.0090479 | 0.97847 | -0.41269 | 0.97871 | -0.4079 | 2.4857
23 | 0.0059496 | 0.001491 | -0.0059492 | -0.0014909 | 4.2338e-07 | 9.7752e-08 | 0.0090479 | 0.0090479 | 0.0090479 | 0.97847 | -0.41269 | 0.97839 | -0.41419 | 2.4857
24 | 0.0056643 | 0.0014194 | -0.0056639 | -0.0014194 | 3.6376e-07 | 6.8451e-08 | 0.0086118 | 0.0086119 | 0.0086119 | 0.97871 | -0.4079 | 0.97865 | -0.40925 | 2.3659
25 | -0.011615 | -0.0029107 | 0.011625 | 0.0029159 | 9.6943e-06 | 5.1616e-06 | 0.017659 | 0.017659 | 0.017659 | 0.97871 | -0.4079 | 0.97961 | -0.39039 | 4.8515
26 | 0.003258 | 0.00081639 | -0.003258 | -0.00081639 | 8.9494e-10 | -6.4818e-10 | 0.0049549 | 0.0049549 | 0.0049549 | 0.97839 | -0.41419 | 0.97839 | -0.41419 | 1.3612
27 | -0.082388 | -0.0207 | 0.082417 | 0.020718 | 2.9541e-05 | 1.7913e-05 | 0.12579 | 0.12579 | 0.12579 | 0.9747 | -0.48584 | 0.97509 | -0.47833 | 8.6397
28 | 0.082388 | 0.0207 | -0.082354 | -0.02068 | 3.3262e-05 | 2.0171e-05 | 0.12579 | 0.12579 | 0.12579 | 0.9747 | -0.48584 | 0.97428 | -0.4943 | 8.6398
29 | -0.082417 | -0.020718 | 0.082457 | 0.020742 | 3.9744e-05 | 2.4099e-05 | 0.12579 | 0.12579 | 0.12579 | 0.97509 | -0.47833 | 0.9756 | -0.46824 | 8.6397
30 | 0.070606 | 0.017736 | -0.070581 | -0.017721 | 2.4424e-05 | 1.4516e-05 | 0.10785 | 0.10785 | 0.10785 | 0.97428 | -0.4943 | 0.97391 | -0.50155 | 7.4074
31 | 0.0069812 | 0.0017498 | -0.0069802 | -0.0017494 | 1.0565e-06 | 3.6391e-07 | 0.010631 | 0.010631 | 0.010631 | 0.97718 | -0.43863 | 0.97702 | -0.44181 | 2.9206
32 | -0.093425 | -0.023491 | 0.093506 | 0.023541 | 8.1698e-05 | 5.0142e-05 | 0.14252 | 0.14252 | 0.14252 | 0.9756 | -0.46824 | 0.97653 | -0.44994 | 9.7886
33 | -0.026431 | -0.0066273 | 0.026446 | 0.0066366 | 1.5079e-05 | 9.3338e-06 | 0.040077 | 0.040077 | 0.040077 | 0.98137 | -0.35659 | 0.98198 | -0.34463 | 11.0102
34 | 0.0080467 | 0.0020168 | -0.0080457 | -0.0020163 | 9.8147e-07 | 4.0655e-07 | 0.012208 | 0.012208 | 0.012208 | 0.98079 | -0.36795 | 0.98066 | -0.37051 | 3.3539
35 | -0.002245 | -0.00056266 | 0.0022451 | 0.00056241 | 1.1239e-07 | -2.506e-07 | 0.0034153 | 0.0034152 | 0.0034153 | 0.97813 | -0.41945 | 0.97818 | -0.4184 | 0.93828
36 | -0.0051961 | -0.001302 | 0.0051961 | 0.001302 | 2.264e-08 | 2.3594e-09 | 0.0079043 | 0.0079043 | 0.0079043 | 0.97818 | -0.4184 | 0.97818 | -0.41831 | 2.1715
37 | -0.03015 | -0.0075814 | 0.03018 | 0.0076001 | 2.9854e-05 | 1.8626e-05 | 0.045746 | 0.045745 | 0.045746 | 0.98092 | -0.36534 | 0.98198 | -0.34463 | 12.5675
38 | 0.0031966 | 0.00080083 | -0.0031964 | -0.00080098 | 1.7252e-07 | -1.4942e-07 | 0.0047879 | 0.004788 | 0.004788 | 0.99345 | -0.12364 | 0.99339 | -0.12477 | 1.3154
39 | 0.4011 | 0.10298 | -0.40104 | -0.10294 | 5.8595e-05 | 3.7411e-05 | 0.60166 | 0.60166 | 0.60166 | 0.99345 | -0.12364 | 0.99329 | -0.12665 | 41.3228
40 | -0.4246 | -0.10978 | 0.42473 | 0.10986 | 0.00013008 | 8.307e-05 | 0.63322 | 0.63322 | 0.63322 | 0.99967 | -0.0062741 | 1 | 0 | 43.4902
41 | -0.003577 | -0.00089624 | 0.0035771 | 0.00089621 | 5.4619e-08 | -2.5689e-08 | 0.005466 | 0.005466 | 0.005466 | 0.97376 | -0.50445 | 0.97378 | -0.50413 | 1.5017
42 | 0.0015542 | 0.00038928 | -0.0015542 | -0.00038951 | 4.5103e-08 | -2.3638e-07 | 0.0023749 | 0.002375 | 0.002375 | 0.97376 | -0.50445 | 0.97373 | -0.50506 | 0.65248
43 | -0.0055286 | -0.0013853 | 0.0055292 | 0.0013854 | 5.6276e-07 | 9.8553e-08 | 0.0084481 | 0.008448 | 0.0084481 | 0.97378 | -0.50413 | 0.97389 | -0.50199 | 2.3209
44 | 0.062239 | 0.01563 | -0.062222 | -0.015621 | 1.6454e-05 | 9.565e-06 | 0.095107 | 0.095107 | 0.095107 | 0.97389 | -0.50199 | 0.9736 | -0.50753 | 6.5321
45 | -0.067768 | -0.017016 | 0.067769 | 0.017016 | 1.4021e-06 | 8.2792e-07 | 0.10355 | 0.10355 | 0.10355 | 0.97389 | -0.50199 | 0.97391 | -0.50155 | 7.1123
46 | 0.053689 | 0.013482 | -0.05366 | -0.013464 | 2.9524e-05 | 1.8314e-05 | 0.082066 | 0.082066 | 0.082066 | 0.9736 | -0.50753 | 0.97302 | -0.51906 | 11.2729
47 | 0.010001 | 0.0025071 | -0.01 | -0.0025065 | 1.1227e-06 | 5.5959e-07 | 0.015295 | 0.015295 | 0.015295 | 0.97302 | -0.51906 | 0.9729 | -0.52142 | 4.2019
48 | 0.043659 | 0.010957 | -0.043647 | -0.010949 | 1.1638e-05 | 7.362e-06 | 0.066772 | 0.066772 | 0.066772 | 0.97302 | -0.51906 | 0.97274 | -0.52465 | 18.3438
49 | -0.018733 | -0.004696 | 0.018735 | 0.0046977 | 2.7918e-06 | 1.6747e-06 | 0.028689 | 0.028689 | 0.028689 | 0.97161 | -0.54694 | 0.97177 | -0.54381 | 7.8817
50 | 0.016111 | 0.0040389 | -0.01611 | -0.0040385 | 7.4631e-07 | 4.3716e-07 | 0.024674 | 0.024674 | 0.024674 | 0.97161 | -0.54694 | 0.97156 | -0.54791 | 6.7786
51 | -0.021257 | -0.0053297 | 0.021266 | 0.005335 | 8.8259e-06 | 5.3733e-06 | 0.03255 | 0.03255 | 0.03255 | 0.97177 | -0.54381 | 0.97221 | -0.5351 | 8.9424
52 | 0.012034 | 0.003017 | -0.012031 | -0.0030154 | 2.8989e-06 | 1.5736e-06 | 0.018432 | 0.018432 | 0.018432 | 0.97156 | -0.54791 | 0.9713 | -0.55297 | 5.0636
53 | -0.023168 | -0.0058119 | 0.02318 | 0.005819 | 1.1546e-05 | 7.0854e-06 | 0.035463 | 0.035462 | 0.035463 | 0.97221 | -0.5351 | 0.97274 | -0.52465 | 9.7425
54 | 0.0087047 | 0.0021817 | -0.0087041 | -0.0021814 | 6.0088e-07 | 2.7305e-07 | 0.013335 | 0.013336 | 0.013336 | 0.9713 | -0.55297 | 0.97123 | -0.55442 | 3.6636
55 | 0.020467 | 0.0051304 | -0.020466 | -0.0051299 | 8.6709e-07 | 5.2566e-07 | 0.031309 | 0.031309 | 0.031309 | 0.97274 | -0.52465 | 0.97269 | -0.52554 | 8.6014
56 | 0.0067206 | 0.0016843 | -0.0067203 | -0.0016842 | 3.8728e-07 | 1.2732e-07 | 0.010297 | 0.010297 | 0.010297 | 0.97123 | -0.55442 | 0.97117 | -0.55563 | 2.8288
57 | 0.0047929 | 0.0012012 | -0.0047926 | -0.0012012 | 2.3263e-07 | 6.5545e-09 | 0.0073436 | 0.0073436 | 0.0073436 | 0.97117 | -0.55563 | 0.97112 | -0.55665 | 2.0175
58 | 0.0082859 | 0.0020769 | -0.0082845 | -0.0020763 | 1.4359e-06 | 6.2299e-07 | 0.012673 | 0.012673 | 0.012673 | 0.9729 | -0.52142 | 0.97272 | -0.52506 | 3.4817
59 | -0.095281 | -0.023986 | 0.095322 | 0.024011 | 4.1353e-05 | 2.5419e-05 | 0.14522 | 0.14522 | 0.14522 | 0.97653 | -0.44994 | 0.97699 | -0.44087 | 9.9742
60 | 0.0020097 | 0.00050358 | -0.0020097 | -0.00050368 | 3.2701e-08 | -9.738e-08 | 0.0030495 | 0.0030495 | 0.0030495 | 0.98066 | -0.37051 | 0.98064 | -0.37085 | 0.83778
61 | 0.0075074 | 0.0018817 | -0.0075065 | -0.0018813 | 8.7558e-07 | 3.3216e-07 | 0.011376 | 0.011376 | 0.011376 | 0.98198 | -0.34463 | 0.98186 | -0.34707 | 3.1253
62 | -0.064133 | -0.016118 | 0.064207 | 0.016165 | 7.3526e-05 | 4.6794e-05 | 0.097198 | 0.097198 | 0.097198 | 0.98198 | -0.34463 | 0.98321 | -0.32064 | 26.7029
63 | 0.00504 | 0.001263 | -0.0050399 | -0.001263 | 1.0179e-07 | 7.069e-09 | 0.0076632 | 0.0076633 | 0.0076633 | 0.97865 | -0.40925 | 0.97862 | -0.40967 | 2.1053
64 | -0.049286 | -0.012367 | 0.049439 | 0.012464 | 0.00015247 | 9.6664e-05 | 0.074871 | 0.074871 | 0.074871 | 0.97961 | -0.39039 | 0.98292 | -0.32573 | 20.5689
65 | 0.018171 | 0.0045607 | -0.018163 | -0.0045556 | 8.4865e-06 | 5.0577e-06 | 0.027605 | 0.027605 | 0.027605 | 0.97961 | -0.39039 | 0.97911 | -0.40019 | 7.5837
66 | 0.01949 | 0.0048903 | -0.019486 | -0.0048879 | 4.0706e-06 | 2.4493e-06 | 0.029607 | 0.029607 | 0.029607 | 0.97961 | -0.39039 | 0.97938 | -0.39477 | 8.1339
67 | 0.0006419 | 0.00016074 | -0.00064189 | -0.00016087 | 3.8467e-09 | -1.3271e-07 | 0.0009762 | 0.00097625 | 0.00097625 | 0.97839 | -0.41419 | 0.97839 | -0.41432 | 0.2682
68 | -0.08029 | -0.020289 | 0.080413 | 0.020368 | 0.00012324 | 7.8585e-05 | 0.12114 | 0.12114 | 0.12114 | 0.98668 | -0.25327 | 0.98833 | -0.22131 | 33.2816
69 | 0.078624 | 0.019872 | -0.078536 | -0.019815 | 8.8846e-05 | 5.6647e-05 | 0.11863 | 0.11863 | 0.11863 | 0.98668 | -0.25327 | 0.98546 | -0.27687 | 32.5916
70 | -0.08245 | -0.020878 | 0.082516 | 0.02092 | 6.5621e-05 | 4.1852e-05 | 0.12421 | 0.12421 | 0.12421 | 0.98833 | -0.22131 | 0.98919 | -0.20475 | 34.124
71 | 0.077293 | 0.019504 | -0.077276 | -0.019493 | 1.7197e-05 | 1.0963e-05 | 0.11676 | 0.11676 | 0.11676 | 0.98546 | -0.27687 | 0.98522 | -0.28152 | 32.076
72 | -0.084199 | -0.021342 | 0.084225 | 0.021359 | 2.6241e-05 | 1.6738e-05 | 0.12674 | 0.12674 | 0.12674 | 0.98919 | -0.20475 | 0.98953 | -0.19827 | 34.8197
73 | 0.075984 | 0.019169 | -0.075956 | -0.019151 | 2.7495e-05 | 1.7526e-05 | 0.11481 | 0.11481 | 0.11481 | 0.98522 | -0.28152 | 0.98483 | -0.28908 | 31.5399
74 | 0.31116 | 0.079633 | -0.31076 | -0.079379 | 0.00039874 | 0.0002542 | 0.4685 | 0.4685 | 0.4685 | 0.98953 | -0.19827 | 0.98814 | -0.22477 | 32.1773
75 | -0.39539 | -0.10099 | 0.3966 | 0.10177 | 0.0012163 | 0.00077652 | 0.59525 | 0.59524 | 0.59525 | 0.98953 | -0.19827 | 0.99285 | -0.13485 | 40.8822
76 | 0.074545 | 0.018798 | -0.074482 | -0.018758 | 6.2684e-05 | 3.995e-05 | 0.11267 | 0.11267 | 0.11267 | 0.98483 | -0.28908 | 0.98393 | -0.30666 | 30.9543
77 | 0.31055 | 0.079326 | -0.30964 | -0.078746 | 0.00090959 | 0.00057988 | 0.46818 | 0.46818 | 0.46818 | 0.98814 | -0.22477 | 0.98498 | -0.28555 | 32.1554
78 | -0.39862 | -0.10227 | 0.39878 | 0.10238 | 0.00015873 | 0.00010135 | 0.59827 | 0.59827 | 0.59827 | 0.99285 | -0.13485 | 0.99329 | -0.12665 | 41.09
79 | 0.0062749 | 0.0015724 | -0.0062742 | -0.0015722 | 7.4612e-07 | 1.9693e-07 | 0.0094896 | 0.0094897 | 0.0094897 | 0.98393 | -0.30666 | 0.9838 | -0.30916 | 2.6071
80 | 0.068207 | 0.017185 | -0.068162 | -0.017156 | 4.5578e-05 | 2.9025e-05 | 0.10318 | 0.10318 | 0.10318 | 0.98393 | -0.30666 | 0.98321 | -0.32064 | 28.3473
81 | 0.25908 | 0.065965 | -0.25876 | -0.065759 | 0.00032357 | 0.00020594 | 0.39177 | 0.39177 | 0.39177 | 0.98498 | -0.28555 | 0.98364 | -0.31148 | 26.9072
82 | 0.050556 | 0.012781 | -0.050459 | -0.012719 | 9.7216e-05 | 6.1654e-05 | 0.076415 | 0.076415 | 0.076415 | 0.98498 | -0.28555 | 0.98292 | -0.32573 | 20.9931
83 | 0.015468 | 0.0038782 | -0.015468 | -0.0038782 | 3.7288e-08 | 2.1604e-08 | 0.023515 | 0.023515 | 0.023515 | 0.97886 | -0.40512 | 0.97885 | -0.40517 | 6.4601
84 | -0.016647 | -0.0041737 | 0.016656 | 0.0041785 | 8.1696e-06 | 4.8007e-06 | 0.025307 | 0.025307 | 0.025307 | 0.97886 | -0.40512 | 0.97938 | -0.39482 | 6.9525
85 | 0.014211 | 0.003563 | -0.01421 | -0.0035629 | 1.7738e-07 | 1.0078e-07 | 0.021603 | 0.021603 | 0.021603 | 0.97885 | -0.40517 | 0.97884 | -0.40543 | 5.9349
86 | -0.018118 | -0.004545 | 0.018118 | 0.004545 | 4.2988e-08 | 2.5609e-08 | 0.027529 | 0.027529 | 0.027529 | 0.97938 | -0.39482 | 0.97938 | -0.39477 | 7.5629
87 | 0.013146 | 0.0032961 | -0.013142 | -0.0032941 | 3.5901e-06 | 1.9964e-06 | 0.019985 | 0.019985 | 0.019985 | 0.97884 | -0.40543 | 0.97855 | -0.41116 | 5.4903
88 | 0.011235 | 0.0028162 | -0.011234 | -0.0028156 | 1.1665e-06 | 6.1271e-07 | 0.017085 | 0.017085 | 0.017085 | 0.97855 | -0.41116 | 0.97844 | -0.41334 | 4.6937
89 | 0.0090588 | 0.0022703 | -0.009058 | -0.00227 | 7.6845e-07 | 3.5622e-07 | 0.013777 | 0.013777 | 0.013777 | 0.97844 | -0.41334 | 0.97835 | -0.41512 | 3.7848
90 | 0.0010202 | 0.00025559 | -0.0010202 | -0.00025568 | 6.9367e-09 | -9.3853e-08 | 0.0015444 | 0.0015444 | 0.0015444 | 0.98292 | -0.32573 | 0.98291 | -0.32587 | 0.4243
91 | 0.016984 | 0.0042601 | -0.01698 | -0.0042576 | 4.2612e-06 | 2.5128e-06 | 0.025813 | 0.025813 | 0.025813 | 0.97911 | -0.40019 | 0.97884 | -0.40545 | 7.0914
92 | 0.015777 | 0.0039563 | -0.015776 | -0.0039555 | 1.3251e-06 | 7.7084e-07 | 0.023985 | 0.023985 | 0.023985 | 0.97884 | -0.40545 | 0.97875 | -0.40722 | 6.5894
93 | 0.014582 | 0.0036564 | -0.01458 | -0.0036551 | 2.2584e-06 | 1.2914e-06 | 0.02217 | 0.022171 | 0.022171 | 0.97875 | -0.40722 | 0.97858 | -0.41047 | 6.0908
94 | 0.01117 | 0.0028004 | -0.011167 | -0.002799 | 2.7592e-06 | 1.4456e-06 | 0.016985 | 0.016985 | 0.016985 | 0.97858 | -0.41047 | 0.97832 | -0.41565 | 4.6663
95 | 0.0099082 | 0.0024834 | -0.0099081 | -0.0024834 | 1.1384e-07 | 5.6074e-08 | 0.01507 | 0.01507 | 0.01507 | 0.97832 | -0.41565 | 0.97831 | -0.41589 | 4.1402
96 | 0.25767 | 0.065487 | -0.25696 | -0.065031 | 0.00071561 | 0.00045545 | 0.39012 | 0.39012 | 0.39012 | 0.98364 | -0.31148 | 0.98066 | -0.36933 | 26.7942
97 | 0.0086507 | 0.0021683 | -0.0086507 | -0.0021683 | 2.3828e-08 | 1.0642e-08 | 0.013158 | 0.013158 | 0.013158 | 0.97831 | -0.41589 | 0.9783 | -0.41595 | 3.6148
98 | -0.0070969 | -0.0017784 | 0.007098 | 0.0017788 | 1.0781e-06 | 3.8029e-07 | 0.010796 | 0.010796 | 0.010796 | 0.97818 | -0.41831 | 0.97835 | -0.41512 | 2.9659
99 | 0.0037476 | 0.00093922 | -0.0037476 | -0.00093923 | 3.3929e-08 | -1.4042e-08 | 0.0056683 | 0.0056683 | 0.0056683 | 0.9838 | -0.30916 | 0.98379 | -0.30935 | 1.5572
100 | 0.0025266 | 0.00063298 | -0.0025264 | -0.00063319 | 1.238e-07 | -2.0781e-07 | 0.0038214 | 0.0038215 | 0.0038215 | 0.9838 | -0.30916 | 0.98375 | -0.31019 | 1.0499
101 | 0.0075363 | 0.001889 | -0.0075347 | -0.0018884 | 1.5537e-06 | 5.9855e-07 | 0.011463 | 0.011463 | 0.011463 | 0.9783 | -0.41595 | 0.97808 | -0.42028 | 3.1492
102 | 0.0063425 | 0.0015896 | -0.0063424 | -0.0015895 | 3.0833e-08 | 8.6498e-09 | 0.0096492 | 0.0096492 | 0.0096492 | 0.97808 | -0.42028 | 0.97808 | -0.42038 | 2.6509
103 | 0.0051111 | 0.0012809 | -0.0051111 | -0.0012809 | 9.2188e-09 | 7.9726e-10 | 0.0077758 | 0.0077758 | 0.0077758 | 0.97808 | -0.42038 | 0.97808 | -0.42042 | 2.1362
104 | 0.0038922 | 0.00097546 | -0.0038922 | -0.00097547 | 3.7236e-08 | -1.1709e-08 | 0.0059215 | 0.0059215 | 0.0059215 | 0.97808 | -0.42042 | 0.97807 | -0.42062 | 1.6268
105 | 0.0029934 | 0.00075011 | -0.0029933 | -0.0007502 | 9.1018e-08 | -9.8032e-08 | 0.0044839 | 0.004484 | 0.004484 | 0.99339 | -0.12477 | 0.99335 | -0.12541 | 1.2319
106 | 0.0081776 | 0.0020494 | -0.0081776 | -0.0020494 | 9.4551e-08 | 3.9985e-08 | 0.012428 | 0.012428 | 0.012428 | 0.97908 | -0.40009 | 0.97907 | -0.40033 | 3.4144
107 | -0.011255 | -0.0028206 | 0.011257 | 0.0028216 | 1.8453e-06 | 9.6944e-07 | 0.017105 | 0.017105 | 0.017105 | 0.97908 | -0.40009 | 0.97926 | -0.39665 | 4.6992
108 | 0.0048002 | 0.0012029 | -0.0047998 | -0.0012029 | 4.391e-07 | 4.3893e-09 | 0.0072955 | 0.0072956 | 0.0072956 | 0.97907 | -0.40033 | 0.97897 | -0.40225 | 2.0043
109 | -0.25558 | -0.064557 | 0.25592 | 0.06477 | 0.00033513 | 0.00021329 | 0.38854 | 0.38854 | 0.38854 | 0.97926 | -0.39665 | 0.98066 | -0.36933 | 26.6857
110 | 0.24432 | 0.061736 | -0.24381 | -0.061407 | 0.00051673 | 0.0003287 | 0.37144 | 0.37144 | 0.37144 | 0.97926 | -0.39665 | 0.97699 | -0.44087 | 25.511
111 | 0.0010407 | 0.00026065 | -0.0010407 | -0.00026081 | 1.2915e-08 | -1.6601e-07 | 0.001579 | 0.0015791 | 0.0015791 | 0.98066 | -0.36933 | 0.98064 | -0.36959 | 0.43381
112 | 0.14848 | 0.037395 | -0.14828 | -0.037269 | 0.00020056 | 0.00012627 | 0.22622 | 0.22622 | 0.22622 | 0.97699 | -0.44087 | 0.97555 | -0.46916 | 15.5368
113 | 0.14828 | 0.037269 | -0.14813 | -0.037172 | 0.0001539 | 9.6894e-05 | 0.22622 | 0.22622 | 0.22622 | 0.97555 | -0.46916 | 0.97445 | -0.49092 | 15.5369
114 | 0.14237 | 0.035727 | -0.14236 | -0.035723 | 6.8673e-06 | 4.3179e-06 | 0.21741 | 0.21741 | 0.21741 | 0.97445 | -0.49092 | 0.9744 | -0.49193 | 14.9323
115 | 0.00060809 | 0.00015228 | -0.00060808 | -0.0001524 | 3.0458e-09 | -1.1743e-07 | 0.00092456 | 0.00092461 | 0.00092461 | 0.97862 | -0.40967 | 0.97862 | -0.40978 | 0.25401
116 | 0.11474 | 0.0288 | -0.11473 | -0.028799 | 2.4505e-06 | 1.5259e-06 | 0.17523 | 0.17523 | 0.17523 | 0.9744 | -0.49193 | 0.97437 | -0.49238 | 12.0351
117 | 0.085144 | 0.021383 | -0.085077 | -0.021341 | 6.6787e-05 | 4.2219e-05 | 0.13004 | 0.13004 | 0.13004 | 0.97437 | -0.49238 | 0.97354 | -0.50883 | 17.8631
118 | 0.025012 | 0.0062743 | -0.024996 | -0.0062645 | 1.5907e-05 | 9.8201e-06 | 0.038231 | 0.038232 | 0.038232 | 0.97354 | -0.50883 | 0.97286 | -0.52218 | 10.5032
119 | 0.060066 | 0.015066 | -0.060036 | -0.015048 | 2.9371e-05 | 1.8682e-05 | 0.091812 | 0.091812 | 0.091812 | 0.97354 | -0.50883 | 0.97302 | -0.5191 | 25.2232
120 | 0.016616 | 0.0041656 | -0.016613 | -0.0041635 | 3.5288e-06 | 2.0774e-06 | 0.025411 | 0.025411 | 0.025411 | 0.97302 | -0.5191 | 0.97279 | -0.52356 | 6.981

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.42853 | 0.1104

## res_load
| p_mw | q_mvar
0 | 0.0018529 | 0.00046437
1 | 0.001715 | 0.00042983
2 | 0.0019922 | 0.0004993
3 | 0.0068546 | 0.0017179
4 | 0.0041244 | 0.0010337
5 | 0.0055928 | 0.0014017
6 | 0.0055888 | 0.0014007
7 | 0.0041925 | 0.0010507
8 | 0.0049431 | 0.0012389
9 | 0.00207 | 0.00051879
10 | 0.0026912 | 0.00067448
11 | 0.011749 | 0.0029445
12 | 0.0079228 | 0.0019856
13 | 0.010968 | 0.0027488
14 | 0.0060616 | 0.0015192
15 | 0.0067229 | 0.0016849
16 | 0.002245 | 0.00056266
17 | 0.002951 | 0.00073959
18 | 0.0053902 | 0.0013509
19 | 0.0048175 | 0.0012074
20 | 0.0081923 | 0.0020532
21 | 0.0020228 | 0.00050697
22 | 0.0019515 | 0.0004891
23 | 0.0015542 | 0.00038951
24 | 0.0085326 | 0.0021385
25 | 0.0028121 | 0.00070479
26 | 0.0026217 | 0.00065707
27 | 0.0025216 | 0.00063197
28 | 0.0040759 | 0.0010215
29 | 0.0019027 | 0.00047687
30 | 0.0033265 | 0.0008337
31 | 0.0019835 | 0.00049711
32 | 0.0018494 | 0.00046351
33 | 0.0019274 | 0.00048305
34 | 0.0069802 | 0.0017494
35 | 0.0017142 | 0.00042963
36 | 0.0082845 | 0.0020763
37 | 0.0047926 | 0.0012012
38 | 0.0021481 | 0.00053836
39 | 0.0017743 | 0.00044468
40 | 0.006036 | 0.0015128
41 | 0.0020097 | 0.00050368
42 | 0.00062389 | 0.00015636
43 | 0.0026161 | 0.00065565
44 | 0.0016654 | 0.00041739
45 | 0.0020369 | 0.0005105
46 | 0.0012428 | 0.00031148
47 | 0.0016834 | 0.0004219
48 | 0.001292 | 0.00032381
49 | 0.001411 | 0.00035362
50 | 0.00021257 | 5.3276e-05
51 | 0.0020192 | 0.00050606
52 | 0.0075065 | 0.0018813
53 | 0.0039551 | 0.00099123
54 | 0.0022624 | 0.00056701
55 | 0.0011791 | 0.00029551
56 | 0.0012577 | 0.00031521
57 | 0.0014623 | 0.00036649
58 | 0.0010646 | 0.00026681
59 | 0.001368 | 0.00034285
60 | 0.0019067 | 0.00047787
61 | 0.0021755 | 0.00054524
62 | 0.0011791 | 0.00029552
63 | 0.0012022 | 0.0003013
64 | 0.0011937 | 0.00029916
65 | 0.0034101 | 0.00085466
66 | 0.001259 | 0.00031554
67 | 0.0010202 | 0.00025568
68 | 0.0010884 | 0.00027279
69 | 0.0012573 | 0.00031512
70 | 0.0019008 | 0.00047639
71 | 0.00196 | 0.00049122
72 | 0.0037476 | 0.00093923
73 | 0.0025264 | 0.00063319
74 | 0.0011144 | 0.0002793
75 | 0.0011922 | 0.0002988
76 | 0.0012314 | 0.00030861
77 | 0.0012189 | 0.00030547
78 | 0.0038922 | 0.00097547
79 | 0.000203 | 5.0878e-05
80 | 0.0029933 | 0.0007502
81 | 0.0030772 | 0.00077122
82 | 0.0033773 | 0.00084643
83 | 0.0047998 | 0.0012029
84 | 0.0010407 | 0.00026081
85 | 0.0057649 | 0.0014448
86 | 0.0044318 | 0.0011107
87 | 0.027623 | 0.0069229
88 | 0.029589 | 0.0074157
89 | 0.024996 | 0.0062645
90 | 0.04342 | 0.010882
91 | 0.016613 | 0.0041635
92 | 0.00064189 | 0.00016087
93 | 0.00060808 | 0.0001524

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1