## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_121-17_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_121-17_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_121-17_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_121-17_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_121-17_0_3_node_20 | 0.4 | n |  | TRUE
5 | bus_LV_121-17_0_3_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_121-17_0_3_node_57 | 0.4 | n |  | TRUE
7 | bus_LV_121-17_0_3_node_56 | 0.4 | n |  | TRUE
8 | bus_LV_121-17_0_3_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_121-17_0_3_node_58 | 0.4 | n |  | TRUE
10 | bus_LV_121-17_0_3_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_121-17_0_3_node_19 | 0.4 | n |  | TRUE
12 | bus_LV_121-17_0_3_node_64 | 0.4 | n |  | TRUE
13 | bus_LV_121-17_0_3_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_121-17_0_3_node_22 | 0.4 | n |  | TRUE
15 | bus_LV_121-17_0_3_node_27 | 0.4 | n |  | TRUE
16 | bus_LV_121-17_0_3_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_121-17_0_3_node_35 | 0.4 | n |  | TRUE
18 | bus_LV_121-17_0_3_node_33 | 0.4 | n |  | TRUE
19 | bus_LV_121-17_0_3_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_121-17_0_3_node_16 | 0.4 | n |  | TRUE
21 | bus_LV_121-17_0_3_node_71 | 0.4 | n |  | TRUE
22 | bus_LV_121-17_0_3_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_121-17_0_3_node_13 | 0.4 | n |  | TRUE
24 | bus_LV_121-17_0_3_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_121-17_0_3_node_59 | 0.4 | n |  | TRUE
26 | bus_LV_121-17_0_3_node_14 | 0.4 | n |  | TRUE
27 | bus_LV_121-17_0_3_node_60 | 0.4 | n |  | TRUE
28 | bus_LV_121-17_0_3_node_61 | 0.4 | n |  | TRUE
29 | bus_LV_121-17_0_3_node_15 | 0.4 | n |  | TRUE
30 | bus_LV_121-17_0_3_node_18 | 0.4 | n |  | TRUE
31 | bus_LV_121-17_0_3_node_31 | 0.4 | n |  | TRUE
32 | bus_LV_121-17_0_3_node_70 | 0.4 | n |  | TRUE
33 | bus_LV_121-17_0_3_node_50 | 0.4 | n |  | TRUE
34 | bus_LV_121-17_0_3_node_75 | 0.4 | n |  | TRUE
35 | bus_LV_121-17_0_3_node_69 | 0.4 | n |  | TRUE
36 | bus_LV_121-17_0_3_node_84 | 0.4 | n |  | TRUE
37 | bus_LV_121-17_0_3_node_83 | 0.4 | n |  | TRUE
38 | bus_LV_121-17_0_3_node_21 | 0.4 | n |  | TRUE
39 | bus_LV_121-17_0_3_node_28 | 0.4 | n |  | TRUE
40 | bus_LV_121-17_0_3_node_65 | 0.4 | n |  | TRUE
41 | bus_LV_121-17_0_3_node_68 | 0.4 | n |  | TRUE
42 | bus_LV_121-17_0_3_node_73 | 0.4 | n |  | TRUE
43 | bus_LV_121-17_0_3_node_72 | 0.4 | n |  | TRUE
44 | bus_LV_121-17_0_3_node_34 | 0.4 | n |  | TRUE
45 | bus_LV_121-17_0_3_node_77 | 0.4 | n |  | TRUE
46 | bus_LV_121-17_0_3_node_32 | 0.4 | n |  | TRUE
47 | bus_LV_121-17_0_3_node_39 | 0.4 | n |  | TRUE
48 | bus_LV_121-17_0_3_node_48 | 0.4 | n |  | TRUE
49 | bus_LV_121-17_0_3_node_74 | 0.4 | n |  | TRUE
50 | bus_LV_121-17_0_3_node_23 | 0.4 | n |  | TRUE
51 | bus_LV_121-17_0_3_node_24 | 0.4 | n |  | TRUE
52 | bus_LV_121-17_0_3_node_25 | 0.4 | n |  | TRUE
53 | bus_LV_121-17_0_3_node_26 | 0.4 | n |  | TRUE
54 | bus_LV_121-17_0_3_node_30 | 0.4 | n |  | TRUE
55 | bus_LV_121-17_0_3_node_51 | 0.4 | n |  | TRUE
56 | bus_LV_121-17_0_3_node_29 | 0.4 | n |  | TRUE
57 | bus_LV_121-17_0_3_node_52 | 0.4 | n |  | TRUE
58 | bus_LV_121-17_0_3_node_53 | 0.4 | n |  | TRUE
59 | bus_LV_121-17_0_3_node_54 | 0.4 | n |  | TRUE
60 | bus_LV_121-17_0_3_node_46 | 0.4 | n |  | TRUE
61 | bus_LV_121-17_0_3_node_82 | 0.4 | n |  | TRUE
62 | bus_LV_121-17_0_3_node_43 | 0.4 | n |  | TRUE
63 | bus_LV_121-17_0_3_node_49 | 0.4 | n |  | TRUE
64 | bus_LV_121-17_0_3_node_36 | 0.4 | n |  | TRUE
65 | bus_LV_121-17_0_3_node_37 | 0.4 | n |  | TRUE
66 | bus_LV_121-17_0_3_node_38 | 0.4 | n |  | TRUE
67 | bus_LV_121-17_0_3_node_40 | 0.4 | n |  | TRUE
68 | bus_LV_121-17_0_3_node_41 | 0.4 | n |  | TRUE
69 | bus_LV_121-17_0_3_node_62 | 0.4 | n |  | TRUE
70 | bus_LV_121-17_0_3_node_80 | 0.4 | n |  | TRUE
71 | bus_LV_121-17_0_3_node_63 | 0.4 | n |  | TRUE
72 | bus_LV_121-17_0_3_node_81 | 0.4 | n |  | TRUE
73 | bus_LV_121-17_0_3_node_79 | 0.4 | n |  | TRUE
74 | bus_LV_121-17_0_3_node_42 | 0.4 | n |  | TRUE
75 | bus_LV_121-17_0_3_node_44 | 0.4 | n |  | TRUE
76 | bus_LV_121-17_0_3_node_47 | 0.4 | n |  | TRUE
77 | bus_LV_121-17_0_3_node_76 | 0.4 | n |  | TRUE
78 | bus_LV_121-17_0_3_node_78 | 0.4 | n |  | TRUE
79 | bus_LV_121-17_0_3_node_66 | 0.4 | n |  | TRUE
80 | bus_LV_121-17_0_3_node_67 | 0.4 | n |  | TRUE
81 | bus_MV_357_0_node_42 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_121-17_0_3_load_0 | 0 | 0.0063921 | 0.001602 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_121-17_0_3_load_2 | 2 | 0.0066548 | 0.0016679 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_121-17_0_3_load_20 | 4 | 0.00081292 | 0.00020374 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_121-17_0_3_load_56 | 7 | 0.0013347 | 0.0003345 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_121-17_0_3_load_64 | 12 | 0.0085955 | 0.0021542 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_121-17_0_3_load_27 | 15 | 0.0062203 | 0.0015589 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_121-17_0_3_load_33 | 18 | 0.0053122 | 0.0013314 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_121-17_0_3_load_71 | 21 | 0.098254 | 0.024625 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_121-17_0_3_load_59 | 25 | 0.011563 | 0.0028981 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_121-17_0_3_load_61 | 28 | 0.066297 | 0.016616 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_121-17_0_3_load_70 | 32 | 0.00099748 | 0.00024999 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_121-17_0_3_load_75 | 34 | 0.0028636 | 0.00071769 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_121-17_0_3_load_69 | 35 | 0.00063179 | 0.00015834 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_121-17_0_3_load_84 | 36 | 0.053614 | 0.013437 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_121-17_0_3_load_83 | 37 | 0.00053012 | 0.00013286 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_121-17_0_3_load_21 | 38 | 0.028641 | 0.0071781 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_121-17_0_3_load_28 | 39 | 0.0029449 | 0.00073807 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_121-17_0_3_load_73 | 42 | 0.0027598 | 0.00069167 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_121-17_0_3_load_72 | 43 | 0.0028106 | 0.00070441 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_121-17_0_3_load_34 | 44 | 0.0070606 | 0.0017696 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_121-17_0_3_load_77 | 45 | 0.037733 | 0.0094569 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_121-17_0_3_load_32 | 46 | 0.00076394 | 0.00019146 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_121-17_0_3_load_48 | 48 | 0.00025221 | 6.3211e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_121-17_0_3_load_74 | 49 | 0.0028208 | 0.00070695 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_121-17_0_3_load_25 | 52 | 0.00046744 | 0.00011715 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_121-17_0_3_load_30 | 54 | 0.001161 | 0.00029097 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_121-17_0_3_load_51 | 55 | 0.010451 | 0.0026194 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_121-17_0_3_load_29 | 56 | 0.0051206 | 0.0012833 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_121-17_0_3_load_54 | 59 | 0.0019386 | 0.00048586 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_121-17_0_3_load_82 | 61 | 0.0027743 | 0.00069529 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_121-17_0_3_load_49 | 63 | 0.00049933 | 0.00012514 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_121-17_0_3_load_36 | 64 | 0.0016591 | 0.00041581 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_121-17_0_3_load_40 | 67 | 0.0049939 | 0.0012516 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_121-17_0_3_load_41 | 68 | 0.0028621 | 0.00071731 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_121-17_0_3_load_62 | 69 | 0.0017486 | 0.00043824 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_121-17_0_3_load_63 | 71 | 0.00090335 | 0.0002264 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_121-17_0_3_load_81 | 72 | 0.00070959 | 0.00017784 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_121-17_0_3_load_79 | 73 | 0.00046071 | 0.00011547 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_121-17_0_3_load_42 | 74 | 0.0013691 | 0.00034314 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_121-17_0_3_load_76 | 77 | 0.00043527 | 0.00010909 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_121-17_0_3_load_78 | 78 | 0.0050188 | 0.0012578 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_121-17_0_3_load_66 | 79 | 0.00059761 | 0.00014977 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_121-17_0_3_load_67 | 80 | 0.0013263 | 0.0003324 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 45 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_121-17_0_3_line_0 |  | 0 | 1 | 0.043578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_121-17_0_3_line_1 |  | 0 | 2 | 0.025147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_121-17_0_3_line_2 |  | 1 | 3 | 0.061786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_121-17_0_3_line_3 |  | 3 | 4 | 0.024543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_121-17_0_3_line_4 |  | 4 | 22 | 0.011125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_121-17_0_3_line_5 |  | 5 | 6 | 0.037049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_121-17_0_3_line_6 |  | 5 | 7 | 0.011068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_121-17_0_3_line_7 |  | 6 | 36 | 0.022275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_121-17_0_3_line_8 |  | 6 | 23 | 0.004228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_121-17_0_3_line_9 |  | 7 | 8 | 0.012467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_121-17_0_3_line_10 |  | 8 | 9 | 0.003156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_121-17_0_3_line_11 |  | 9 | 37 | 0.000674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_121-17_0_3_line_12 |  | 10 | 11 | 0.044063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_121-17_0_3_line_13 |  | 10 | 12 | 0.029115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_121-17_0_3_line_14 |  | 11 | 35 | 0.0198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_121-17_0_3_line_15 |  | 13 | 14 | 0.003769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_121-17_0_3_line_16 |  | 13 | 15 | 0.0096276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_121-17_0_3_line_17 |  | 14 | 38 | 0.024331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_121-17_0_3_line_18 |  | 14 | 29 | 0.011705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_121-17_0_3_line_19 |  | 15 | 39 | 0.030871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_121-17_0_3_line_20 |  | 16 | 17 | 0.028614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_121-17_0_3_line_21 |  | 16 | 18 | 0.013144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_121-17_0_3_line_22 |  | 17 | 42 | 0.017718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_121-17_0_3_line_23 |  | 17 | 43 | 0.033447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_121-17_0_3_line_24 |  | 18 | 44 | 0.029485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_121-17_0_3_line_25 |  | 19 | 20 | 0.21777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_121-17_0_3_line_26 |  | 19 | 21 | 0.037637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_121-17_0_3_line_27 |  | 20 | 32 | 0.020983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_121-17_0_3_line_28 |  | 20 | 22 | 0.27239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_121-17_0_3_line_29 |  | 21 | 29 | 0.028871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_121-17_0_3_line_30 |  | 23 | 24 | 0.024432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_121-17_0_3_line_31 |  | 23 | 25 | 0.01245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
32 | LV_121-17_0_3_line_32 |  | 24 | 33 | 0.030911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_121-17_0_3_line_33 |  | 25 | 26 | 0.012603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
34 | LV_121-17_0_3_line_34 |  | 26 | 27 | 0.013233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_121-17_0_3_line_35 |  | 26 | 28 | 0.023472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_121-17_0_3_line_36 |  | 27 | 45 | 0.002369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
37 | LV_121-17_0_3_line_37 |  | 29 | 30 | 0.0086793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_121-17_0_3_line_38 |  | 29 | 31 | 0.023868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
39 | LV_121-17_0_3_line_39 |  | 30 | 34 | 0.019104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_121-17_0_3_line_40 |  | 31 | 46 | 0.043302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
41 | LV_121-17_0_3_line_41 |  | 32 | 40 | 0.012332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_121-17_0_3_line_42 |  | 33 | 47 | 0.007662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_121-17_0_3_line_43 |  | 33 | 48 | 0.0044376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
44 | LV_121-17_0_3_line_44 |  | 34 | 49 | 0.0013162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_121-17_0_3_line_45 |  | 35 | 41 | 0.0056785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_121-17_0_3_line_46 |  | 39 | 56 | 0.0037534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_121-17_0_3_line_47 |  | 40 | 41 | 0.044939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_121-17_0_3_line_48 |  | 41 | 79 | 0.0050847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_121-17_0_3_line_49 |  | 42 | 49 | 0.0010687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_121-17_0_3_line_50 |  | 46 | 63 | 0.0082156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
51 | LV_121-17_0_3_line_51 |  | 47 | 69 | 0.023181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_121-17_0_3_line_52 |  | 47 | 65 | 0.045368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_121-17_0_3_line_53 |  | 48 | 63 | 0.011687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
54 | LV_121-17_0_3_line_54 |  | 50 | 51 | 0.041391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_121-17_0_3_line_55 |  | 50 | 52 | 0.018667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_121-17_0_3_line_56 |  | 50 | 53 | 0.004322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_121-17_0_3_line_57 |  | 51 | 54 | 0.052911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_121-17_0_3_line_58 |  | 52 | 55 | 0.015998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_121-17_0_3_line_59 |  | 53 | 56 | 0.012924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_121-17_0_3_line_60 |  | 55 | 57 | 0.025438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_121-17_0_3_line_61 |  | 57 | 58 | 0.013549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_121-17_0_3_line_62 |  | 58 | 59 | 0.029995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_121-17_0_3_line_63 |  | 60 | 61 | 0.01402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_121-17_0_3_line_64 |  | 60 | 62 | 0.03817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_121-17_0_3_line_65 |  | 62 | 74 | 0.013092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_121-17_0_3_line_66 |  | 64 | 65 | 0.037092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_121-17_0_3_line_67 |  | 64 | 66 | 0.0085322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_121-17_0_3_line_68 |  | 66 | 67 | 0.0031675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_121-17_0_3_line_69 |  | 66 | 68 | 0.011066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_121-17_0_3_line_70 |  | 68 | 70 | 0.021636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_121-17_0_3_line_71 |  | 69 | 71 | 0.037805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_121-17_0_3_line_72 |  | 70 | 72 | 0.00381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_121-17_0_3_line_73 |  | 70 | 73 | 0.017479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_121-17_0_3_line_74 |  | 71 | 76 | 0.0067688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_121-17_0_3_line_75 |  | 73 | 78 | 0.013702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_121-17_0_3_line_76 |  | 74 | 75 | 0.0060757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_121-17_0_3_line_77 |  | 75 | 76 | 0.027973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_121-17_0_3_line_78 |  | 76 | 77 | 0.010003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_121-17_0_3_line_79 |  | 79 | 80 | 0.071631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_121-17_0_3_trafo_77 | 0.63 MVA 20/0.4 kV | 81 | 45 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11
0 | 2702714.9642 | 1241635.8311 | 2702708.7841 | 1241658.664 | 2702699.7673 | 1241675.4432 | 2702699.2227 | 1241676.1282
1 | 2702683.5729 | 1241695.812 | 2702699.2227 | 1241676.1282
2 | 2702714.9642 | 1241635.8311 | 2702720.377 | 1241628.9306 | 2702730.3363 | 1241622.3534 | 2702742.7734 | 1241620.2893 | 2702748.3193 | 1241624.4774 | 2702765.5096 | 1241637.4294
3 | 2702765.5096 | 1241637.4294 | 2702768.3034 | 1241639.4127 | 2702776.5043 | 1241645.7262 | 2702769.6843 | 1241654.0575
4 | 2702762.6375 | 1241662.6659 | 2702769.6843 | 1241654.0575
5 | 2702667.4355 | 1241797.2 | 2702672.3783 | 1241799.9654 | 2702676.5772 | 1241793.7221 | 2702682.2528 | 1241796.5225 | 2702690.2536 | 1241783.8177 | 2702692.5866 | 1241784.8923
6 | 2702692.5866 | 1241784.8923 | 2702702.4275 | 1241789.9574
7 | 2702678.5654 | 1241810.3471 | 2702664.423 | 1241802.6188 | 2702667.4355 | 1241797.2
8 | 2702667.4355 | 1241797.2 | 2702663.7359 | 1241795.1344
9 | 2702713.512 | 1241795.6627 | 2702702.4275 | 1241789.9574
10 | 2702713.512 | 1241795.6627 | 2702716.3068 | 1241797.1455
11 | 2702716.3068 | 1241797.1455 | 2702716.9064 | 1241797.4561
12 | 2702847.0824 | 1241922.3845 | 2702851.9114 | 1241926.4714 | 2702873.4401 | 1241901.1026 | 2702876.5133 | 1241897.8645
13 | 2702847.0824 | 1241922.3845 | 2702824.8541 | 1241903.5811
14 | 2702876.5133 | 1241897.8645 | 2702868.8306 | 1241890.0364 | 2702866.1599 | 1241881.6179
15 | 2702555.6715 | 1241838.989 | 2702553.6056 | 1241842.1447
16 | 2702553.6056 | 1241842.1447 | 2702546.7802 | 1241838.4906 | 2702545.2255 | 1241837.4236
17 | 2702555.6715 | 1241838.989 | 2702549.2549 | 1241834.875 | 2702535.4068 | 1241825.5249
18 | 2702566.5126 | 1241843.4798 | 2702555.6715 | 1241838.989
19 | 2702545.2255 | 1241837.4236 | 2702530.9229 | 1241827.6083 | 2702519.8665 | 1241819.8196
20 | 2702508.9393 | 1241885.0507 | 2702519.3289 | 1241883.7291 | 2702526.6021 | 1241883.777 | 2702536.5342 | 1241879.1783
21 | 2702508.9393 | 1241885.0507 | 2702495.8339 | 1241886.0537
22 | 2702536.5342 | 1241879.1783 | 2702544.6393 | 1241873.5362 | 2702550.0665 | 1241867.8743
23 | 2702536.5342 | 1241879.1783 | 2702544.8634 | 1241888.5628 | 2702553.2887 | 1241893.2675 | 2702562.0903 | 1241895.0098 | 2702564.3643 | 1241894.8907
24 | 2702466.5219 | 1241885.0408 | 2702482.2726 | 1241887.0917 | 2702495.8339 | 1241886.0537
25 | 2702618.1108 | 1241885.0816 | 2702620.8492 | 1241888.0757 | 2702630.366 | 1241898.7373 | 2702640.903 | 1241911.1847 | 2702642.7812 | 1241907.5143 | 2702646.1991 | 1241893.963 | 2702683.8784 | 1241879.9483 | 2702719.9158 | 1241866.0056 | 2702741.422 | 1241853.7016 | 2702760.7369 | 1241838.7022 | 2702797.6145 | 1241840.8757
26 | 2702618.1108 | 1241885.0816 | 2702614.716 | 1241881.1309 | 2702600.1736 | 1241867.6803 | 2702590.1435 | 1241860.0232
27 | 2702797.6145 | 1241840.8757 | 2702812.488 | 1241841.7451 | 2702818.3103 | 1241843.5102
28 | 2702762.6375 | 1241662.6659 | 2702760.0068 | 1241665.6782 | 2702769.8962 | 1241674.0447 | 2702832.68 | 1241674.1099 | 2702848.7133 | 1241679.2028 | 2702835.4944 | 1241700.6347 | 2702826.5418 | 1241727.2113 | 2702813.6836 | 1241765.3624 | 2702799.3609 | 1241795.9602 | 2702790.6994 | 1241807.9417 | 2702796.0758 | 1241826.6937 | 2702797.6145 | 1241840.8757
29 | 2702566.5126 | 1241843.4798 | 2702576.4665 | 1241851.18 | 2702590.1435 | 1241860.0232
30 | 2702642.7342 | 1241782.6505 | 2702647.2542 | 1241785.3752 | 2702663.7359 | 1241795.1344
31 | 2702663.7359 | 1241795.1344 | 2702658.1734 | 1241806.2722
32 | 2702616.1973 | 1241766.6682 | 2702642.7342 | 1241782.6505
33 | 2702652.5425 | 1241817.547 | 2702658.1734 | 1241806.2722
34 | 2702652.5425 | 1241817.547 | 2702640.8628 | 1241811.2624
35 | 2702652.5425 | 1241817.547 | 2702658.6258 | 1241820.8214 | 2702660.4506 | 1241817.6172 | 2702671.656 | 1241823.9608
36 | 2702640.8628 | 1241811.2624 | 2702638.7765 | 1241810.1401
37 | 2702564.1226 | 1241851.8227 | 2702564.9876 | 1241848.5908 | 2702566.5126 | 1241843.4798
38 | 2702578.4246 | 1241822.7808 | 2702566.5126 | 1241843.4798
39 | 2702564.1226 | 1241851.8227 | 2702563.0509 | 1241854.3284 | 2702551.7168 | 1241866.1526
40 | 2702578.4246 | 1241822.7808 | 2702602.5613 | 1241786.8299
41 | 2702830.112 | 1241847.0879 | 2702818.3103 | 1241843.5102
42 | 2702616.1973 | 1241766.6682 | 2702620.7354 | 1241760.4863
43 | 2702616.1973 | 1241766.6682 | 2702613.7113 | 1241770.344
44 | 2702550.806 | 1241867.1028 | 2702551.7168 | 1241866.1526
45 | 2702864.4428 | 1241876.2053 | 2702866.1599 | 1241881.6179
46 | 2702516.798 | 1241817.658 | 2702519.8665 | 1241819.8196
47 | 2702864.4428 | 1241876.2053 | 2702830.112 | 1241847.0879
48 | 2702864.4428 | 1241876.2053 | 2702864.8686 | 1241871.1384
49 | 2702550.0665 | 1241867.8743 | 2702550.806 | 1241867.1028
50 | 2702607.1639 | 1241780.0246 | 2702602.5862 | 1241786.7929 | 2702602.5613 | 1241786.8299
51 | 2702620.7354 | 1241760.4863 | 2702602.1654 | 1241746.6111
52 | 2702620.7354 | 1241760.4863 | 2702642.9037 | 1241730.035 | 2702647.4284 | 1241723.7529
53 | 2702613.7113 | 1241770.344 | 2702607.1639 | 1241780.0246
54 | 2702531.6124 | 1241771.0988 | 2702509.1205 | 1241805.8816
55 | 2702509.1205 | 1241805.8816 | 2702494.7387 | 1241793.9814
56 | 2702506.7666 | 1241809.5104 | 2702509.1205 | 1241805.8816
57 | 2702531.6124 | 1241771.0988 | 2702548.4469 | 1241784.9559 | 2702567.8695 | 1241787.3155 | 2702577.8099 | 1241793.1807
58 | 2702482.4131 | 1241783.7825 | 2702494.7387 | 1241793.9814
59 | 2702506.7666 | 1241809.5104 | 2702516.4076 | 1241817.383 | 2702516.798 | 1241817.658
60 | 2702463.2189 | 1241767.1036 | 2702471.5549 | 1241774.7979 | 2702482.4131 | 1241783.7825
61 | 2702455.0546 | 1241777.9154 | 2702460.2343 | 1241770.9106 | 2702463.2189 | 1241767.1036
62 | 2702455.0546 | 1241777.9154 | 2702438.1535 | 1241800.7413 | 2702437.0462 | 1241801.887
63 | 2702501.6012 | 1241718.1174 | 2702512.3334 | 1241727.1764
64 | 2702501.6012 | 1241718.1174 | 2702515.3236 | 1241699.4177 | 2702519.5646 | 1241695.1099 | 2702523.3188 | 1241693.151 | 2702528.067 | 1241693.1775
65 | 2702528.067 | 1241693.1775 | 2702533.555 | 1241694.5956 | 2702539.4697 | 1241699.0824
66 | 2702647.4284 | 1241723.7529 | 2702645.6727 | 1241722.5216 | 2702617.4849 | 1241701.8627
67 | 2702622.6013 | 1241695.0348 | 2702617.4849 | 1241701.8627
68 | 2702622.6013 | 1241695.0348 | 2702624.5874 | 1241692.5672
69 | 2702622.6013 | 1241695.0348 | 2702613.661 | 1241688.5133
70 | 2702596.1815 | 1241675.7632 | 2702613.661 | 1241688.5133
71 | 2702602.1654 | 1241746.6111 | 2702602.0726 | 1241746.5418 | 2702572.9108 | 1241724.4875 | 2702572.0152 | 1241723.804
72 | 2702596.1815 | 1241675.7632 | 2702593.1593 | 1241673.4314
73 | 2702596.1815 | 1241675.7632 | 2702589.3567 | 1241678.6252 | 2702585.4655 | 1241675.8225 | 2702585.6557 | 1241671.8227 | 2702584.629 | 1241671.0602
74 | 2702566.6343 | 1241719.6975 | 2702572.0152 | 1241723.804
75 | 2702573.629 | 1241662.8906 | 2702584.629 | 1241671.0602
76 | 2702544.3103 | 1241702.7543 | 2702539.4697 | 1241699.0824
77 | 2702544.3103 | 1241702.7543 | 2702545.6171 | 1241703.711 | 2702566.6343 | 1241719.6975
78 | 2702566.6343 | 1241719.6975 | 2702561.1734 | 1241728.0874
79 | 2702880.8789 | 1241801.3768 | 2702865.3004 | 1241866.0011 | 2702864.8686 | 1241871.1384

## bus_geodata
| x | y | coords
0 | 2702699.2227 | 1241676.1282
1 | 2702714.9642 | 1241635.8311
2 | 2702683.5729 | 1241695.812
3 | 2702765.5096 | 1241637.4294
4 | 2702769.6843 | 1241654.0575
5 | 2702692.5866 | 1241784.8923
6 | 2702667.4355 | 1241797.2
7 | 2702702.4275 | 1241789.9574
8 | 2702713.512 | 1241795.6627
9 | 2702716.3068 | 1241797.1455
10 | 2702847.0824 | 1241922.3845
11 | 2702876.5133 | 1241897.8645
12 | 2702824.8541 | 1241903.5811
13 | 2702553.6056 | 1241842.1447
14 | 2702555.6715 | 1241838.989
15 | 2702545.2255 | 1241837.4236
16 | 2702508.9393 | 1241885.0506
17 | 2702536.5342 | 1241879.1783
18 | 2702495.8339 | 1241886.0537
19 | 2702618.1108 | 1241885.0816
20 | 2702797.6145 | 1241840.8757
21 | 2702590.1435 | 1241860.0232
22 | 2702762.6375 | 1241662.6659
23 | 2702663.7359 | 1241795.1344
24 | 2702642.7342 | 1241782.6505
25 | 2702658.1734 | 1241806.2722
26 | 2702652.5425 | 1241817.547
27 | 2702640.8628 | 1241811.2624
28 | 2702671.656 | 1241823.9608
29 | 2702566.5126 | 1241843.4798
30 | 2702564.1226 | 1241851.8227
31 | 2702578.4246 | 1241822.7808
32 | 2702818.3103 | 1241843.5102
33 | 2702616.1973 | 1241766.6682
34 | 2702551.7168 | 1241866.1526
35 | 2702866.1599 | 1241881.6179
36 | 2702678.5654 | 1241810.3471
37 | 2702716.9064 | 1241797.4561
38 | 2702535.4068 | 1241825.5249
39 | 2702519.8665 | 1241819.8196
40 | 2702830.112 | 1241847.0879
41 | 2702864.4428 | 1241876.2053
42 | 2702550.0665 | 1241867.8743
43 | 2702564.3643 | 1241894.8907
44 | 2702466.5219 | 1241885.0408
45 | 2702638.7765 | 1241810.1401
46 | 2702602.5613 | 1241786.8299
47 | 2702620.7354 | 1241760.4863
48 | 2702613.7113 | 1241770.344
49 | 2702550.806 | 1241867.1028
50 | 2702509.1205 | 1241805.8816
51 | 2702531.6124 | 1241771.0988
52 | 2702494.7387 | 1241793.9814
53 | 2702506.7666 | 1241809.5104
54 | 2702577.8099 | 1241793.1807
55 | 2702482.4131 | 1241783.7825
56 | 2702516.798 | 1241817.658
57 | 2702463.2189 | 1241767.1036
58 | 2702455.0546 | 1241777.9154
59 | 2702437.0462 | 1241801.887
60 | 2702501.6012 | 1241718.1174
61 | 2702512.3334 | 1241727.1764
62 | 2702528.067 | 1241693.1775
63 | 2702607.1639 | 1241780.0246
64 | 2702617.4849 | 1241701.8627
65 | 2702647.4284 | 1241723.7529
66 | 2702622.6013 | 1241695.0348
67 | 2702624.5874 | 1241692.5672
68 | 2702613.661 | 1241688.5133
69 | 2702602.1654 | 1241746.6111
70 | 2702596.1815 | 1241675.7632
71 | 2702572.0152 | 1241723.804
72 | 2702593.1593 | 1241673.4314
73 | 2702584.629 | 1241671.0602
74 | 2702539.4697 | 1241699.0824
75 | 2702544.3103 | 1241702.7543
76 | 2702566.6343 | 1241719.6975
77 | 2702561.1734 | 1241728.0874
78 | 2702573.629 | 1241662.8906
79 | 2702864.8686 | 1241871.1384
80 | 2702880.8789 | 1241801.3768
81 | 2702640.8628 | 1241811.2624

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97082 | -0.56519 | 0.0063921 | 0.001602
1 | 0.97135 | -0.55468 | 0 | 0
2 | 0.97067 | -0.56828 | 0.0066548 | 0.0016679
3 | 0.97211 | -0.5398 | 0 | 0
4 | 0.97241 | -0.53389 | 0.00081292 | 0.00020374
5 | 0.99575 | -0.080819 | 0 | 0
6 | 0.99582 | -0.079603 | 0 | 0
7 | 0.99574 | -0.081182 | 0.0013347 | 0.0003345
8 | 0.99573 | -0.081298 | 0 | 0
9 | 0.99573 | -0.081327 | 0 | 0
10 | 0.97468 | -0.48908 | 0 | 0
11 | 0.97504 | -0.48214 | 0 | 0
12 | 0.97445 | -0.49368 | 0.0085955 | 0.0021542
13 | 0.98488 | -0.29008 | 0 | 0
14 | 0.98498 | -0.28817 | 0 | 0
15 | 0.98463 | -0.29498 | 0.0062203 | 0.0015589
16 | 0.98437 | -0.30002 | 0 | 0
17 | 0.98469 | -0.29366 | 0 | 0
18 | 0.98422 | -0.30295 | 0.0053122 | 0.0013314
19 | 0.98136 | -0.35852 | 0 | 0
20 | 0.97608 | -0.46168 | 0 | 0
21 | 0.98227 | -0.3408 | 0.098254 | 0.024625
22 | 0.97255 | -0.53105 | 0 | 0
23 | 0.99603 | -0.075481 | 0 | 0
24 | 0.99431 | -0.10835 | 0 | 0
25 | 0.99712 | -0.054737 | 0.011563 | 0.0028981
26 | 0.99827 | -0.032934 | 0 | 0
27 | 0.99974 | -0.0049934 | 0 | 0
28 | 0.99685 | -0.06019 | 0.066297 | 0.016616
29 | 0.98559 | -0.2762 | 0 | 0
30 | 0.9854 | -0.27988 | 0 | 0
31 | 0.98785 | -0.23243 | 0 | 0
32 | 0.97584 | -0.46635 | 0.00099748 | 0.00024999
33 | 0.99212 | -0.15011 | 0 | 0
34 | 0.98498 | -0.28799 | 0.0028636 | 0.00071769
35 | 0.9752 | -0.47902 | 0.00063179 | 0.00015834
36 | 0.99473 | -0.10062 | 0.053614 | 0.013437
37 | 0.99573 | -0.081334 | 0.00053012 | 0.00013286
38 | 0.98433 | -0.30069 | 0.028641 | 0.0071781
39 | 0.984 | -0.30725 | 0.0029449 | 0.00073807
40 | 0.97571 | -0.46887 | 0 | 0
41 | 0.97524 | -0.47805 | 0 | 0
42 | 0.98494 | -0.28882 | 0.0027598 | 0.00069167
43 | 0.98461 | -0.29535 | 0.0028106 | 0.00070441
44 | 0.98403 | -0.3067 | 0.0070606 | 0.0017696
45 | 1 | 0 | -0.36845 | -0.093523
46 | 0.99058 | -0.17975 | 0.00076394 | 0.00019146
47 | 0.99196 | -0.15322 | 0 | 0
48 | 0.99184 | -0.15552 | 0.00025221 | 6.3211e-05
49 | 0.98496 | -0.28848 | 0.0028208 | 0.00070695
50 | 0.98371 | -0.3129 | 0 | 0
51 | 0.98366 | -0.31377 | 0 | 0
52 | 0.98349 | -0.31723 | 0.00046744 | 0.00011715
53 | 0.98376 | -0.31181 | 0 | 0
54 | 0.98361 | -0.31488 | 0.001161 | 0.00029097
55 | 0.9833 | -0.3208 | 0.010451 | 0.0026194
56 | 0.98393 | -0.30855 | 0.0051206 | 0.0012833
57 | 0.98326 | -0.32169 | 0 | 0
58 | 0.98323 | -0.32216 | 0 | 0
59 | 0.98318 | -0.32321 | 0.0019386 | 0.00048586
60 | 0.99133 | -0.16544 | 0 | 0
61 | 0.9913 | -0.16613 | 0.0027743 | 0.00069529
62 | 0.99143 | -0.16357 | 0 | 0
63 | 0.9911 | -0.16975 | 0.00049933 | 0.00012514
64 | 0.99078 | -0.17619 | 0.0016591 | 0.00041581
65 | 0.99131 | -0.16585 | 0 | 0
66 | 0.99067 | -0.17832 | 0 | 0
67 | 0.99065 | -0.1786 | 0.0049939 | 0.0012516
68 | 0.99058 | -0.1801 | 0.0028621 | 0.00071731
69 | 0.99181 | -0.15619 | 0.0017486 | 0.00043824
70 | 0.99045 | -0.18248 | 0 | 0
71 | 0.99162 | -0.15987 | 0.00090335 | 0.0002264
72 | 0.99045 | -0.18253 | 0.00070959 | 0.00017784
73 | 0.99037 | -0.18418 | 0.00046071 | 0.00011547
74 | 0.99146 | -0.16292 | 0.0013691 | 0.00034314
75 | 0.99149 | -0.16247 | 0 | 0
76 | 0.99159 | -0.16042 | 0 | 0
77 | 0.99159 | -0.1605 | 0.00043527 | 0.00010909
78 | 0.9903 | -0.1854 | 0.0050188 | 0.0012578
79 | 0.97524 | -0.47823 | 0.00059761 | 0.00014977
80 | 0.97515 | -0.47998 | 0.0013263 | 0.0003324
81 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.013048 | -0.0032702 | 0.013054 | 0.0032738 | 6.5361e-06 | 3.644e-06 | 0.019999 | 0.019999 | 0.019999 | 0.97082 | -0.56519 | 0.97135 | -0.55468 | 5.4943
1 | 0.0066558 | 0.0016682 | -0.0066548 | -0.0016679 | 9.8143e-07 | 3.1723e-07 | 0.010202 | 0.010202 | 0.010202 | 0.97082 | -0.56519 | 0.97067 | -0.56828 | 2.8027
2 | -0.013054 | -0.0032738 | 0.013064 | 0.003279 | 9.2667e-06 | 5.1653e-06 | 0.019999 | 0.019999 | 0.019999 | 0.97135 | -0.55468 | 0.97211 | -0.5398 | 5.4942
3 | -0.013064 | -0.003279 | 0.013067 | 0.0032811 | 3.6809e-06 | 2.0514e-06 | 0.019999 | 0.019999 | 0.019999 | 0.97211 | -0.5398 | 0.97241 | -0.53389 | 5.4941
4 | -0.01388 | -0.0034848 | 0.013882 | 0.0034859 | 1.8825e-06 | 1.0668e-06 | 0.021243 | 0.021242 | 0.021243 | 0.97241 | -0.53389 | 0.97255 | -0.53105 | 5.8359
5 | -0.0018648 | -0.00046703 | 0.0018649 | 0.00046662 | 1.0788e-07 | -4.1293e-07 | 0.0027866 | 0.0027864 | 0.0027866 | 0.99575 | -0.080819 | 0.99582 | -0.079603 | 0.76555
6 | 0.0018648 | 0.00046703 | -0.0018648 | -0.00046715 | 3.223e-08 | -1.2334e-07 | 0.0027866 | 0.0027867 | 0.0027867 | 0.99575 | -0.080819 | 0.99574 | -0.081182 | 0.76557
7 | 0.053668 | 0.013471 | -0.053614 | -0.013437 | 5.373e-05 | 3.4097e-05 | 0.080201 | 0.080202 | 0.080202 | 0.99582 | -0.079603 | 0.99473 | -0.10062 | 22.0334
8 | -0.055533 | -0.013938 | 0.055544 | 0.013945 | 1.0919e-05 | 6.9333e-06 | 0.082988 | 0.082988 | 0.082988 | 0.99582 | -0.079603 | 0.99603 | -0.075481 | 22.7989
9 | 0.00053012 | 0.00013265 | -0.00053012 | -0.00013281 | 2.9337e-09 | -1.6028e-07 | 0.00079214 | 0.00079219 | 0.00079219 | 0.99574 | -0.081182 | 0.99573 | -0.081298 | 0.21764
10 | 0.00053012 | 0.00013281 | -0.00053012 | -0.00013285 | 7.4273e-10 | -4.0576e-08 | 0.00079219 | 0.00079221 | 0.00079221 | 0.99573 | -0.081298 | 0.99573 | -0.081327 | 0.21764
11 | 0.00053012 | 0.00013285 | -0.00053012 | -0.00013286 | 1.5863e-10 | -8.6654e-09 | 0.00079221 | 0.00079221 | 0.00079221 | 0.99573 | -0.081327 | 0.99573 | -0.081334 | 0.21764
12 | -0.0085973 | -0.0021551 | 0.0086002 | 0.0021563 | 2.8466e-06 | 1.2724e-06 | 0.013125 | 0.013125 | 0.013125 | 0.97468 | -0.48908 | 0.97504 | -0.48214 | 3.6059
13 | 0.0085973 | 0.0021551 | -0.0085955 | -0.0021542 | 1.8809e-06 | 8.4101e-07 | 0.013125 | 0.013126 | 0.013126 | 0.97468 | -0.48908 | 0.97445 | -0.49368 | 3.6059
14 | -0.0086002 | -0.0021563 | 0.0086015 | 0.0021569 | 1.2791e-06 | 5.7164e-07 | 0.013125 | 0.013125 | 0.013125 | 0.97504 | -0.48214 | 0.9752 | -0.47902 | 3.6058
15 | -0.028333 | -0.0071088 | 0.028336 | 0.0071104 | 2.5903e-06 | 1.6098e-06 | 0.04281 | 0.04281 | 0.04281 | 0.98488 | -0.29008 | 0.98498 | -0.28817 | 11.761
16 | 0.028333 | 0.0071088 | -0.028326 | -0.0071047 | 6.6167e-06 | 4.1122e-06 | 0.04281 | 0.04281 | 0.04281 | 0.98488 | -0.29008 | 0.98463 | -0.29498 | 11.761
17 | 0.028658 | 0.0071887 | -0.028641 | -0.0071781 | 1.7104e-05 | 1.0637e-05 | 0.043296 | 0.043296 | 0.043296 | 0.98498 | -0.28817 | 0.98433 | -0.30069 | 11.8946
18 | -0.056993 | -0.014299 | 0.057026 | 0.01432 | 3.2544e-05 | 2.0679e-05 | 0.086106 | 0.086106 | 0.086106 | 0.98498 | -0.28817 | 0.98559 | -0.2762 | 23.6556
19 | 0.022106 | 0.0055458 | -0.022093 | -0.0055379 | 1.2922e-05 | 7.8777e-06 | 0.03341 | 0.03341 | 0.03341 | 0.98463 | -0.29498 | 0.984 | -0.30725 | 9.1786
20 | -0.012376 | -0.0031023 | 0.01238 | 0.0031043 | 3.7555e-06 | 2.0396e-06 | 0.018708 | 0.018708 | 0.018708 | 0.98437 | -0.30002 | 0.98469 | -0.29366 | 5.1396
21 | 0.012376 | 0.0031023 | -0.012374 | -0.0031013 | 1.7251e-06 | 9.3698e-07 | 0.018708 | 0.018708 | 0.018708 | 0.98437 | -0.30002 | 0.98422 | -0.30295 | 5.1396
22 | -0.01519 | -0.0038085 | 0.015194 | 0.0038105 | 3.5013e-06 | 2.0154e-06 | 0.022955 | 0.022955 | 0.022955 | 0.98469 | -0.29366 | 0.98494 | -0.28882 | 6.3064
23 | 0.0028108 | 0.00070413 | -0.0028106 | -0.00070441 | 2.2629e-07 | -2.8061e-07 | 0.0042475 | 0.0042476 | 0.0042476 | 0.98469 | -0.29366 | 0.98461 | -0.29535 | 1.1669
24 | 0.0070619 | 0.00177 | -0.0070606 | -0.0017696 | 1.2604e-06 | 4.3203e-07 | 0.010677 | 0.010677 | 0.010677 | 0.98422 | -0.30295 | 0.98403 | -0.3067 | 2.9332
25 | 0.026222 | 0.0066434 | -0.026092 | -0.0065634 | 0.00012927 | 7.9994e-05 | 0.039785 | 0.039786 | 0.039786 | 0.98136 | -0.35852 | 0.97608 | -0.46168 | 10.9303
26 | -0.026222 | -0.0066434 | 0.026244 | 0.0066573 | 2.234e-05 | 1.3822e-05 | 0.039785 | 0.039785 | 0.039785 | 0.98136 | -0.35852 | 0.98227 | -0.3408 | 10.93
27 | 0.012164 | 0.0030515 | -0.012161 | -0.00305 | 2.7062e-06 | 1.4698e-06 | 0.018545 | 0.018545 | 0.018545 | 0.97608 | -0.46168 | 0.97584 | -0.46635 | 5.0948
28 | 0.013928 | 0.003512 | -0.013882 | -0.0034859 | 4.6089e-05 | 2.6105e-05 | 0.021241 | 0.021242 | 0.021242 | 0.97608 | -0.46168 | 0.97255 | -0.53105 | 5.8358
29 | -0.1245 | -0.031282 | 0.12488 | 0.031528 | 0.00038522 | 0.00024617 | 0.18863 | 0.18863 | 0.18863 | 0.98227 | -0.3408 | 0.98559 | -0.2762 | 51.8206
30 | 0.23212 | 0.059252 | -0.23175 | -0.059017 | 0.00036807 | 0.00023461 | 0.34716 | 0.34716 | 0.34716 | 0.99603 | -0.075481 | 0.99431 | -0.10835 | 31.7913
31 | -0.28767 | -0.073197 | 0.28795 | 0.07338 | 0.00028794 | 0.00018379 | 0.43015 | 0.43015 | 0.43015 | 0.99603 | -0.075481 | 0.99712 | -0.054737 | 39.3908
32 | 0.23175 | 0.059017 | -0.23129 | -0.058721 | 0.00046568 | 0.00029683 | 0.34716 | 0.34716 | 0.34716 | 0.99431 | -0.10835 | 0.99212 | -0.15011 | 31.7913
33 | -0.29952 | -0.076279 | 0.29983 | 0.07648 | 0.00031534 | 0.00020132 | 0.4474 | 0.4474 | 0.4474 | 0.99712 | -0.054737 | 0.99827 | -0.032934 | 40.971
34 | -0.36622 | -0.09315 | 0.36671 | 0.093466 | 0.00049378 | 0.0003155 | 0.54637 | 0.54637 | 0.54637 | 0.99827 | -0.032934 | 0.99974 | -0.0049934 | 50.0335
35 | 0.066384 | 0.016671 | -0.066297 | -0.016616 | 8.6206e-05 | 5.4865e-05 | 0.098963 | 0.098963 | 0.098963 | 0.99827 | -0.032934 | 0.99685 | -0.06019 | 27.1877
36 | -0.36671 | -0.093466 | 0.3668 | 0.093522 | 8.8399e-05 | 5.6482e-05 | 0.54637 | 0.54637 | 0.54637 | 0.99974 | -0.0049934 | 1 | 0 | 50.0335
37 | 0.023652 | 0.0059354 | -0.023648 | -0.0059329 | 4.151e-06 | 2.546e-06 | 0.035712 | 0.035712 | 0.035712 | 0.98559 | -0.2762 | 0.9854 | -0.27988 | 9.811
38 | -0.20556 | -0.051783 | 0.20599 | 0.052059 | 0.00043131 | 0.00027543 | 0.31045 | 0.31044 | 0.31045 | 0.98559 | -0.2762 | 0.98785 | -0.23243 | 42.6436
39 | 0.023648 | 0.0059329 | -0.023639 | -0.0059273 | 9.1368e-06 | 5.6043e-06 | 0.035712 | 0.035712 | 0.035712 | 0.9854 | -0.27988 | 0.98498 | -0.28799 | 9.8111
40 | -0.20599 | -0.052059 | 0.20651 | 0.052391 | 0.00052166 | 0.00033219 | 0.31044 | 0.31044 | 0.31044 | 0.98785 | -0.23243 | 0.99058 | -0.17975 | 28.429
41 | 0.011164 | 0.0028 | -0.011163 | -0.0027993 | 1.3403e-06 | 7.0374e-07 | 0.017024 | 0.017024 | 0.017024 | 0.97584 | -0.46635 | 0.97571 | -0.46887 | 4.677
42 | 0.022962 | 0.005761 | -0.022959 | -0.005759 | 3.4083e-06 | 2.0824e-06 | 0.034441 | 0.034442 | 0.034442 | 0.99212 | -0.15011 | 0.99196 | -0.15322 | 9.462
43 | 0.20833 | 0.05296 | -0.20827 | -0.052925 | 5.4246e-05 | 3.4545e-05 | 0.31272 | 0.31272 | 0.31272 | 0.99212 | -0.15011 | 0.99184 | -0.15552 | 28.6373
44 | 0.020775 | 0.0052096 | -0.020775 | -0.0052093 | 4.8622e-07 | 2.9443e-07 | 0.031386 | 0.031386 | 0.031386 | 0.98498 | -0.28799 | 0.98496 | -0.28848 | 8.6226
45 | -0.0092333 | -0.0023153 | 0.0092337 | 0.0023155 | 4.227e-07 | 1.9968e-07 | 0.014089 | 0.014089 | 0.014089 | 0.9752 | -0.47902 | 0.97524 | -0.47805 | 3.8706
46 | 0.019148 | 0.0047998 | -0.019147 | -0.0047991 | 1.1802e-06 | 7.0765e-07 | 0.028957 | 0.028957 | 0.028957 | 0.984 | -0.30725 | 0.98393 | -0.30855 | 7.9551
47 | 0.011163 | 0.0027993 | -0.011158 | -0.0027968 | 4.8842e-06 | 2.5649e-06 | 0.017024 | 0.017024 | 0.017024 | 0.97571 | -0.46887 | 0.97524 | -0.47805 | 4.677
48 | 0.001924 | 0.0004813 | -0.001924 | -0.00048135 | 1.6429e-08 | -5.293e-08 | 0.0029353 | 0.0029354 | 0.0029354 | 0.97524 | -0.47805 | 0.97524 | -0.47823 | 0.80642
49 | -0.017954 | -0.0045021 | 0.017954 | 0.0045023 | 2.9487e-07 | 1.7512e-07 | 0.027125 | 0.027125 | 0.027125 | 0.98494 | -0.28882 | 0.98496 | -0.28848 | 7.4518
50 | -0.20728 | -0.052582 | 0.20738 | 0.052646 | 9.9706e-05 | 6.3494e-05 | 0.31159 | 0.31159 | 0.31159 | 0.99058 | -0.17975 | 0.9911 | -0.16975 | 28.5341
51 | 0.0072336 | 0.0018118 | -0.0072326 | -0.0018115 | 1.0235e-06 | 3.5582e-07 | 0.010851 | 0.010851 | 0.010851 | 0.99196 | -0.15322 | 0.99181 | -0.15619 | 2.981
52 | 0.015725 | 0.0039471 | -0.015716 | -0.0039417 | 9.4684e-06 | 5.4745e-06 | 0.023591 | 0.023591 | 0.023591 | 0.99196 | -0.15322 | 0.99131 | -0.16585 | 6.4811
53 | 0.20802 | 0.052862 | -0.20788 | -0.052771 | 0.00014252 | 9.0759e-05 | 0.31234 | 0.31234 | 0.31234 | 0.99184 | -0.15552 | 0.9911 | -0.16975 | 28.6027
54 | 0.0011611 | 0.00028985 | -0.0011611 | -0.00029034 | 4.7864e-08 | -4.9481e-07 | 0.001756 | 0.0017561 | 0.0017561 | 0.98371 | -0.3129 | 0.98366 | -0.31377 | 0.48246
55 | 0.012862 | 0.0032243 | -0.01286 | -0.0032228 | 2.65e-06 | 1.4591e-06 | 0.019457 | 0.019457 | 0.019457 | 0.98371 | -0.3129 | 0.98349 | -0.31723 | 5.3453
56 | -0.014024 | -0.0035141 | 0.014024 | 0.0035145 | 7.293e-07 | 4.1188e-07 | 0.021213 | 0.021213 | 0.021213 | 0.98371 | -0.3129 | 0.98376 | -0.31181 | 5.8277
57 | 0.0011611 | 0.00029034 | -0.001161 | -0.00029097 | 6.1201e-08 | -6.3246e-07 | 0.0017561 | 0.0017564 | 0.0017564 | 0.98366 | -0.31377 | 0.98361 | -0.31488 | 0.48252
58 | 0.012392 | 0.0031056 | -0.01239 | -0.0031045 | 2.109e-06 | 1.1468e-06 | 0.01875 | 0.01875 | 0.01875 | 0.98349 | -0.31723 | 0.9833 | -0.3208 | 5.151
59 | -0.014024 | -0.0035145 | 0.014026 | 0.0035158 | 2.1809e-06 | 1.2316e-06 | 0.021213 | 0.021213 | 0.021213 | 0.98376 | -0.31181 | 0.98393 | -0.30855 | 5.8277
60 | 0.0019388 | 0.00048513 | -0.0019387 | -0.0004854 | 8.2103e-08 | -2.7011e-07 | 0.0029337 | 0.0029338 | 0.0029338 | 0.9833 | -0.3208 | 0.98326 | -0.32169 | 0.806
61 | 0.0019387 | 0.0004854 | -0.0019387 | -0.00048554 | 4.3735e-08 | -1.4386e-07 | 0.0029338 | 0.0029339 | 0.0029339 | 0.98326 | -0.32169 | 0.98323 | -0.32216 | 0.80601
62 | 0.0019387 | 0.00048554 | -0.0019386 | -0.00048586 | 9.6826e-08 | -3.1844e-07 | 0.0029339 | 0.002934 | 0.002934 | 0.98323 | -0.32216 | 0.98318 | -0.32321 | 0.80605
63 | 0.0027743 | 0.00069517 | -0.0027743 | -0.00069529 | 9.1174e-08 | -1.224e-07 | 0.0041643 | 0.0041644 | 0.0041644 | 0.99133 | -0.16544 | 0.9913 | -0.16613 | 1.1441
64 | -0.0027743 | -0.00069517 | 0.0027746 | 0.00069484 | 2.4821e-07 | -3.3331e-07 | 0.0041643 | 0.0041641 | 0.0041643 | 0.99133 | -0.16544 | 0.99143 | -0.16357 | 1.144
65 | -0.0027746 | -0.00069484 | 0.0027747 | 0.00069472 | 8.5131e-08 | -1.1435e-07 | 0.0041641 | 0.0041641 | 0.0041641 | 0.99143 | -0.16357 | 0.99146 | -0.16292 | 1.144
66 | -0.015708 | -0.0039372 | 0.015716 | 0.0039417 | 7.7413e-06 | 4.4765e-06 | 0.023591 | 0.023591 | 0.023591 | 0.99078 | -0.17619 | 0.99131 | -0.16585 | 6.4811
67 | 0.014049 | 0.0035214 | -0.014047 | -0.0035206 | 1.4244e-06 | 8.0176e-07 | 0.0211 | 0.0211 | 0.0211 | 0.99078 | -0.17619 | 0.99067 | -0.17832 | 5.7966
68 | 0.0049939 | 0.0012516 | -0.0049939 | -0.0012516 | 6.6834e-08 | 1.9903e-09 | 0.007501 | 0.007501 | 0.007501 | 0.99067 | -0.17832 | 0.99065 | -0.1786 | 2.0607
69 | 0.0090534 | 0.002269 | -0.0090527 | -0.0022686 | 7.6739e-07 | 3.4866e-07 | 0.013599 | 0.013599 | 0.013599 | 0.99067 | -0.17832 | 0.99058 | -0.1801 | 3.7359
70 | 0.0061906 | 0.0015513 | -0.0061899 | -0.0015512 | 7.0161e-07 | 1.7055e-07 | 0.0092992 | 0.0092993 | 0.0092993 | 0.99058 | -0.1801 | 0.99045 | -0.18248 | 2.5548
71 | 0.005484 | 0.0013732 | -0.005483 | -0.0013731 | 9.5961e-07 | 1.2636e-07 | 0.0082272 | 0.0082274 | 0.0082274 | 0.99181 | -0.15619 | 0.99162 | -0.15987 | 2.2603
72 | 0.00070959 | 0.00017779 | -0.00070959 | -0.00017784 | 1.6237e-09 | -4.7996e-08 | 0.001066 | 0.0010661 | 0.0010661 | 0.99045 | -0.18248 | 0.99045 | -0.18253 | 0.29287
73 | 0.0054803 | 0.0013734 | -0.0054798 | -0.0013733 | 4.4433e-07 | 5.9432e-08 | 0.0082333 | 0.0082334 | 0.0082334 | 0.99045 | -0.18248 | 0.99037 | -0.18418 | 2.2619
74 | 0.0045797 | 0.0011467 | -0.0045796 | -0.0011467 | 1.1987e-07 | -1.0604e-08 | 0.0068719 | 0.0068719 | 0.0068719 | 0.99162 | -0.15987 | 0.99159 | -0.16042 | 1.8879
75 | 0.0050191 | 0.0012578 | -0.0050188 | -0.0012578 | 2.9221e-07 | 1.0711e-08 | 0.0075411 | 0.0075412 | 0.0075412 | 0.99037 | -0.18418 | 0.9903 | -0.1854 | 2.0718
76 | -0.0041438 | -0.0010379 | 0.0041439 | 0.0010378 | 8.8116e-08 | -2.1962e-08 | 0.0062189 | 0.0062189 | 0.0062189 | 0.99146 | -0.16292 | 0.99149 | -0.16247 | 1.7085
77 | -0.0041439 | -0.0010378 | 0.0041443 | 0.0010377 | 4.0568e-07 | -1.0117e-07 | 0.0062189 | 0.0062188 | 0.0062189 | 0.99149 | -0.16247 | 0.99159 | -0.16042 | 1.7085
78 | 0.00043527 | 0.00010896 | -0.00043527 | -0.00010909 | 1.6003e-09 | -1.2801e-07 | 0.00065313 | 0.00065318 | 0.00065318 | 0.99159 | -0.16042 | 0.99159 | -0.1605 | 0.17944
79 | 0.0013264 | 0.00033158 | -0.0013263 | -0.0003324 | 1.1001e-07 | -8.2329e-07 | 0.0020235 | 0.0020239 | 0.0020239 | 0.97524 | -0.47823 | 0.97515 | -0.47998 | 0.556

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.40618 | 0.10298

## res_load
| p_mw | q_mvar
0 | 0.0063921 | 0.001602
1 | 0.0066548 | 0.0016679
2 | 0.00081292 | 0.00020374
3 | 0.0013347 | 0.0003345
4 | 0.0085955 | 0.0021542
5 | 0.0062203 | 0.0015589
6 | 0.0053122 | 0.0013314
7 | 0.098254 | 0.024625
8 | 0.011563 | 0.0028981
9 | 0.066297 | 0.016616
10 | 0.00099748 | 0.00024999
11 | 0.0028636 | 0.00071769
12 | 0.00063179 | 0.00015834
13 | 0.053614 | 0.013437
14 | 0.00053012 | 0.00013286
15 | 0.028641 | 0.0071781
16 | 0.0029449 | 0.00073807
17 | 0.0027598 | 0.00069167
18 | 0.0028106 | 0.00070441
19 | 0.0070606 | 0.0017696
20 | 0.037733 | 0.0094569
21 | 0.00076394 | 0.00019146
22 | 0.00025221 | 6.3211e-05
23 | 0.0028208 | 0.00070695
24 | 0.00046744 | 0.00011715
25 | 0.001161 | 0.00029097
26 | 0.010451 | 0.0026194
27 | 0.0051206 | 0.0012833
28 | 0.0019386 | 0.00048586
29 | 0.0027743 | 0.00069529
30 | 0.00049933 | 0.00012514
31 | 0.0016591 | 0.00041581
32 | 0.0049939 | 0.0012516
33 | 0.0028621 | 0.00071731
34 | 0.0017486 | 0.00043824
35 | 0.00090335 | 0.0002264
36 | 0.00070959 | 0.00017784
37 | 0.00046071 | 0.00011547
38 | 0.0013691 | 0.00034314
39 | 0.00043527 | 0.00010909
40 | 0.0050188 | 0.0012578
41 | 0.00059761 | 0.00014977
42 | 0.0013263 | 0.0003324

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1