## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_121-26_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_121-26_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_121-26_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_121-26_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_121-26_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_121-26_0_5_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_121-26_0_5_node_22 | 0.4 | n |  | TRUE
7 | bus_LV_121-26_0_5_node_23 | 0.4 | n |  | TRUE
8 | bus_LV_121-26_0_5_node_42 | 0.4 | n |  | TRUE
9 | bus_LV_121-26_0_5_node_44 | 0.4 | n |  | TRUE
10 | bus_LV_121-26_0_5_node_141 | 0.4 | n |  | TRUE
11 | bus_LV_121-26_0_5_node_134 | 0.4 | n |  | TRUE
12 | bus_LV_121-26_0_5_node_19 | 0.4 | n |  | TRUE
13 | bus_LV_121-26_0_5_node_45 | 0.4 | n |  | TRUE
14 | bus_LV_121-26_0_5_node_6 | 0.4 | n |  | TRUE
15 | bus_LV_121-26_0_5_node_7 | 0.4 | n |  | TRUE
16 | bus_LV_121-26_0_5_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_121-26_0_5_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_121-26_0_5_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_121-26_0_5_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_121-26_0_5_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_121-26_0_5_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_121-26_0_5_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_121-26_0_5_node_36 | 0.4 | n |  | TRUE
24 | bus_LV_121-26_0_5_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_121-26_0_5_node_43 | 0.4 | n |  | TRUE
26 | bus_LV_121-26_0_5_node_69 | 0.4 | n |  | TRUE
27 | bus_LV_121-26_0_5_node_142 | 0.4 | n |  | TRUE
28 | bus_LV_121-26_0_5_node_37 | 0.4 | n |  | TRUE
29 | bus_LV_121-26_0_5_node_80 | 0.4 | n |  | TRUE
30 | bus_LV_121-26_0_5_node_67 | 0.4 | n |  | TRUE
31 | bus_LV_121-26_0_5_node_143 | 0.4 | n |  | TRUE
32 | bus_LV_121-26_0_5_node_16 | 0.4 | n |  | TRUE
33 | bus_LV_121-26_0_5_node_17 | 0.4 | n |  | TRUE
34 | bus_LV_121-26_0_5_node_18 | 0.4 | n |  | TRUE
35 | bus_LV_121-26_0_5_node_20 | 0.4 | n |  | TRUE
36 | bus_LV_121-26_0_5_node_21 | 0.4 | n |  | TRUE
37 | bus_LV_121-26_0_5_node_24 | 0.4 | n |  | TRUE
38 | bus_LV_121-26_0_5_node_39 | 0.4 | n |  | TRUE
39 | bus_LV_121-26_0_5_node_40 | 0.4 | n |  | TRUE
40 | bus_LV_121-26_0_5_node_133 | 0.4 | n |  | TRUE
41 | bus_LV_121-26_0_5_node_28 | 0.4 | n |  | TRUE
42 | bus_LV_121-26_0_5_node_26 | 0.4 | n |  | TRUE
43 | bus_LV_121-26_0_5_node_27 | 0.4 | n |  | TRUE
44 | bus_LV_121-26_0_5_node_29 | 0.4 | n |  | TRUE
45 | bus_LV_121-26_0_5_node_83 | 0.4 | n |  | TRUE
46 | bus_LV_121-26_0_5_node_102 | 0.4 | n |  | TRUE
47 | bus_LV_121-26_0_5_node_30 | 0.4 | n |  | TRUE
48 | bus_LV_121-26_0_5_node_31 | 0.4 | n |  | TRUE
49 | bus_LV_121-26_0_5_node_32 | 0.4 | n |  | TRUE
50 | bus_LV_121-26_0_5_node_33 | 0.4 | n |  | TRUE
51 | bus_LV_121-26_0_5_node_35 | 0.4 | n |  | TRUE
52 | bus_LV_121-26_0_5_node_77 | 0.4 | n |  | TRUE
53 | bus_LV_121-26_0_5_node_34 | 0.4 | n |  | TRUE
54 | bus_LV_121-26_0_5_node_72 | 0.4 | n |  | TRUE
55 | bus_LV_121-26_0_5_node_41 | 0.4 | n |  | TRUE
56 | bus_LV_121-26_0_5_node_76 | 0.4 | n |  | TRUE
57 | bus_LV_121-26_0_5_node_38 | 0.4 | n |  | TRUE
58 | bus_LV_121-26_0_5_node_46 | 0.4 | n |  | TRUE
59 | bus_LV_121-26_0_5_node_47 | 0.4 | n |  | TRUE
60 | bus_LV_121-26_0_5_node_48 | 0.4 | n |  | TRUE
61 | bus_LV_121-26_0_5_node_49 | 0.4 | n |  | TRUE
62 | bus_LV_121-26_0_5_node_50 | 0.4 | n |  | TRUE
63 | bus_LV_121-26_0_5_node_65 | 0.4 | n |  | TRUE
64 | bus_LV_121-26_0_5_node_60 | 0.4 | n |  | TRUE
65 | bus_LV_121-26_0_5_node_98 | 0.4 | n |  | TRUE
66 | bus_LV_121-26_0_5_node_146 | 0.4 | n |  | TRUE
67 | bus_LV_121-26_0_5_node_152 | 0.4 | n |  | TRUE
68 | bus_LV_121-26_0_5_node_58 | 0.4 | n |  | TRUE
69 | bus_LV_121-26_0_5_node_97 | 0.4 | n |  | TRUE
70 | bus_LV_121-26_0_5_node_51 | 0.4 | n |  | TRUE
71 | bus_LV_121-26_0_5_node_52 | 0.4 | n |  | TRUE
72 | bus_LV_121-26_0_5_node_53 | 0.4 | n |  | TRUE
73 | bus_LV_121-26_0_5_node_54 | 0.4 | n |  | TRUE
74 | bus_LV_121-26_0_5_node_55 | 0.4 | n |  | TRUE
75 | bus_LV_121-26_0_5_node_56 | 0.4 | n |  | TRUE
76 | bus_LV_121-26_0_5_node_62 | 0.4 | n |  | TRUE
77 | bus_LV_121-26_0_5_node_91 | 0.4 | n |  | TRUE
78 | bus_LV_121-26_0_5_node_119 | 0.4 | n |  | TRUE
79 | bus_LV_121-26_0_5_node_63 | 0.4 | n |  | TRUE
80 | bus_LV_121-26_0_5_node_92 | 0.4 | n |  | TRUE
81 | bus_LV_121-26_0_5_node_118 | 0.4 | n |  | TRUE
82 | bus_LV_121-26_0_5_node_57 | 0.4 | n |  | TRUE
83 | bus_LV_121-26_0_5_node_59 | 0.4 | n |  | TRUE
84 | bus_LV_121-26_0_5_node_61 | 0.4 | n |  | TRUE
85 | bus_LV_121-26_0_5_node_81 | 0.4 | n |  | TRUE
86 | bus_LV_121-26_0_5_node_82 | 0.4 | n |  | TRUE
87 | bus_LV_121-26_0_5_node_64 | 0.4 | n |  | TRUE
88 | bus_LV_121-26_0_5_node_96 | 0.4 | n |  | TRUE
89 | bus_LV_121-26_0_5_node_144 | 0.4 | n |  | TRUE
90 | bus_LV_121-26_0_5_node_66 | 0.4 | n |  | TRUE
91 | bus_LV_121-26_0_5_node_68 | 0.4 | n |  | TRUE
92 | bus_LV_121-26_0_5_node_70 | 0.4 | n |  | TRUE
93 | bus_LV_121-26_0_5_node_99 | 0.4 | n |  | TRUE
94 | bus_LV_121-26_0_5_node_71 | 0.4 | n |  | TRUE
95 | bus_LV_121-26_0_5_node_100 | 0.4 | n |  | TRUE
96 | bus_LV_121-26_0_5_node_137 | 0.4 | n |  | TRUE
97 | bus_LV_121-26_0_5_node_101 | 0.4 | n |  | TRUE
98 | bus_LV_121-26_0_5_node_73 | 0.4 | n |  | TRUE
99 | bus_LV_121-26_0_5_node_74 | 0.4 | n |  | TRUE
100 | bus_LV_121-26_0_5_node_75 | 0.4 | n |  | TRUE
101 | bus_LV_121-26_0_5_node_93 | 0.4 | n |  | TRUE
102 | bus_LV_121-26_0_5_node_94 | 0.4 | n |  | TRUE
103 | bus_LV_121-26_0_5_node_78 | 0.4 | n |  | TRUE
104 | bus_LV_121-26_0_5_node_79 | 0.4 | n |  | TRUE
105 | bus_LV_121-26_0_5_node_136 | 0.4 | n |  | TRUE
106 | bus_LV_121-26_0_5_node_104 | 0.4 | n |  | TRUE
107 | bus_LV_121-26_0_5_node_105 | 0.4 | n |  | TRUE
108 | bus_LV_121-26_0_5_node_103 | 0.4 | n |  | TRUE
109 | bus_LV_121-26_0_5_node_84 | 0.4 | n |  | TRUE
110 | bus_LV_121-26_0_5_node_85 | 0.4 | n |  | TRUE
111 | bus_LV_121-26_0_5_node_86 | 0.4 | n |  | TRUE
112 | bus_LV_121-26_0_5_node_87 | 0.4 | n |  | TRUE
113 | bus_LV_121-26_0_5_node_88 | 0.4 | n |  | TRUE
114 | bus_LV_121-26_0_5_node_89 | 0.4 | n |  | TRUE
115 | bus_LV_121-26_0_5_node_120 | 0.4 | n |  | TRUE
116 | bus_LV_121-26_0_5_node_90 | 0.4 | n |  | TRUE
117 | bus_LV_121-26_0_5_node_148 | 0.4 | n |  | TRUE
118 | bus_LV_121-26_0_5_node_147 | 0.4 | n |  | TRUE
119 | bus_LV_121-26_0_5_node_106 | 0.4 | n |  | TRUE
120 | bus_LV_121-26_0_5_node_107 | 0.4 | n |  | TRUE
121 | bus_LV_121-26_0_5_node_95 | 0.4 | n |  | TRUE
122 | bus_LV_121-26_0_5_node_113 | 0.4 | n |  | TRUE
123 | bus_LV_121-26_0_5_node_114 | 0.4 | n |  | TRUE
124 | bus_LV_121-26_0_5_node_109 | 0.4 | n |  | TRUE
125 | bus_LV_121-26_0_5_node_110 | 0.4 | n |  | TRUE
126 | bus_LV_121-26_0_5_node_117 | 0.4 | n |  | TRUE
127 | bus_LV_121-26_0_5_node_115 | 0.4 | n |  | TRUE
128 | bus_LV_121-26_0_5_node_108 | 0.4 | n |  | TRUE
129 | bus_LV_121-26_0_5_node_111 | 0.4 | n |  | TRUE
130 | bus_LV_121-26_0_5_node_112 | 0.4 | n |  | TRUE
131 | bus_LV_121-26_0_5_node_138 | 0.4 | n |  | TRUE
132 | bus_LV_121-26_0_5_node_135 | 0.4 | n |  | TRUE
133 | bus_LV_121-26_0_5_node_149 | 0.4 | n |  | TRUE
134 | bus_LV_121-26_0_5_node_131 | 0.4 | n |  | TRUE
135 | bus_LV_121-26_0_5_node_116 | 0.4 | n |  | TRUE
136 | bus_LV_121-26_0_5_node_155 | 0.4 | n |  | TRUE
137 | bus_LV_121-26_0_5_node_153 | 0.4 | n |  | TRUE
138 | bus_LV_121-26_0_5_node_122 | 0.4 | n |  | TRUE
139 | bus_LV_121-26_0_5_node_139 | 0.4 | n |  | TRUE
140 | bus_LV_121-26_0_5_node_140 | 0.4 | n |  | TRUE
141 | bus_LV_121-26_0_5_node_123 | 0.4 | n |  | TRUE
142 | bus_LV_121-26_0_5_node_124 | 0.4 | n |  | TRUE
143 | bus_LV_121-26_0_5_node_125 | 0.4 | n |  | TRUE
144 | bus_LV_121-26_0_5_node_126 | 0.4 | n |  | TRUE
145 | bus_LV_121-26_0_5_node_127 | 0.4 | n |  | TRUE
146 | bus_LV_121-26_0_5_node_132 | 0.4 | n |  | TRUE
147 | bus_LV_121-26_0_5_node_128 | 0.4 | n |  | TRUE
148 | bus_LV_121-26_0_5_node_130 | 0.4 | n |  | TRUE
149 | bus_LV_121-26_0_5_node_156 | 0.4 | n |  | TRUE
150 | bus_LV_121-26_0_5_node_154 | 0.4 | n |  | TRUE
151 | bus_LV_121-26_0_5_node_145 | 0.4 | n |  | TRUE
152 | bus_MV_357_0_node_57 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_121-26_0_5_load_0 | 0 | 0.0020558 | 0.00051522 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_121-26_0_5_load_1 | 1 | 0.0028569 | 0.00071601 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_121-26_0_5_load_4 | 4 | 0.003225 | 0.00080826 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_121-26_0_5_load_5 | 5 | 0.0031956 | 0.00080089 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_121-26_0_5_load_22 | 6 | 0.0021836 | 0.00054727 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_121-26_0_5_load_42 | 8 | 0.0021078 | 0.00052825 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_121-26_0_5_load_44 | 9 | 0.0019507 | 0.0004889 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_121-26_0_5_load_141 | 10 | 0.001934 | 0.00048472 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_121-26_0_5_load_134 | 11 | 0.00064824 | 0.00016246 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_121-26_0_5_load_45 | 13 | 0.0028303 | 0.00070935 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_121-26_0_5_load_6 | 14 | 0.0011764 | 0.00029483 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_121-26_0_5_load_7 | 15 | 0.0019341 | 0.00048472 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_121-26_0_5_load_8 | 16 | 0.0010421 | 0.00026117 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_121-26_0_5_load_9 | 17 | 0.0021836 | 0.00054727 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_121-26_0_5_load_10 | 18 | 0.0056199 | 0.0014085 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_121-26_0_5_load_11 | 20 | 0.0028987 | 0.0007265 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_121-26_0_5_load_13 | 21 | 0.0028326 | 0.00070991 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_121-26_0_5_load_36 | 23 | 0.0021147 | 0.00052999 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_121-26_0_5_load_43 | 25 | 0.0083691 | 0.0020975 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_121-26_0_5_load_142 | 27 | 0.0011379 | 0.00028518 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_121-26_0_5_load_37 | 28 | 0.0031949 | 0.00080071 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_121-26_0_5_load_80 | 29 | 0.0014854 | 0.00037228 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_121-26_0_5_load_67 | 30 | 0.0039721 | 0.0009955 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_121-26_0_5_load_143 | 31 | 0.0031555 | 0.00079084 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_121-26_0_5_load_16 | 32 | 0.0014884 | 0.00037302 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_121-26_0_5_load_17 | 33 | 0.0040282 | 0.0010096 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_121-26_0_5_load_20 | 35 | 0.0032265 | 0.00080864 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_121-26_0_5_load_21 | 36 | 0.0014962 | 0.00037499 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_121-26_0_5_load_24 | 37 | 0.0023235 | 0.00058233 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_121-26_0_5_load_39 | 38 | 0.0029083 | 0.00072889 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_121-26_0_5_load_40 | 39 | 0.0022503 | 0.00056397 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_121-26_0_5_load_28 | 41 | 0.0039436 | 0.00098835 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_121-26_0_5_load_26 | 42 | 0.0029162 | 0.00073087 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_121-26_0_5_load_27 | 43 | 0.0045532 | 0.0011411 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_121-26_0_5_load_29 | 44 | 0.002114 | 0.00052982 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_121-26_0_5_load_83 | 45 | 0.0023411 | 0.00058674 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_121-26_0_5_load_102 | 46 | 0.0019214 | 0.00048154 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_121-26_0_5_load_30 | 47 | 0.0033125 | 0.00083018 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_121-26_0_5_load_31 | 48 | 0.001228 | 0.00030777 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_121-26_0_5_load_33 | 50 | 0.003811 | 0.00095513 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_121-26_0_5_load_77 | 52 | 0.0013365 | 0.00033497 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_121-26_0_5_load_72 | 54 | 0.0053787 | 0.001348 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_121-26_0_5_load_41 | 55 | 0.0028905 | 0.00072443 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_121-26_0_5_load_76 | 56 | 0.0010131 | 0.00025391 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_121-26_0_5_load_38 | 57 | 0.0020033 | 0.00050207 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_121-26_0_5_load_46 | 58 | 0.0031475 | 0.00078885 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_121-26_0_5_load_47 | 59 | 0.0010609 | 0.00026589 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_121-26_0_5_load_48 | 60 | 0.0011324 | 0.00028381 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_121-26_0_5_load_50 | 62 | 0.0010275 | 0.00025751 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_121-26_0_5_load_60 | 64 | 0.0023525 | 0.00058959 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_121-26_0_5_load_98 | 65 | 0.0031006 | 0.00077709 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_121-26_0_5_load_146 | 66 | 0.0028877 | 0.00072373 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_121-26_0_5_load_152 | 67 | 0.025777 | 0.0064604 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_121-26_0_5_load_58 | 68 | 0.0025183 | 0.00063115 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_121-26_0_5_load_97 | 69 | 0.001624 | 0.00040702 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_121-26_0_5_load_51 | 70 | 0.0031559 | 0.00079094 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_121-26_0_5_load_52 | 71 | 0.0036664 | 0.00091889 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_121-26_0_5_load_53 | 72 | 0.0023903 | 0.00059906 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_121-26_0_5_load_54 | 73 | 0.0022723 | 0.00056948 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_121-26_0_5_load_55 | 74 | 0.0055814 | 0.0013988 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_121-26_0_5_load_56 | 75 | 0.0014148 | 0.00035459 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_121-26_0_5_load_62 | 76 | 0.0022679 | 0.00056838 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_121-26_0_5_load_91 | 77 | 0.0011844 | 0.00029684 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_121-26_0_5_load_119 | 78 | 0.0010895 | 0.00027305 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_121-26_0_5_load_63 | 79 | 0.001501 | 0.00037619 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_121-26_0_5_load_92 | 80 | 0.0011813 | 0.00029607 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_121-26_0_5_load_118 | 81 | 0.0013632 | 0.00034166 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_121-26_0_5_load_57 | 82 | 0.0036985 | 0.00092692 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_121-26_0_5_load_59 | 83 | 0.0013235 | 0.00033171 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_121-26_0_5_load_61 | 84 | 0.0028197 | 0.00070667 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_121-26_0_5_load_81 | 85 | 0.0013727 | 0.00034403 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_121-26_0_5_load_82 | 86 | 0.0011163 | 0.00027977 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_121-26_0_5_load_64 | 87 | 0.0017568 | 0.00044031 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_121-26_0_5_load_96 | 88 | 0.0016681 | 0.00041806 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_121-26_0_5_load_144 | 89 | 0.0032306 | 0.00080965 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_121-26_0_5_load_66 | 90 | 0.0042104 | 0.0010552 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_121-26_0_5_load_70 | 92 | 0.0028057 | 0.00070319 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_121-26_0_5_load_99 | 93 | 0.0017894 | 0.00044847 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_121-26_0_5_load_71 | 94 | 0.0034649 | 0.00086839 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_121-26_0_5_load_100 | 95 | 0.0030984 | 0.00077653 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_121-26_0_5_load_137 | 96 | 0.0015437 | 0.00038689 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_121-26_0_5_load_101 | 97 | 0.0024495 | 0.00061391 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_121-26_0_5_load_73 | 98 | 0.0028733 | 0.0007201 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_121-26_0_5_load_74 | 99 | 0.0016427 | 0.0004117 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_121-26_0_5_load_75 | 100 | 0.0037173 | 0.00093165 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_121-26_0_5_load_93 | 101 | 0.0018062 | 0.00045267 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_121-26_0_5_load_94 | 102 | 0.0021605 | 0.00054147 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_121-26_0_5_load_78 | 103 | 0.0010748 | 0.00026937 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_121-26_0_5_load_79 | 104 | 0.0010794 | 0.00027053 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_121-26_0_5_load_136 | 105 | 0.0013006 | 0.00032596 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_121-26_0_5_load_104 | 106 | 0.00094317 | 0.00023638 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_121-26_0_5_load_105 | 107 | 0.000961 | 0.00024085 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_121-26_0_5_load_84 | 109 | 0.004162 | 0.0010431 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_121-26_0_5_load_85 | 110 | 0.0085595 | 0.0021452 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_121-26_0_5_load_86 | 111 | 0.0021375 | 0.00053571 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_121-26_0_5_load_87 | 112 | 0.0030927 | 0.0007751 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_121-26_0_5_load_89 | 114 | 0.0027469 | 0.00068845 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_121-26_0_5_load_120 | 115 | 0.00052425 | 0.00013139 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_121-26_0_5_load_90 | 116 | 0.0031196 | 0.00078184 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_121-26_0_5_load_148 | 117 | 0.0033857 | 0.00084854 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_121-26_0_5_load_147 | 118 | 0.0027051 | 0.00067795 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_121-26_0_5_load_106 | 119 | 0.0023239 | 0.00058243 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_121-26_0_5_load_107 | 120 | 0.0042877 | 0.0010746 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_121-26_0_5_load_95 | 121 | 0.004588 | 0.0011499 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_121-26_0_5_load_113 | 122 | 0.0012301 | 0.00030828 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_121-26_0_5_load_109 | 124 | 0.0019448 | 0.00048742 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_121-26_0_5_load_117 | 126 | 0.0018933 | 0.0004745 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_121-26_0_5_load_115 | 127 | 0.0010712 | 0.00026847 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_121-26_0_5_load_108 | 128 | 0.0017711 | 0.00044387 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_121-26_0_5_load_112 | 130 | 0.0010676 | 0.00026756 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_121-26_0_5_load_138 | 131 | 0.0024034 | 0.00060236 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_121-26_0_5_load_135 | 132 | 0.0011894 | 0.0002981 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_121-26_0_5_load_149 | 133 | 0.00089831 | 0.00022514 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_121-26_0_5_load_131 | 134 | 0.0022849 | 0.00057264 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_121-26_0_5_load_116 | 135 | 0.00051225 | 0.00012838 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_121-26_0_5_load_155 | 136 | 0.00070109 | 0.00017571 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_121-26_0_5_load_153 | 137 | 0.0010557 | 0.00026459 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_121-26_0_5_load_122 | 138 | 0.00029003 | 7.2689e-05 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_121-26_0_5_load_139 | 139 | 0.00027902 | 6.9928e-05 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_121-26_0_5_load_140 | 140 | 0.00027892 | 6.9905e-05 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_121-26_0_5_load_123 | 141 | 0.0031115 | 0.00077981 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_121-26_0_5_load_124 | 142 | 0.0014163 | 0.00035496 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_121-26_0_5_load_125 | 143 | 0.0029165 | 0.00073095 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_121-26_0_5_load_126 | 144 | 0.001371 | 0.00034361 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_121-26_0_5_load_127 | 145 | 0.0029932 | 0.00075016 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_121-26_0_5_load_132 | 146 | 0.0015314 | 0.0003838 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_121-26_0_5_load_128 | 147 | 0.002481 | 0.0006218 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_121-26_0_5_load_156 | 149 | 0.00045511 | 0.00011406 | 0 | 0 |  | 1 | TRUE | wye
128 | LV_121-26_0_5_load_154 | 150 | 0.0007634 | 0.00019133 | 0 | 0 |  | 1 | TRUE | wye
129 | LV_121-26_0_5_load_145 | 151 | 0.0030213 | 0.00075721 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 92 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_121-26_0_5_line_0 |  | 0 | 1 | 0.00063372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_121-26_0_5_line_1 |  | 0 | 2 | 0.017422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_121-26_0_5_line_2 |  | 1 | 3 | 0.020836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_121-26_0_5_line_3 |  | 2 | 4 | 0.0056489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_121-26_0_5_line_4 |  | 2 | 5 | 0.025245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_121-26_0_5_line_5 |  | 3 | 6 | 0.018425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_121-26_0_5_line_6 |  | 3 | 7 | 0.06848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_121-26_0_5_line_7 |  | 4 | 8 | 0.025313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_121-26_0_5_line_8 |  | 5 | 9 | 0.0083909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_121-26_0_5_line_9 |  | 6 | 10 | 0.0086528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_121-26_0_5_line_10 |  | 7 | 11 | 0.060589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_121-26_0_5_line_11 |  | 8 | 12 | 0.0083081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
12 | LV_121-26_0_5_line_12 |  | 9 | 13 | 0.00026227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_121-26_0_5_line_13 |  | 10 | 17 | 0.024358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_121-26_0_5_line_14 |  | 11 | 40 | 0.01481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_121-26_0_5_line_15 |  | 12 | 33 | 0.011739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_121-26_0_5_line_16 |  | 13 | 57 | 0.0098963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_121-26_0_5_line_17 |  | 14 | 15 | 0.023012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_121-26_0_5_line_18 |  | 14 | 16 | 0.0086528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_121-26_0_5_line_19 |  | 15 | 17 | 0.0086528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_121-26_0_5_line_20 |  | 18 | 19 | 0.011805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_121-26_0_5_line_21 |  | 19 | 22 | 0.0168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_121-26_0_5_line_22 |  | 20 | 21 | 0.010038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_121-26_0_5_line_23 |  | 21 | 23 | 0.00010584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_121-26_0_5_line_24 |  | 22 | 24 | 0.013965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_121-26_0_5_line_25 |  | 22 | 25 | 0.016088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_121-26_0_5_line_26 |  | 23 | 28 | 0.0085466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_121-26_0_5_line_27 |  | 24 | 26 | 0.002951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_121-26_0_5_line_28 |  | 24 | 27 | 0.018266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_121-26_0_5_line_29 |  | 26 | 29 | 0.014578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
30 | LV_121-26_0_5_line_30 |  | 26 | 30 | 0.018542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_121-26_0_5_line_31 |  | 27 | 31 | 0.00096563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_121-26_0_5_line_32 |  | 28 | 57 | 0.013247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_121-26_0_5_line_33 |  | 29 | 96 | 0.0089665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
34 | LV_121-26_0_5_line_34 |  | 30 | 90 | 0.024866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
35 | LV_121-26_0_5_line_35 |  | 32 | 33 | 0.012587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
36 | LV_121-26_0_5_line_36 |  | 32 | 34 | 0.015033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
37 | LV_121-26_0_5_line_37 |  | 34 | 35 | 0.010631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_121-26_0_5_line_38 |  | 34 | 36 | 0.022746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
39 | LV_121-26_0_5_line_39 |  | 35 | 37 | 0.0019339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_121-26_0_5_line_40 |  | 36 | 38 | 0.021638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
41 | LV_121-26_0_5_line_41 |  | 38 | 39 | 0.0087917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
42 | LV_121-26_0_5_line_42 |  | 39 | 55 | 0.0015485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
43 | LV_121-26_0_5_line_43 |  | 40 | 146 | 0.017435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_121-26_0_5_line_44 |  | 41 | 42 | 0.010631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_121-26_0_5_line_45 |  | 42 | 43 | 0.026154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_121-26_0_5_line_46 |  | 43 | 44 | 0.0034759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_121-26_0_5_line_47 |  | 44 | 45 | 0.02004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_121-26_0_5_line_48 |  | 45 | 46 | 0.009149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_121-26_0_5_line_49 |  | 46 | 108 | 0.012105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_121-26_0_5_line_50 |  | 47 | 48 | 0.027688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
51 | LV_121-26_0_5_line_51 |  | 47 | 49 | 0.0077578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
52 | LV_121-26_0_5_line_52 |  | 48 | 50 | 2.5656e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
53 | LV_121-26_0_5_line_53 |  | 49 | 51 | 0.013904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
54 | LV_121-26_0_5_line_54 |  | 50 | 52 | 0.0071123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
55 | LV_121-26_0_5_line_55 |  | 51 | 55 | 0.019076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
56 | LV_121-26_0_5_line_56 |  | 51 | 53 | 0.011362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_121-26_0_5_line_57 |  | 52 | 56 | 0.020029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
58 | LV_121-26_0_5_line_58 |  | 53 | 54 | 0.0031132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_121-26_0_5_line_59 |  | 56 | 103 | 0.0038643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
60 | LV_121-26_0_5_line_60 |  | 58 | 59 | 0.0016844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
61 | LV_121-26_0_5_line_61 |  | 58 | 60 | 0.0043108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
62 | LV_121-26_0_5_line_62 |  | 59 | 61 | 0.010418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
63 | LV_121-26_0_5_line_63 |  | 60 | 62 | 0.0055899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
64 | LV_121-26_0_5_line_64 |  | 61 | 63 | 0.01667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_121-26_0_5_line_65 |  | 61 | 64 | 0.014428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
66 | LV_121-26_0_5_line_66 |  | 62 | 65 | 0.0014082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
67 | LV_121-26_0_5_line_67 |  | 63 | 66 | 0.0087261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_121-26_0_5_line_68 |  | 63 | 67 | 0.0095062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_121-26_0_5_line_69 |  | 64 | 68 | 0.020406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
70 | LV_121-26_0_5_line_70 |  | 65 | 69 | 0.0062704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
71 | LV_121-26_0_5_line_71 |  | 66 | 89 | 0.016496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_121-26_0_5_line_72 |  | 68 | 82 | 0.0060726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
73 | LV_121-26_0_5_line_73 |  | 69 | 88 | 0.0017511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
74 | LV_121-26_0_5_line_74 |  | 70 | 71 | 0.0077718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
75 | LV_121-26_0_5_line_75 |  | 70 | 72 | 0.0016087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
76 | LV_121-26_0_5_line_76 |  | 71 | 73 | 0.0023305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
77 | LV_121-26_0_5_line_77 |  | 72 | 74 | 0.0069981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_121-26_0_5_line_78 |  | 72 | 75 | 0.014858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
79 | LV_121-26_0_5_line_79 |  | 73 | 76 | 0.0017737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
80 | LV_121-26_0_5_line_80 |  | 74 | 77 | 0.0054452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_121-26_0_5_line_81 |  | 75 | 78 | 0.00071125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
82 | LV_121-26_0_5_line_82 |  | 76 | 79 | 0.0052813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
83 | LV_121-26_0_5_line_83 |  | 77 | 80 | 0.0003763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_121-26_0_5_line_84 |  | 78 | 81 | 0.00027844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
85 | LV_121-26_0_5_line_85 |  | 79 | 87 | 0.0048158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
86 | LV_121-26_0_5_line_86 |  | 80 | 119 | 0.018788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_121-26_0_5_line_87 |  | 81 | 104 | 0.0025618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
88 | LV_121-26_0_5_line_88 |  | 82 | 83 | 0.0047071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
89 | LV_121-26_0_5_line_89 |  | 83 | 84 | 0.0017629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
90 | LV_121-26_0_5_line_90 |  | 84 | 85 | 0.002799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
91 | LV_121-26_0_5_line_91 |  | 85 | 86 | 0.011112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
92 | LV_121-26_0_5_line_92 |  | 86 | 106 | 0.00029096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
93 | LV_121-26_0_5_line_93 |  | 87 | 88 | 0.010361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
94 | LV_121-26_0_5_line_94 |  | 89 | 151 | 0.0009637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_121-26_0_5_line_95 |  | 90 | 91 | 0.018181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
96 | LV_121-26_0_5_line_96 |  | 91 | 92 | 0.025651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
97 | LV_121-26_0_5_line_97 |  | 92 | 93 | 0.017972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_121-26_0_5_line_98 |  | 94 | 95 | 0.0015605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_121-26_0_5_line_99 |  | 95 | 97 | 0.017879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_121-26_0_5_line_100 |  | 96 | 105 | 0.011643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
101 | LV_121-26_0_5_line_101 |  | 97 | 107 | 0.018529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
102 | LV_121-26_0_5_line_102 |  | 97 | 124 | 0.021051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
103 | LV_121-26_0_5_line_103 |  | 98 | 99 | 0.018562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_121-26_0_5_line_104 |  | 99 | 100 | 0.00089988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_121-26_0_5_line_105 |  | 100 | 101 | 0.0056466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_121-26_0_5_line_106 |  | 101 | 102 | 0.0026005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_121-26_0_5_line_107 |  | 102 | 121 | 0.00077456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_121-26_0_5_line_108 |  | 103 | 104 | 0.0011612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
109 | LV_121-26_0_5_line_109 |  | 105 | 132 | 0.0083239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
110 | LV_121-26_0_5_line_110 |  | 106 | 107 | 0.00027195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
111 | LV_121-26_0_5_line_111 |  | 108 | 126 | 0.0092999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_121-26_0_5_line_112 |  | 108 | 127 | 0.014847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_121-26_0_5_line_113 |  | 109 | 110 | 0.024059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_121-26_0_5_line_114 |  | 109 | 111 | 0.014814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_121-26_0_5_line_115 |  | 110 | 112 | 0.0010926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_121-26_0_5_line_116 |  | 111 | 113 | 0.05529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_121-26_0_5_line_117 |  | 112 | 114 | 0.0014517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_121-26_0_5_line_118 |  | 113 | 115 | 0.041668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_121-26_0_5_line_119 |  | 114 | 116 | 0.00032873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_121-26_0_5_line_120 |  | 116 | 117 | 0.00062639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_121-26_0_5_line_121 |  | 117 | 118 | 0.014566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_121-26_0_5_line_122 |  | 118 | 151 | 0.00088561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_121-26_0_5_line_123 |  | 119 | 120 | 0.013236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_121-26_0_5_line_124 |  | 120 | 128 | 0.0013286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_121-26_0_5_line_125 |  | 121 | 122 | 0.0091901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_121-26_0_5_line_126 |  | 122 | 123 | 0.0092271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_121-26_0_5_line_127 |  | 123 | 135 | 0.044803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_121-26_0_5_line_128 |  | 123 | 127 | 0.0033496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_121-26_0_5_line_129 |  | 124 | 125 | 0.0072271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
130 | LV_121-26_0_5_line_130 |  | 125 | 129 | 0.027586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
131 | LV_121-26_0_5_line_131 |  | 125 | 130 | 0.013777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_121-26_0_5_line_132 |  | 126 | 128 | 0.00085738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_121-26_0_5_line_133 |  | 129 | 131 | 0.042711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_121-26_0_5_line_134 |  | 129 | 132 | 0.015853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
135 | LV_121-26_0_5_line_135 |  | 130 | 133 | 0.00080225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_121-26_0_5_line_136 |  | 131 | 134 | 0.0019539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_121-26_0_5_line_137 |  | 134 | 148 | 0.023055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_121-26_0_5_line_138 |  | 135 | 136 | 0.0053205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_121-26_0_5_line_139 |  | 136 | 137 | 0.018847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_121-26_0_5_line_140 |  | 137 | 150 | 0.0068159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_121-26_0_5_line_141 |  | 138 | 139 | 0.017921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_121-26_0_5_line_142 |  | 139 | 140 | 0.0097815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_121-26_0_5_line_143 |  | 140 | 149 | 0.0089267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_121-26_0_5_line_144 |  | 141 | 142 | 0.0021624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_121-26_0_5_line_145 |  | 141 | 143 | 0.018469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_121-26_0_5_line_146 |  | 142 | 144 | 0.016175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_121-26_0_5_line_147 |  | 143 | 145 | 0.0078736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_121-26_0_5_line_148 |  | 144 | 146 | 0.00055041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_121-26_0_5_line_149 |  | 147 | 148 | 0.0054723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_121-26_0_5_line_150 |  | 149 | 150 | 0.0099679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_121-26_0_5_trafo_70 | 0.63 MVA 20/0.4 kV | 152 | 92 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2701657.0228 | 1243287.9804 | 2701656.4826 | 1243287.6492
1 | 2701671.875 | 1243297.0865 | 2701657.0228 | 1243287.9804
2 | 2701638.7193 | 1243276.7583 | 2701656.4826 | 1243287.6492
3 | 2701671.875 | 1243297.0865 | 2701676.8521 | 1243299.7583
4 | 2701671.875 | 1243297.0865 | 2701687.5359 | 1243277.2866
5 | 2701638.7193 | 1243276.7583 | 2701650.2999 | 1243262.4274
6 | 2701625.3539 | 1243231.3277 | 2701606.9091 | 1243254.6632 | 2701614.3002 | 1243260.0828 | 2701638.7193 | 1243276.7583
7 | 2701699.1542 | 1243311.7308 | 2701676.8521 | 1243299.7583
8 | 2701692.7413 | 1243270.7055 | 2701687.5359 | 1243277.2866
9 | 2701650.2999 | 1243262.4274 | 2701655.7383 | 1243255.6974
10 | 2701625.3539 | 1243231.3277 | 2701662.9217 | 1243183.7909
11 | 2701706.4743 | 1243315.6604 | 2701699.1542 | 1243311.7308
12 | 2701692.7413 | 1243270.7055 | 2701692.904 | 1243270.4998
13 | 2701655.7383 | 1243255.6974 | 2701671.048 | 1243236.7517
14 | 2701672.1043 | 1243172.1716 | 2701662.9217 | 1243183.7909
15 | 2701706.4743 | 1243315.6604 | 2701717.1152 | 1243320.6182
16 | 2701699.0433 | 1243262.738 | 2701692.904 | 1243270.4998
17 | 2701690.9498 | 1243212.1232 | 2701676.4864 | 1243230.0216
18 | 2701690.9498 | 1243212.1232 | 2701696.3883 | 1243205.3931
19 | 2701671.048 | 1243236.7517 | 2701676.4864 | 1243230.0216
20 | 2701748.3534 | 1243216.5906 | 2701740.6364 | 1243225.5241
21 | 2701745.5711 | 1243203.8331 | 2701743.6192 | 1243206.1236 | 2701742.5857 | 1243208.1964 | 2701742.2525 | 1243210.4368 | 2701742.7694 | 1243212.4695 | 2701744.2177 | 1243214.418 | 2701746.3553 | 1243215.8447 | 2701748.3534 | 1243216.5906
22 | 2701718.8557 | 1243237.6894 | 2701712.6286 | 1243245.5623
23 | 2701712.5629 | 1243245.6454 | 2701712.6286 | 1243245.5623
24 | 2701754.7705 | 1243193.3049 | 2701745.5711 | 1243203.8331
25 | 2701745.5711 | 1243203.8331 | 2701733.2828 | 1243193.4486
26 | 2701707.2609 | 1243252.3486 | 2701712.5629 | 1243245.6454
27 | 2701756.6616 | 1243191.0356 | 2701754.7705 | 1243193.3049
28 | 2701754.7705 | 1243193.3049 | 2701740.6782 | 1243181.6836
29 | 2701756.6616 | 1243191.0356 | 2701765.7788 | 1243179.6605
30 | 2701756.6616 | 1243191.0356 | 2701765.9968 | 1243199.024 | 2701770.7333 | 1243203.1105
31 | 2701740.6782 | 1243181.6836 | 2701739.9332 | 1243181.0692
32 | 2701699.0433 | 1243262.738 | 2701707.2609 | 1243252.3486
33 | 2701771.3867 | 1243172.664 | 2701765.7788 | 1243179.6605
34 | 2701789.5607 | 1243219.3542 | 2701770.7333 | 1243203.1105
35 | 2701717.1152 | 1243320.6182 | 2701728.5249 | 1243325.9342
36 | 2701742.6446 | 1243329.8914 | 2701739.3805 | 1243330.2357 | 2701736.8777 | 1243329.8259 | 2701728.5249 | 1243325.9342
37 | 2701742.6446 | 1243329.8914 | 2701745.6653 | 1243340.0844
38 | 2701742.6446 | 1243329.8914 | 2701744.8229 | 1243328.9392 | 2701747.0198 | 1243326.9086 | 2701757.7356 | 1243313.2296
39 | 2701746.2148 | 1243341.9386 | 2701745.6653 | 1243340.0844
40 | 2701757.7356 | 1243313.2296 | 2701771.0795 | 1243296.1956
41 | 2701776.5011 | 1243289.2747 | 2701771.0795 | 1243296.1956
42 | 2701776.5011 | 1243289.2747 | 2701777.4561 | 1243288.0557
43 | 2701672.1043 | 1243172.1716 | 2701675.0738 | 1243172.2559 | 2701677.9445 | 1243171.4934 | 2701680.5571 | 1243169.4699 | 2701685.7081 | 1243163.1035
44 | 2701782.5539 | 1243341.9183 | 2701790.5482 | 1243337.4521 | 2701791.7329 | 1243336.5756
45 | 2701814.5217 | 1243324.5987 | 2701807.947 | 1243326.1975 | 2701803.4883 | 1243327.8778 | 2701791.7329 | 1243336.5756
46 | 2701814.5217 | 1243324.5987 | 2701817.8992 | 1243323.7775
47 | 2701837.625 | 1243327.2761 | 2701830.1578 | 1243325.7115 | 2701817.8992 | 1243323.7775 | 2701817.8992 | 1243323.7775
48 | 2701846.5796 | 1243329.1523 | 2701837.625 | 1243327.2761
49 | 2701858.4271 | 1243331.6346 | 2701846.5796 | 1243329.1523
50 | 2701832.0976 | 1243269.0719 | 2701820.3135 | 1243267.2641 | 2701804.7286 | 1243264.8837
51 | 2701797.0859 | 1243263.5516 | 2701804.7286 | 1243264.8837 | 2701804.7286 | 1243264.8837
52 | 2701832.1229 | 1243269.0758 | 2701832.0976 | 1243269.0719
53 | 2701797.0859 | 1243263.5516 | 2701795.6185 | 1243265.3611 | 2701785.7101 | 1243271.3959
54 | 2701839.1448 | 1243270.2062 | 2701833.8625 | 1243269.3426 | 2701832.1229 | 1243269.0758
55 | 2701785.7101 | 1243271.3959 | 2701783.9022 | 1243279.8269 | 2701777.4561 | 1243288.0557
56 | 2701785.7101 | 1243271.3959 | 2701781.427 | 1243263.2828 | 2701781.0103 | 1243261.1295
57 | 2701839.1448 | 1243270.2062 | 2701857.194 | 1243273.1571 | 2701858.864 | 1243273.6462
58 | 2701781.0103 | 1243261.1295 | 2701781.094 | 1243258.0174
59 | 2701862.5725 | 1243274.7323 | 2701858.864 | 1243273.6462
60 | 2701900.157 | 1243228.77 | 2701899.8671 | 1243229.2335 | 2701899.3363 | 1243230.2398
61 | 2701897.3253 | 1243234.0527 | 2701899.3363 | 1243230.2398
62 | 2701905.6815 | 1243219.9373 | 2701900.157 | 1243228.77
63 | 2701897.3253 | 1243234.0527 | 2701894.7174 | 1243238.9971 | 2701894.7174 | 1243238.9971
64 | 2701905.6815 | 1243219.9373 | 2701911.8669 | 1243211.0477 | 2701914.6766 | 1243205.9143
65 | 2701905.6815 | 1243219.9373 | 2701892.9377 | 1243213.1719
66 | 2701894.7174 | 1243238.9971 | 2701894.1862 | 1243240.3013
67 | 2701914.6766 | 1243205.9143 | 2701920.226 | 1243209.4011 | 2701922.0659 | 1243210.5559
68 | 2701914.6766 | 1243205.9143 | 2701915.8856 | 1243201.9875 | 2701916.5662 | 1243198.8968 | 2701916.828 | 1243196.6795
69 | 2701892.9377 | 1243213.1719 | 2701874.9143 | 1243203.6036
70 | 2701891.8208 | 1243246.1084 | 2701894.1862 | 1243240.3013
71 | 2701922.0659 | 1243210.5559 | 2701929.3232 | 1243218.0307 | 2701933.5567 | 1243222.3909
72 | 2701869.5506 | 1243200.7562 | 2701874.9143 | 1243203.6036
73 | 2701891.303 | 1243247.7812 | 2701891.8208 | 1243246.1084 | 2701891.8208 | 1243246.1084
74 | 2701881.8141 | 1243278.6914 | 2701883.969 | 1243271.471 | 2701884.039 | 1243271.2449
75 | 2701881.354 | 1243280.2329 | 2701881.8141 | 1243278.6914
76 | 2701884.7282 | 1243269.0187 | 2701884.039 | 1243271.2449
77 | 2701881.354 | 1243280.2329 | 2701878.5361 | 1243286.6386
78 | 2701881.354 | 1243280.2329 | 2701867.0952 | 1243276.0569
79 | 2701885.2527 | 1243267.3243 | 2701884.7282 | 1243269.0187
80 | 2701876.3435 | 1243291.6228 | 2701878.5361 | 1243286.6386
81 | 2701867.0952 | 1243276.0569 | 2701866.4126 | 1243275.857
82 | 2701885.2527 | 1243267.3243 | 2701886.8146 | 1243262.2793
83 | 2701876.192 | 1243291.9673 | 2701876.3435 | 1243291.6228
84 | 2701866.4126 | 1243275.857 | 2701866.1454 | 1243275.7787
85 | 2701888.2388 | 1243257.6789 | 2701886.8146 | 1243262.2793
86 | 2701876.192 | 1243291.9673 | 2701874.3289 | 1243296.2024 | 2701867.9592 | 1243308.8503
87 | 2701866.1454 | 1243275.7787 | 2701863.6868 | 1243275.0587
88 | 2701865.3931 | 1243198.549 | 2701869.5506 | 1243200.7562
89 | 2701865.3931 | 1243198.549 | 2701863.836 | 1243197.7224
90 | 2701863.836 | 1243197.7224 | 2701861.3637 | 1243196.4099
91 | 2701851.5925 | 1243191.119 | 2701854.7475 | 1243192.8975 | 2701861.3637 | 1243196.4099
92 | 2701851.5925 | 1243191.119 | 2701851.3391 | 1243190.9761
93 | 2701891.303 | 1243247.7812 | 2701888.2388 | 1243257.6789
94 | 2701933.5567 | 1243222.3909 | 2701934.228 | 1243223.0823
95 | 2701801.7182 | 1243232.3959 | 2701800.0554 | 1243228.4087 | 2701789.5607 | 1243219.3542
96 | 2701801.7182 | 1243232.3959 | 2701803.4991 | 1243237.864 | 2701804.8306 | 1243240.8891 | 2701806.9078 | 1243243.6269 | 2701811.7276 | 1243245.5778 | 2701819.5544 | 1243247.0193
97 | 2701837.2289 | 1243250.2745 | 2701819.5544 | 1243247.0193
98 | 2701826.3621 | 1243195.8111 | 2701827.1884 | 1243194.4874
99 | 2701836.6558 | 1243179.3209 | 2701827.1884 | 1243194.4874
100 | 2701778.6682 | 1243163.5794 | 2701771.3867 | 1243172.664
101 | 2701836.6558 | 1243179.3209 | 2701841.7888 | 1243184.1683 | 2701846.1308 | 1243187.5343 | 2701850.068 | 1243190.2596 | 2701851.1022 | 1243190.8426
102 | 2701836.6558 | 1243179.3209 | 2701833.1446 | 1243176.0026 | 2701823.6971 | 1243168.3901 | 2701820.5903 | 1243165.7348
103 | 2701878.4417 | 1243391.2472 | 2701876.701 | 1243379.452 | 2701875.0496 | 1243373.0218
104 | 2701875.0496 | 1243373.0218 | 2701874.8257 | 1243372.1502
105 | 2701873.4211 | 1243366.6811 | 2701874.8257 | 1243372.1502
106 | 2701873.4211 | 1243366.6811 | 2701872.7742 | 1243364.1623
107 | 2701872.7742 | 1243364.1623 | 2701872.5816 | 1243363.4121
108 | 2701862.5725 | 1243274.7323 | 2701863.6868 | 1243275.0587
109 | 2701783.8741 | 1243157.0843 | 2701778.6682 | 1243163.5794
110 | 2701851.3391 | 1243190.9761 | 2701851.1022 | 1243190.8426
111 | 2701858.4271 | 1243331.6346 | 2701861.7755 | 1243322.9583
112 | 2701858.4271 | 1243331.6346 | 2701857.69 | 1243335.3804 | 2701858.7844 | 1243341.2037 | 2701861.8821 | 1243345.26
113 | 2701965.6506 | 1243252.3969 | 2701959.4822 | 1243247.2937 | 2701951.4091 | 1243240.2273 | 2701947.5733 | 1243236.5346
114 | 2701977.8466 | 1243260.772 | 2701973.7013 | 1243258.3243 | 2701969.557 | 1243255.3397 | 2701966.757 | 1243253.3122 | 2701965.6506 | 1243252.3969
115 | 2701946.7862 | 1243235.7768 | 2701947.5733 | 1243236.5346
116 | 2702031.1134 | 1243272.5889 | 2702025.4614 | 1243272.436 | 2702010.7925 | 1243271.3052 | 2702006.3413 | 1243270.7838 | 2702003.414 | 1243270.4444 | 2701996.8245 | 1243268.9744 | 2701990.946 | 1243267.0497 | 2701986.7782 | 1243265.4323 | 2701981.9931 | 1243263.2262 | 2701980.8781 | 1243262.5621 | 2701977.8466 | 1243260.772
117 | 2701945.7403 | 1243234.77 | 2701946.7862 | 1243235.7768
118 | 2702031.1134 | 1243272.5889 | 2702027.8445 | 1243297.3741 | 2702026.7049 | 1243314.0028
119 | 2701945.5035 | 1243234.542 | 2701945.7403 | 1243234.77
120 | 2701945.0523 | 1243234.1076 | 2701945.5035 | 1243234.542
121 | 2701945.0523 | 1243234.1076 | 2701943.1767 | 1243232.302 | 2701941.8843 | 1243230.9676 | 2701934.845 | 1243223.7177
122 | 2701934.228 | 1243223.0823 | 2701934.845 | 1243223.7177
123 | 2701867.9592 | 1243308.8503 | 2701864.7961 | 1243315.1312 | 2701862.5625 | 1243320.919
124 | 2701862.0842 | 1243322.1585 | 2701862.5625 | 1243320.919
125 | 2701872.5816 | 1243363.4121 | 2701871.3656 | 1243358.6776 | 2701869.7655 | 1243354.6843
126 | 2701864.771 | 1243346.9554 | 2701869.3288 | 1243353.5943 | 2701869.7655 | 1243354.6843
127 | 2701864.771 | 1243346.9554 | 2701874.9055 | 1243349.3201 | 2701897.0023 | 1243355.9045 | 2701907.5637 | 1243360.0316
128 | 2701864.771 | 1243346.9554 | 2701861.8821 | 1243345.26
129 | 2701816.7636 | 1243159.6533 | 2701818.4293 | 1243163.0289 | 2701820.5903 | 1243165.7348
130 | 2701816.7636 | 1243159.6533 | 2701813.0621 | 1243158.6112 | 2701809.4301 | 1243156.6029 | 2701793.7889 | 1243144.7143
131 | 2701816.7636 | 1243159.6533 | 2701819.919 | 1243159.0403 | 2701822.1487 | 1243157.7442 | 2701825.8357 | 1243154.3493 | 2701827.7432 | 1243152.0702
132 | 2701861.7755 | 1243322.9583 | 2701862.0842 | 1243322.1585
133 | 2701793.7889 | 1243144.7143 | 2701759.8226 | 1243118.8206
134 | 2701793.7889 | 1243144.7143 | 2701783.8741 | 1243157.0843
135 | 2701827.7432 | 1243152.0702 | 2701828.2581 | 1243151.455
136 | 2701758.2687 | 1243117.636 | 2701759.8226 | 1243118.8206
137 | 2701739.9342 | 1243103.659 | 2701758.2687 | 1243117.636
138 | 2701912.5193 | 1243361.9681 | 2701907.5637 | 1243360.0316
139 | 2701929.7728 | 1243369.4274 | 2701926.6783 | 1243367.5009 | 2701912.5193 | 1243361.9681
140 | 2701929.7728 | 1243369.4274 | 2701935.559 | 1243373.0296
141 | 2701960.6687 | 1243386.8624 | 2701976.1381 | 1243395.9095
142 | 2701952.0903 | 1243382.1654 | 2701958.4428 | 1243385.5606 | 2701960.6687 | 1243386.8624
143 | 2701944.2176 | 1243377.9576 | 2701952.0903 | 1243382.1654
144 | 2701697.9195 | 1243151.4484 | 2701696.228 | 1243150.1013
145 | 2701697.9195 | 1243151.4484 | 2701712.3669 | 1243162.9545
146 | 2701696.228 | 1243150.1013 | 2701696.228 | 1243150.1013 | 2701686.0543 | 1243162.6756
147 | 2701707.2894 | 1243168.9721 | 2701712.3669 | 1243162.9545
148 | 2701686.0543 | 1243162.6756 | 2701685.7081 | 1243163.1035
149 | 2701739.9342 | 1243103.659 | 2701735.5823 | 1243100.3414
150 | 2701935.559 | 1243373.0296 | 2701938.967 | 1243375.1513 | 2701944.2176 | 1243377.9576

## bus_geodata
| x | y | coords
0 | 2701657.0228 | 1243287.9804
1 | 2701656.4826 | 1243287.6492
2 | 2701671.875 | 1243297.0865
3 | 2701638.7193 | 1243276.7583
4 | 2701676.8521 | 1243299.7583
5 | 2701687.5359 | 1243277.2866
6 | 2701650.2999 | 1243262.4274
7 | 2701625.3539 | 1243231.3277
8 | 2701699.1542 | 1243311.7308
9 | 2701692.7413 | 1243270.7055
10 | 2701655.7383 | 1243255.6974
11 | 2701662.9217 | 1243183.7909
12 | 2701706.4743 | 1243315.6604
13 | 2701692.904 | 1243270.4998
14 | 2701690.9498 | 1243212.1232
15 | 2701676.4864 | 1243230.0216
16 | 2701696.3883 | 1243205.3931
17 | 2701671.048 | 1243236.7517
18 | 2701740.6364 | 1243225.5241
19 | 2701748.3534 | 1243216.5906
20 | 2701718.8557 | 1243237.6894
21 | 2701712.6286 | 1243245.5623
22 | 2701745.5711 | 1243203.8331
23 | 2701712.5629 | 1243245.6454
24 | 2701754.7705 | 1243193.3049
25 | 2701733.2828 | 1243193.4486
26 | 2701756.6616 | 1243191.0356
27 | 2701740.6782 | 1243181.6836
28 | 2701707.2609 | 1243252.3486
29 | 2701765.7789 | 1243179.6605
30 | 2701770.7333 | 1243203.1105
31 | 2701739.9332 | 1243181.0692
32 | 2701728.5249 | 1243325.9342
33 | 2701717.1152 | 1243320.6182
34 | 2701742.6446 | 1243329.8914
35 | 2701745.6653 | 1243340.0844
36 | 2701757.7356 | 1243313.2296
37 | 2701746.2148 | 1243341.9386
38 | 2701771.0795 | 1243296.1956
39 | 2701776.5011 | 1243289.2747
40 | 2701672.1043 | 1243172.1716
41 | 2701782.5539 | 1243341.9183
42 | 2701791.7329 | 1243336.5756
43 | 2701814.5217 | 1243324.5987
44 | 2701817.8992 | 1243323.7775
45 | 2701837.625 | 1243327.2761
46 | 2701846.5796 | 1243329.1523
47 | 2701804.7286 | 1243264.8837
48 | 2701832.0976 | 1243269.0719
49 | 2701797.0859 | 1243263.5516
50 | 2701832.1229 | 1243269.0758
51 | 2701785.7101 | 1243271.3959
52 | 2701839.1448 | 1243270.2062
53 | 2701781.0103 | 1243261.1295
54 | 2701781.094 | 1243258.0174
55 | 2701777.4561 | 1243288.0557
56 | 2701858.864 | 1243273.6462
57 | 2701699.0433 | 1243262.738
58 | 2701899.3363 | 1243230.2398
59 | 2701900.157 | 1243228.77
60 | 2701897.3253 | 1243234.0527
61 | 2701905.6815 | 1243219.9373
62 | 2701894.7174 | 1243238.9971
63 | 2701914.6766 | 1243205.9143
64 | 2701892.9377 | 1243213.1719
65 | 2701894.1862 | 1243240.3013
66 | 2701922.0659 | 1243210.5559
67 | 2701916.828 | 1243196.6795
68 | 2701874.9143 | 1243203.6036
69 | 2701891.8208 | 1243246.1084
70 | 2701881.8141 | 1243278.6914
71 | 2701884.039 | 1243271.2449
72 | 2701881.354 | 1243280.2329
73 | 2701884.7282 | 1243269.0187
74 | 2701878.5361 | 1243286.6386
75 | 2701867.0952 | 1243276.0569
76 | 2701885.2527 | 1243267.3243
77 | 2701876.3435 | 1243291.6228
78 | 2701866.4126 | 1243275.857
79 | 2701886.8146 | 1243262.2793
80 | 2701876.192 | 1243291.9673
81 | 2701866.1454 | 1243275.7787
82 | 2701869.5506 | 1243200.7562
83 | 2701865.3931 | 1243198.549
84 | 2701863.836 | 1243197.7224
85 | 2701861.3637 | 1243196.4099
86 | 2701851.5925 | 1243191.119
87 | 2701888.2388 | 1243257.6789
88 | 2701891.303 | 1243247.7812
89 | 2701933.5567 | 1243222.3909
90 | 2701789.5607 | 1243219.3542
91 | 2701801.7182 | 1243232.3959
92 | 2701819.5544 | 1243247.0193
93 | 2701837.2289 | 1243250.2745
94 | 2701826.3621 | 1243195.8111
95 | 2701827.1884 | 1243194.4874
96 | 2701771.3867 | 1243172.664
97 | 2701836.6558 | 1243179.3209
98 | 2701878.4417 | 1243391.2472
99 | 2701875.0496 | 1243373.0218
100 | 2701874.8257 | 1243372.1502
101 | 2701873.4211 | 1243366.6811
102 | 2701872.7742 | 1243364.1623
103 | 2701862.5725 | 1243274.7323
104 | 2701863.6868 | 1243275.0587
105 | 2701778.6682 | 1243163.5794
106 | 2701851.3391 | 1243190.9761
107 | 2701851.1022 | 1243190.8426
108 | 2701858.4272 | 1243331.6346
109 | 2701965.6506 | 1243252.3969
110 | 2701947.5733 | 1243236.5346
111 | 2701977.8466 | 1243260.772
112 | 2701946.7862 | 1243235.7768
113 | 2702031.1134 | 1243272.5889
114 | 2701945.7403 | 1243234.77
115 | 2702026.7049 | 1243314.0028
116 | 2701945.5035 | 1243234.542
117 | 2701945.0523 | 1243234.1076
118 | 2701934.845 | 1243223.7177
119 | 2701867.9592 | 1243308.8503
120 | 2701862.5625 | 1243320.919
121 | 2701872.5816 | 1243363.4121
122 | 2701869.7655 | 1243354.6843
123 | 2701864.771 | 1243346.9554
124 | 2701820.5903 | 1243165.7348
125 | 2701816.7636 | 1243159.6533
126 | 2701861.7755 | 1243322.9583
127 | 2701861.8821 | 1243345.26
128 | 2701862.0842 | 1243322.1585
129 | 2701793.7889 | 1243144.7143
130 | 2701827.7432 | 1243152.0702
131 | 2701759.8226 | 1243118.8206
132 | 2701783.8741 | 1243157.0843
133 | 2701828.2581 | 1243151.455
134 | 2701758.2687 | 1243117.636
135 | 2701907.5637 | 1243360.0316
136 | 2701912.5193 | 1243361.9681
137 | 2701929.7728 | 1243369.4274
138 | 2701976.1381 | 1243395.9095
139 | 2701960.6687 | 1243386.8624
140 | 2701952.0903 | 1243382.1654
141 | 2701697.9195 | 1243151.4484
142 | 2701696.228 | 1243150.1013
143 | 2701712.3669 | 1243162.9545
144 | 2701686.0543 | 1243162.6756
145 | 2701707.2894 | 1243168.9721
146 | 2701685.7081 | 1243163.1035
147 | 2701735.5823 | 1243100.3414
148 | 2701739.9342 | 1243103.659
149 | 2701944.2176 | 1243377.9576
150 | 2701935.559 | 1243373.0296
151 | 2701934.228 | 1243223.0823
152 | 2701837.2289 | 1243250.2745

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97321 | -0.51638 | 0.0020558 | 0.00051522
1 | 0.9732 | -0.5167 | 0.0028569 | 0.00071601
2 | 0.97369 | -0.50697 | 0 | 0
3 | 0.97272 | -0.52608 | 0 | 0
4 | 0.97395 | -0.50174 | 0.003225 | 0.00080826
5 | 0.97319 | -0.51673 | 0.0031956 | 0.00080089
6 | 0.97254 | -0.52963 | 0.0021836 | 0.00054727
7 | 0.97183 | -0.54375 | 0 | 0
8 | 0.97438 | -0.49343 | 0.0021078 | 0.00052825
9 | 0.97306 | -0.51949 | 0.0019507 | 0.0004889
10 | 0.97247 | -0.53095 | 0.001934 | 0.00048472
11 | 0.97103 | -0.55941 | 0.00064824 | 0.00016246
12 | 0.97448 | -0.49131 | 0 | 0
13 | 0.97305 | -0.51956 | 0.0028303 | 0.00070935
14 | 0.97225 | -0.5354 | 0.0011764 | 0.00029483
15 | 0.9723 | -0.53446 | 0.0019341 | 0.00048472
16 | 0.97224 | -0.53556 | 0.0010421 | 0.00026117
17 | 0.97233 | -0.53379 | 0.0021836 | 0.00054727
18 | 0.99317 | -0.12942 | 0.0056199 | 0.0014085
19 | 0.99323 | -0.12825 | 0 | 0
20 | 0.9727 | -0.52642 | 0.0028987 | 0.0007265
21 | 0.97273 | -0.52588 | 0.0028326 | 0.00070991
22 | 0.99331 | -0.12658 | 0 | 0
23 | 0.97273 | -0.52587 | 0.0021147 | 0.00052999
24 | 0.99349 | -0.12313 | 0 | 0
25 | 0.99319 | -0.12896 | 0.0083691 | 0.0020975
26 | 0.99354 | -0.12218 | 0 | 0
27 | 0.99342 | -0.12452 | 0.0011379 | 0.00028518
28 | 0.97279 | -0.52463 | 0.0031949 | 0.00080071
29 | 0.99254 | -0.14123 | 0.0014854 | 0.00037228
30 | 0.99489 | -0.096506 | 0.0039721 | 0.0009955
31 | 0.99342 | -0.12457 | 0.0031555 | 0.00079084
32 | 0.97481 | -0.48486 | 0.0014884 | 0.00037302
33 | 0.97464 | -0.48831 | 0.0040282 | 0.0010096
34 | 0.97503 | -0.48064 | 0 | 0
35 | 0.97497 | -0.48172 | 0.0032265 | 0.00080864
36 | 0.97538 | -0.47367 | 0.0014962 | 0.00037499
37 | 0.97497 | -0.4818 | 0.0023235 | 0.00058233
38 | 0.97572 | -0.46691 | 0.0029083 | 0.00072889
39 | 0.97587 | -0.46404 | 0.0022503 | 0.00056397
40 | 0.97085 | -0.56306 | 0 | 0
41 | 0.97484 | -0.4844 | 0.0039436 | 0.00098835
42 | 0.97488 | -0.48363 | 0.0029162 | 0.00073087
43 | 0.97505 | -0.48034 | 0.0045532 | 0.0011411
44 | 0.97508 | -0.47961 | 0.002114 | 0.00052982
45 | 0.97534 | -0.47465 | 0.0023411 | 0.00058674
46 | 0.97547 | -0.47199 | 0.0019214 | 0.00048154
47 | 0.97665 | -0.44877 | 0.0033125 | 0.00083018
48 | 0.9772 | -0.43802 | 0.001228 | 0.00030777
49 | 0.9765 | -0.45167 | 0 | 0
50 | 0.9772 | -0.43801 | 0.003811 | 0.00095513
51 | 0.97624 | -0.45686 | 0 | 0
52 | 0.97735 | -0.43509 | 0.0013365 | 0.00033497
53 | 0.97618 | -0.45798 | 0 | 0
54 | 0.97616 | -0.45829 | 0.0053787 | 0.001348
55 | 0.9759 | -0.46352 | 0.0028905 | 0.00072443
56 | 0.97777 | -0.42674 | 0.0010131 | 0.00025391
57 | 0.97293 | -0.52194 | 0.0020033 | 0.00050207
58 | 0.98045 | -0.37433 | 0.0031475 | 0.00078885
59 | 0.98053 | -0.3729 | 0.0010609 | 0.00026589
60 | 0.98027 | -0.37791 | 0.0011324 | 0.00028381
61 | 0.98098 | -0.36404 | 0 | 0
62 | 0.98003 | -0.38254 | 0.0010275 | 0.00025751
63 | 0.97997 | -0.3838 | 0 | 0
64 | 0.98183 | -0.34753 | 0.0023525 | 0.00058959
65 | 0.97997 | -0.38369 | 0.0031006 | 0.00077709
66 | 0.97965 | -0.39007 | 0.0028877 | 0.00072373
67 | 0.97975 | -0.38824 | 0.025777 | 0.0064604
68 | 0.98304 | -0.324 | 0.0025183 | 0.00063115
69 | 0.97971 | -0.38877 | 0.001624 | 0.00040702
70 | 0.97836 | -0.41524 | 0.0031559 | 0.00079094
71 | 0.97866 | -0.40945 | 0.0036664 | 0.00091889
72 | 0.9783 | -0.41641 | 0.0023903 | 0.00059906
73 | 0.97875 | -0.40768 | 0.0022723 | 0.00056948
74 | 0.97791 | -0.42399 | 0.0055814 | 0.0013988
75 | 0.97796 | -0.42307 | 0.0014148 | 0.00035459
76 | 0.97882 | -0.40632 | 0.0022679 | 0.00056838
77 | 0.97764 | -0.42934 | 0.0011844 | 0.00029684
78 | 0.97794 | -0.42339 | 0.0010895 | 0.00027305
79 | 0.97903 | -0.40219 | 0.001501 | 0.00037619
80 | 0.97762 | -0.4297 | 0.0011813 | 0.00029607
81 | 0.97794 | -0.42351 | 0.0013632 | 0.00034166
82 | 0.9834 | -0.31694 | 0.0036985 | 0.00092692
83 | 0.98369 | -0.31139 | 0.0013235 | 0.00033171
84 | 0.9838 | -0.3093 | 0.0028197 | 0.00070667
85 | 0.98397 | -0.30595 | 0.0013727 | 0.00034403
86 | 0.98466 | -0.2926 | 0.0011163 | 0.00027977
87 | 0.97922 | -0.3984 | 0.0017568 | 0.00044031
88 | 0.97964 | -0.39017 | 0.0016681 | 0.00041806
89 | 0.97909 | -0.40106 | 0.0032306 | 0.00080965
90 | 0.99672 | -0.061753 | 0.0042104 | 0.0010552
91 | 0.99808 | -0.03609 | 0 | 0
92 | 1 | 0 | -0.3319 | -0.085176
93 | 0.99997 | -0.00056062 | 0.0017894 | 0.00044847
94 | 0.98574 | -0.27166 | 0.0034649 | 0.00086839
95 | 0.98575 | -0.27156 | 0.0030984 | 0.00077653
96 | 0.99193 | -0.15291 | 0.0015437 | 0.00038689
97 | 0.98586 | -0.26945 | 0.0024495 | 0.00061391
98 | 0.97485 | -0.48422 | 0.0028733 | 0.0007201
99 | 0.9749 | -0.48324 | 0.0016427 | 0.0004117
100 | 0.9749 | -0.48317 | 0.0037173 | 0.00093165
101 | 0.97495 | -0.48231 | 0.0018062 | 0.00045267
102 | 0.97497 | -0.48184 | 0.0021605 | 0.00054147
103 | 0.97786 | -0.42511 | 0.0010748 | 0.00026937
104 | 0.97788 | -0.42461 | 0.0010794 | 0.00027053
105 | 0.99114 | -0.16802 | 0.0013006 | 0.00032596
106 | 0.98468 | -0.29225 | 0.00094317 | 0.00023638
107 | 0.98469 | -0.29192 | 0.000961 | 0.00024085
108 | 0.97567 | -0.46804 | 0 | 0
109 | 0.97845 | -0.41368 | 0.004162 | 0.0010431
110 | 0.9786 | -0.41069 | 0.0085595 | 0.0021452
111 | 0.97841 | -0.4144 | 0.0021375 | 0.00053571
112 | 0.97862 | -0.41038 | 0.0030927 | 0.0007751
113 | 0.97839 | -0.41493 | 0 | 0
114 | 0.97864 | -0.40989 | 0.0027469 | 0.00068845
115 | 0.97837 | -0.41533 | 0.00052425 | 0.00013139
116 | 0.97865 | -0.40977 | 0.0031196 | 0.00078184
117 | 0.97866 | -0.40949 | 0.0033857 | 0.00084854
118 | 0.97904 | -0.40214 | 0.0027051 | 0.00067795
119 | 0.97672 | -0.44736 | 0.0023239 | 0.00058243
120 | 0.97612 | -0.45926 | 0.0042877 | 0.0010746
121 | 0.97498 | -0.48166 | 0.004588 | 0.0011499
122 | 0.97512 | -0.47883 | 0.0012301 | 0.00030828
123 | 0.97528 | -0.47579 | 0 | 0
124 | 0.98722 | -0.24314 | 0.0019448 | 0.00048742
125 | 0.98769 | -0.23406 | 0 | 0
126 | 0.97603 | -0.46103 | 0.0018933 | 0.0004745
127 | 0.97535 | -0.47441 | 0.0010712 | 0.00026847
128 | 0.97606 | -0.46035 | 0.0017711 | 0.00044387
129 | 0.9895 | -0.19924 | 0 | 0
130 | 0.98767 | -0.23455 | 0.0010676 | 0.00026756
131 | 0.98922 | -0.2047 | 0.0024034 | 0.00060236
132 | 0.99057 | -0.17879 | 0.0011894 | 0.0002981
133 | 0.98767 | -0.23456 | 0.00089831 | 0.00022514
134 | 0.98922 | -0.20486 | 0.0022849 | 0.00057264
135 | 0.9751 | -0.47935 | 0.00051225 | 0.00012838
136 | 0.97508 | -0.47972 | 0.00070109 | 0.00017571
137 | 0.97502 | -0.4808 | 0.0010557 | 0.00026459
138 | 0.97498 | -0.48163 | 0.00029003 | 7.2689e-05
139 | 0.97499 | -0.48154 | 0.00027902 | 6.9928e-05
140 | 0.97499 | -0.48144 | 0.00027892 | 6.9905e-05
141 | 0.97045 | -0.57097 | 0.0031115 | 0.00077981
142 | 0.97047 | -0.57061 | 0.0014163 | 0.00035496
143 | 0.97035 | -0.57299 | 0.0029165 | 0.00073095
144 | 0.97063 | -0.56748 | 0.001371 | 0.00034361
145 | 0.97033 | -0.57342 | 0.0029932 | 0.00075016
146 | 0.97063 | -0.56736 | 0.0015314 | 0.0003838
147 | 0.98915 | -0.20612 | 0.002481 | 0.0006218
148 | 0.98916 | -0.20588 | 0 | 0
149 | 0.975 | -0.4813 | 0.00045511 | 0.00011406
150 | 0.97501 | -0.48106 | 0.0007634 | 0.00019133
151 | 0.97906 | -0.40165 | 0.0030213 | 0.00075721
152 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.027343 | 0.0068663 | -0.027343 | -0.006866 | 4.1547e-07 | 2.5802e-07 | 0.041812 | 0.041812 | 0.041812 | 0.97321 | -0.51638 | 0.9732 | -0.5167 | 11.4868
1 | -0.029399 | -0.0073815 | 0.029412 | 0.0073897 | 1.3203e-05 | 8.2334e-06 | 0.044955 | 0.044955 | 0.044955 | 0.97321 | -0.51638 | 0.97369 | -0.50697 | 12.3504
2 | 0.024486 | 0.00615 | -0.024475 | -0.0061432 | 1.0955e-05 | 6.7524e-06 | 0.037444 | 0.037444 | 0.037444 | 0.9732 | -0.5167 | 0.97272 | -0.52608 | 10.2868
3 | -0.050449 | -0.012667 | 0.050461 | 0.012675 | 1.2594e-05 | 7.9899e-06 | 0.077105 | 0.077105 | 0.077105 | 0.97369 | -0.50697 | 0.97395 | -0.50174 | 21.1828
4 | 0.021036 | 0.0052774 | -0.021027 | -0.0052714 | 9.7852e-06 | 5.9487e-06 | 0.03215 | 0.03215 | 0.03215 | 0.97369 | -0.50697 | 0.97319 | -0.51673 | 8.8325
5 | 0.010457 | 0.002621 | -0.010455 | -0.0026201 | 1.7681e-06 | 9.0294e-07 | 0.015997 | 0.015997 | 0.015997 | 0.97272 | -0.52608 | 0.97254 | -0.52963 | 4.3948
6 | 0.014018 | 0.0035222 | -0.014006 | -0.0035155 | 1.1812e-05 | 6.7106e-06 | 0.021447 | 0.021447 | 0.021447 | 0.97272 | -0.52608 | 0.97183 | -0.54375 | 5.8921
7 | -0.053686 | -0.013483 | 0.053708 | 0.013496 | 2.1292e-05 | 1.2681e-05 | 0.082033 | 0.082032 | 0.082033 | 0.97395 | -0.50174 | 0.97438 | -0.49343 | 7.5121
8 | 0.017831 | 0.0044705 | -0.017829 | -0.0044691 | 2.339e-06 | 1.3927e-06 | 0.027264 | 0.027264 | 0.027264 | 0.97319 | -0.51673 | 0.97306 | -0.51949 | 7.4902
9 | 0.0082718 | 0.0020728 | -0.0082713 | -0.0020726 | 5.1974e-07 | 2.2527e-07 | 0.012656 | 0.012656 | 0.012656 | 0.97254 | -0.52963 | 0.97247 | -0.53095 | 3.4769
10 | 0.014006 | 0.0035155 | -0.013996 | -0.0035096 | 1.0452e-05 | 5.9389e-06 | 0.021447 | 0.021448 | 0.021448 | 0.97183 | -0.54375 | 0.97103 | -0.55941 | 5.8922
11 | -0.055815 | -0.014024 | 0.055821 | 0.014027 | 5.6607e-06 | 3.2089e-06 | 0.085251 | 0.085251 | 0.085251 | 0.97438 | -0.49343 | 0.97448 | -0.49131 | 5.8552
12 | 0.015878 | 0.0039802 | -0.015878 | -0.0039802 | 5.7986e-08 | 3.3853e-08 | 0.024281 | 0.024281 | 0.024281 | 0.97306 | -0.51949 | 0.97305 | -0.51956 | 6.6707
13 | 0.0063373 | 0.0015879 | -0.0063364 | -0.0015876 | 8.5888e-07 | 2.4751e-07 | 0.0096967 | 0.0096968 | 0.0096968 | 0.97247 | -0.53095 | 0.97233 | -0.53379 | 2.664
14 | 0.013347 | 0.0033471 | -0.013345 | -0.0033458 | 2.3235e-06 | 1.3039e-06 | 0.020454 | 0.020454 | 0.020454 | 0.97103 | -0.55941 | 0.97085 | -0.56306 | 5.6193
15 | -0.055821 | -0.014027 | 0.055829 | 0.014032 | 7.9985e-06 | 4.5339e-06 | 0.085251 | 0.085251 | 0.085251 | 0.97448 | -0.49131 | 0.97464 | -0.48831 | 5.8551
16 | 0.013048 | 0.0032708 | -0.013046 | -0.00327 | 1.4775e-06 | 8.2267e-07 | 0.019953 | 0.019953 | 0.019953 | 0.97305 | -0.51956 | 0.97293 | -0.52194 | 5.4816
17 | -0.0022185 | -0.0005559 | 0.0022186 | 0.00055568 | 9.9479e-08 | -2.2172e-07 | 0.0033953 | 0.0033952 | 0.0033953 | 0.97225 | -0.5354 | 0.9723 | -0.53446 | 0.93278
18 | 0.0010421 | 0.00026107 | -0.0010421 | -0.00026117 | 8.2535e-09 | -1.0202e-07 | 0.0015949 | 0.0015949 | 0.0015949 | 0.97225 | -0.5354 | 0.97224 | -0.53556 | 0.43816
19 | -0.0041526 | -0.0010404 | 0.0041528 | 0.0010404 | 1.3105e-07 | -2.3449e-08 | 0.0063551 | 0.0063551 | 0.0063551 | 0.9723 | -0.53446 | 0.97233 | -0.53379 | 1.7459
20 | -0.0056199 | -0.0014085 | 0.0056202 | 0.0014085 | 3.1385e-07 | 4.8091e-08 | 0.00842 | 0.00842 | 0.00842 | 0.99317 | -0.12942 | 0.99323 | -0.12825 | 2.3132
21 | -0.0056202 | -0.0014085 | 0.0056206 | 0.0014086 | 4.4664e-07 | 6.8403e-08 | 0.00842 | 0.0084199 | 0.00842 | 0.99323 | -0.12825 | 0.99331 | -0.12658 | 2.3132
22 | -0.0028987 | -0.0007265 | 0.0028988 | 0.00072642 | 7.402e-08 | -7.7231e-08 | 0.0044344 | 0.0044344 | 0.0044344 | 0.9727 | -0.52642 | 0.97273 | -0.52588 | 1.2182
23 | -0.0057314 | -0.0014363 | 0.0057314 | 0.0014363 | 3.0495e-09 | 6.3965e-10 | 0.0087674 | 0.0087674 | 0.0087674 | 0.97273 | -0.52588 | 0.97273 | -0.52587 | 2.4086
24 | -0.013991 | -0.0035065 | 0.013993 | 0.0035078 | 2.3004e-06 | 1.2914e-06 | 0.020959 | 0.020959 | 0.020959 | 0.99331 | -0.12658 | 0.99349 | -0.12313 | 5.7578
25 | 0.00837 | 0.0020979 | -0.0083691 | -0.0020975 | 9.4853e-07 | 3.9883e-07 | 0.012539 | 0.012539 | 0.012539 | 0.99331 | -0.12658 | 0.99319 | -0.12896 | 3.4447
26 | -0.0078461 | -0.0019663 | 0.0078465 | 0.0019665 | 4.6169e-07 | 1.8938e-07 | 0.012002 | 0.012002 | 0.012002 | 0.97273 | -0.52587 | 0.97279 | -0.52463 | 3.2973
27 | -0.018287 | -0.0045837 | 0.018287 | 0.0045842 | 8.3016e-07 | 4.9309e-07 | 0.027389 | 0.027389 | 0.027389 | 0.99349 | -0.12313 | 0.99354 | -0.12218 | 7.5246
28 | 0.0042937 | 0.001076 | -0.0042934 | -0.001076 | 2.8328e-07 | -5.521e-08 | 0.0064309 | 0.0064309 | 0.0064309 | 0.99349 | -0.12313 | 0.99342 | -0.12452 | 1.7667
29 | 0.30007 | 0.076865 | -0.29979 | -0.076688 | 0.00027675 | 0.00017637 | 0.45 | 0.45 | 0.45 | 0.99354 | -0.12218 | 0.99254 | -0.14123 | 30.9065
30 | -0.31835 | -0.081449 | 0.31875 | 0.081702 | 0.00039617 | 0.00025258 | 0.47739 | 0.47739 | 0.47739 | 0.99354 | -0.12218 | 0.99489 | -0.096506 | 32.7876
31 | 0.0031555 | 0.00079084 | -0.0031555 | -0.00079084 | 8.0896e-09 | -7.3247e-09 | 0.0047265 | 0.0047266 | 0.0047266 | 0.99342 | -0.12452 | 0.99342 | -0.12457 | 1.2985
32 | -0.011041 | -0.0027672 | 0.011043 | 0.002768 | 1.4169e-06 | 7.4236e-07 | 0.016889 | 0.016889 | 0.016889 | 0.97279 | -0.52463 | 0.97293 | -0.52194 | 4.6399
33 | 0.2983 | 0.076316 | -0.29813 | -0.076209 | 0.00016854 | 0.0001074 | 0.44777 | 0.44777 | 0.44777 | 0.99254 | -0.14123 | 0.99193 | -0.15291 | 30.7535
34 | -0.32272 | -0.082697 | 0.32327 | 0.083044 | 0.00054458 | 0.00034724 | 0.48333 | 0.48333 | 0.48333 | 0.99489 | -0.096506 | 0.99672 | -0.061753 | 33.1956
35 | 0.059867 | 0.015047 | -0.059857 | -0.015042 | 9.8584e-06 | 5.6818e-06 | 0.091401 | 0.091401 | 0.091401 | 0.97481 | -0.48486 | 0.97464 | -0.48831 | 6.2775
36 | -0.061355 | -0.01542 | 0.061368 | 0.015427 | 1.2366e-05 | 7.1647e-06 | 0.093672 | 0.093672 | 0.093672 | 0.97481 | -0.48486 | 0.97503 | -0.48064 | 6.4336
37 | 0.0055503 | 0.001391 | -0.0055501 | -0.001391 | 2.8604e-07 | 5.0482e-08 | 0.0084705 | 0.0084706 | 0.0084706 | 0.97503 | -0.48064 | 0.97497 | -0.48172 | 2.3271
38 | -0.066918 | -0.016818 | 0.06694 | 0.016832 | 2.2247e-05 | 1.3103e-05 | 0.10214 | 0.10214 | 0.10214 | 0.97503 | -0.48064 | 0.97538 | -0.47367 | 7.0153
39 | 0.0023236 | 0.00058232 | -0.0023235 | -0.00058233 | 9.1203e-09 | -1.8281e-08 | 0.0035462 | 0.0035462 | 0.0035462 | 0.97497 | -0.48172 | 0.97497 | -0.4818 | 0.97424
40 | -0.068437 | -0.017207 | 0.068459 | 0.01722 | 2.2121e-05 | 1.3077e-05 | 0.10442 | 0.10442 | 0.10442 | 0.97538 | -0.47367 | 0.97572 | -0.46691 | 7.172
41 | -0.071367 | -0.017948 | 0.071377 | 0.017954 | 9.7674e-06 | 5.8118e-06 | 0.10886 | 0.10886 | 0.10886 | 0.97572 | -0.46691 | 0.97587 | -0.46404 | 7.4766
42 | -0.073627 | -0.018518 | 0.073629 | 0.018519 | 1.8305e-06 | 1.0941e-06 | 0.11229 | 0.11229 | 0.11229 | 0.97587 | -0.46404 | 0.9759 | -0.46352 | 7.7123
43 | 0.013345 | 0.0033458 | -0.013342 | -0.0033443 | 2.7354e-06 | 1.5351e-06 | 0.020454 | 0.020454 | 0.020454 | 0.97085 | -0.56306 | 0.97063 | -0.56736 | 5.6193
44 | -0.0039436 | -0.00098835 | 0.0039437 | 0.00098831 | 1.4445e-07 | -4.0097e-08 | 0.0060195 | 0.0060195 | 0.0060195 | 0.97484 | -0.4844 | 0.97488 | -0.48363 | 1.6537
45 | -0.0068599 | -0.0017192 | 0.006861 | 0.0017195 | 1.0753e-06 | 3.6201e-07 | 0.010471 | 0.010471 | 0.010471 | 0.97488 | -0.48363 | 0.97505 | -0.48034 | 2.8766
46 | -0.011414 | -0.0028607 | 0.011415 | 0.0028609 | 3.9551e-07 | 2.0977e-07 | 0.017419 | 0.017419 | 0.017419 | 0.97505 | -0.48034 | 0.97508 | -0.47961 | 4.7855
47 | -0.013529 | -0.0033907 | 0.013532 | 0.0033925 | 3.203e-06 | 1.7999e-06 | 0.020645 | 0.020645 | 0.020645 | 0.97508 | -0.47961 | 0.97534 | -0.47465 | 5.6718
48 | -0.015873 | -0.0039793 | 0.015875 | 0.0039804 | 2.0121e-06 | 1.1735e-06 | 0.024217 | 0.024217 | 0.024217 | 0.97534 | -0.47465 | 0.97547 | -0.47199 | 6.653
49 | -0.017796 | -0.004462 | 0.0178 | 0.004464 | 3.3455e-06 | 1.99e-06 | 0.027148 | 0.027148 | 0.027148 | 0.97547 | -0.47199 | 0.97567 | -0.46804 | 7.4582
50 | -0.085267 | -0.021456 | 0.085311 | 0.021483 | 4.3829e-05 | 2.6664e-05 | 0.12994 | 0.12994 | 0.12994 | 0.97665 | -0.44877 | 0.9772 | -0.43802 | 8.9247
51 | 0.081955 | 0.020626 | -0.081943 | -0.020619 | 1.1345e-05 | 6.8727e-06 | 0.1249 | 0.1249 | 0.1249 | 0.97665 | -0.44877 | 0.9765 | -0.45167 | 8.5781
52 | -0.086539 | -0.02179 | 0.086539 | 0.02179 | 4.178e-08 | 2.5466e-08 | 0.13181 | 0.13181 | 0.13181 | 0.9772 | -0.43802 | 0.9772 | -0.43801 | 9.0531
53 | 0.081943 | 0.020619 | -0.081923 | -0.020607 | 2.0334e-05 | 1.2318e-05 | 0.1249 | 0.1249 | 0.1249 | 0.9765 | -0.45167 | 0.97624 | -0.45686 | 8.5781
54 | -0.09035 | -0.022745 | 0.090363 | 0.022753 | 1.2628e-05 | 7.7252e-06 | 0.13762 | 0.13762 | 0.13762 | 0.9772 | -0.43801 | 0.97735 | -0.43509 | 9.4516
55 | 0.076544 | 0.019258 | -0.076519 | -0.019244 | 2.4355e-05 | 1.4633e-05 | 0.1167 | 0.1167 | 0.1167 | 0.97624 | -0.45686 | 0.9759 | -0.46352 | 8.015
56 | 0.0053791 | 0.0013481 | -0.0053788 | -0.001348 | 2.8642e-07 | 4.1257e-08 | 0.0081989 | 0.008199 | 0.008199 | 0.97624 | -0.45686 | 0.97618 | -0.45798 | 2.2525
57 | -0.091699 | -0.023088 | 0.091736 | 0.023111 | 3.662e-05 | 2.2432e-05 | 0.13965 | 0.13965 | 0.13965 | 0.97735 | -0.43509 | 0.97777 | -0.42674 | 9.5914
58 | 0.0053788 | 0.001348 | -0.0053787 | -0.001348 | 7.8481e-08 | 1.1308e-08 | 0.008199 | 0.008199 | 0.008199 | 0.97618 | -0.45798 | 0.97616 | -0.45829 | 2.2525
59 | -0.092749 | -0.023365 | 0.092756 | 0.023369 | 7.2221e-06 | 4.4282e-06 | 0.14119 | 0.14119 | 0.14119 | 0.97777 | -0.42674 | 0.97786 | -0.42511 | 9.6973
60 | -0.18747 | -0.04731 | 0.18748 | 0.047318 | 1.2794e-05 | 8.1029e-06 | 0.28464 | 0.28464 | 0.28464 | 0.98045 | -0.37433 | 0.98053 | -0.3729 | 19.5492
61 | 0.18432 | 0.046521 | -0.18429 | -0.046501 | 3.1652e-05 | 2.004e-05 | 0.27986 | 0.27986 | 0.27986 | 0.98045 | -0.37433 | 0.98027 | -0.37791 | 19.2211
62 | -0.18854 | -0.047584 | 0.18862 | 0.047635 | 8.0027e-05 | 5.0692e-05 | 0.28625 | 0.28625 | 0.28625 | 0.98053 | -0.3729 | 0.98098 | -0.36404 | 19.6597
63 | 0.18316 | 0.046217 | -0.18312 | -0.046192 | 4.0542e-05 | 2.5665e-05 | 0.27814 | 0.27814 | 0.27814 | 0.98027 | -0.37791 | 0.98003 | -0.38254 | 19.103
64 | 0.065462 | 0.016447 | -0.0654 | -0.016408 | 6.1655e-05 | 3.9249e-05 | 0.099312 | 0.099312 | 0.099312 | 0.98098 | -0.36404 | 0.97997 | -0.3838 | 27.2834
65 | -0.25408 | -0.064082 | 0.25429 | 0.06421 | 0.00020108 | 0.00012796 | 0.38556 | 0.38556 | 0.38556 | 0.98098 | -0.36404 | 0.98183 | -0.34753 | 26.4806
66 | 0.18209 | 0.045934 | -0.18208 | -0.045928 | 1.0099e-05 | 6.3924e-06 | 0.27658 | 0.27658 | 0.27658 | 0.98003 | -0.38254 | 0.97997 | -0.38369 | 18.9959
67 | 0.039618 | 0.0099442 | -0.039606 | -0.0099367 | 1.1844e-05 | 7.4702e-06 | 0.060162 | 0.060162 | 0.060162 | 0.97997 | -0.3838 | 0.97965 | -0.39007 | 16.5279
68 | 0.025783 | 0.0064638 | -0.025777 | -0.0064604 | 5.4638e-06 | 3.3771e-06 | 0.03915 | 0.03915 | 0.03915 | 0.97997 | -0.3838 | 0.97975 | -0.38824 | 10.7555
69 | -0.25664 | -0.0648 | 0.25693 | 0.064984 | 0.00028966 | 0.00018435 | 0.38912 | 0.38912 | 0.38912 | 0.98183 | -0.34753 | 0.98304 | -0.324 | 26.7254
70 | 0.17898 | 0.045151 | -0.17894 | -0.045123 | 4.3451e-05 | 2.7492e-05 | 0.27187 | 0.27187 | 0.27187 | 0.97997 | -0.38369 | 0.97971 | -0.38877 | 18.6725
71 | 0.036718 | 0.009213 | -0.036699 | -0.0092009 | 1.9244e-05 | 1.2108e-05 | 0.055776 | 0.055776 | 0.055776 | 0.97965 | -0.39007 | 0.97909 | -0.40106 | 15.323
72 | -0.25945 | -0.065615 | 0.25953 | 0.065671 | 8.7899e-05 | 5.5947e-05 | 0.39293 | 0.39293 | 0.39293 | 0.98304 | -0.324 | 0.9834 | -0.31694 | 26.9872
73 | 0.17731 | 0.044716 | -0.1773 | -0.044709 | 1.1915e-05 | 7.5374e-06 | 0.26941 | 0.26941 | 0.26941 | 0.97971 | -0.38877 | 0.97964 | -0.39017 | 18.5031
74 | -0.16396 | -0.041288 | 0.16401 | 0.041316 | 4.5336e-05 | 2.8624e-05 | 0.24944 | 0.24944 | 0.24944 | 0.97836 | -0.41524 | 0.97866 | -0.40945 | 17.1322
75 | 0.16081 | 0.040497 | -0.1608 | -0.040491 | 9.0264e-06 | 5.6961e-06 | 0.24464 | 0.24464 | 0.24464 | 0.97836 | -0.41524 | 0.9783 | -0.41641 | 16.8025
76 | -0.16767 | -0.042235 | 0.16769 | 0.042244 | 1.4209e-05 | 8.9765e-06 | 0.25502 | 0.25502 | 0.25502 | 0.97866 | -0.40945 | 0.97875 | -0.40768 | 17.515
77 | 0.059588 | 0.014989 | -0.059566 | -0.014975 | 2.1567e-05 | 1.3715e-05 | 0.090654 | 0.090654 | 0.090654 | 0.9783 | -0.41641 | 0.97791 | -0.42399 | 24.9051
78 | 0.098819 | 0.024903 | -0.098787 | -0.024884 | 3.1489e-05 | 1.9407e-05 | 0.15035 | 0.15035 | 0.15035 | 0.9783 | -0.41641 | 0.97796 | -0.42307 | 10.3266
79 | -0.16996 | -0.042814 | 0.16997 | 0.042821 | 1.1109e-05 | 7.0205e-06 | 0.25847 | 0.25847 | 0.25847 | 0.97875 | -0.40768 | 0.97882 | -0.40632 | 17.7523
80 | 0.053985 | 0.013576 | -0.053971 | -0.013567 | 1.3784e-05 | 8.7536e-06 | 0.082162 | 0.082162 | 0.082162 | 0.97791 | -0.42399 | 0.97764 | -0.42934 | 22.5719
81 | 0.097372 | 0.024529 | -0.097371 | -0.024528 | 1.4645e-06 | 9.016e-07 | 0.1482 | 0.1482 | 0.1482 | 0.97796 | -0.42307 | 0.97794 | -0.42339 | 10.1787
82 | -0.17224 | -0.043389 | 0.17227 | 0.043411 | 3.3966e-05 | 2.1473e-05 | 0.26192 | 0.26192 | 0.26192 | 0.97882 | -0.40632 | 0.97903 | -0.40219 | 17.9891
83 | 0.052787 | 0.013271 | -0.052786 | -0.01327 | 9.1123e-07 | 5.7847e-07 | 0.080359 | 0.080359 | 0.080359 | 0.97764 | -0.42934 | 0.97762 | -0.4297 | 22.0766
84 | 0.096281 | 0.024255 | -0.096281 | -0.024255 | 5.6059e-07 | 3.4481e-07 | 0.14654 | 0.14654 | 0.14654 | 0.97794 | -0.42339 | 0.97794 | -0.42351 | 10.0649
85 | -0.17377 | -0.043787 | 0.17381 | 0.043807 | 3.1515e-05 | 1.9927e-05 | 0.2642 | 0.2642 | 0.2642 | 0.97903 | -0.40219 | 0.97922 | -0.3984 | 18.1458
86 | 0.051605 | 0.012974 | -0.051561 | -0.012946 | 4.3484e-05 | 2.7594e-05 | 0.078561 | 0.078561 | 0.078561 | 0.97762 | -0.4297 | 0.97672 | -0.44736 | 21.5827
87 | 0.094917 | 0.023913 | -0.094912 | -0.02391 | 5.0128e-06 | 3.0796e-06 | 0.14447 | 0.14447 | 0.14447 | 0.97794 | -0.42351 | 0.97788 | -0.42461 | 9.9224
88 | -0.26323 | -0.066598 | 0.2633 | 0.066643 | 7.0088e-05 | 4.4618e-05 | 0.39853 | 0.39853 | 0.39853 | 0.9834 | -0.31694 | 0.98369 | -0.31139 | 27.3715
89 | -0.26463 | -0.066974 | 0.26465 | 0.066991 | 2.6514e-05 | 1.688e-05 | 0.40053 | 0.40053 | 0.40053 | 0.98369 | -0.31139 | 0.9838 | -0.3093 | 27.509
90 | -0.26747 | -0.067698 | 0.26752 | 0.067725 | 4.2999e-05 | 2.7377e-05 | 0.4048 | 0.4048 | 0.4048 | 0.9838 | -0.3093 | 0.98397 | -0.30595 | 27.802
91 | -0.26889 | -0.068069 | 0.26906 | 0.068179 | 0.00017246 | 0.00010981 | 0.40687 | 0.40687 | 0.40687 | 0.98397 | -0.30595 | 0.98466 | -0.2926 | 27.9445
92 | -0.27018 | -0.068459 | 0.27018 | 0.068462 | 4.5531e-06 | 2.8992e-06 | 0.40856 | 0.40856 | 0.40856 | 0.98466 | -0.2926 | 0.98468 | -0.29225 | 28.0604
93 | -0.17556 | -0.044247 | 0.17563 | 0.044291 | 6.9181e-05 | 4.3754e-05 | 0.26687 | 0.26687 | 0.26687 | 0.97922 | -0.3984 | 0.97964 | -0.39017 | 18.3291
94 | 0.033468 | 0.0083912 | -0.033467 | -0.0083906 | 9.3503e-07 | 5.863e-07 | 0.050866 | 0.050866 | 0.050866 | 0.97909 | -0.40106 | 0.97906 | -0.40165 | 13.9741
95 | -0.32748 | -0.0841 | 0.32788 | 0.08436 | 0.00040859 | 0.00026055 | 0.48961 | 0.48961 | 0.48961 | 0.99672 | -0.061753 | 0.99808 | -0.03609 | 33.6272
96 | -0.32788 | -0.08436 | 0.32846 | 0.084728 | 0.00057647 | 0.0003676 | 0.48961 | 0.48961 | 0.48961 | 0.99808 | -0.03609 | 1 | 0 | 33.6272
97 | 0.0017895 | 0.00044827 | -0.0017894 | -0.00044847 | 4.7783e-08 | -2.0519e-07 | 0.0026627 | 0.0026628 | 0.0026628 | 1 | 0 | 0.99997 | -0.00056062 | 0.73153
98 | -0.0034649 | -0.00086839 | 0.003465 | 0.00086838 | 1.6009e-08 | -9.6472e-09 | 0.0052305 | 0.0052304 | 0.0052305 | 0.98574 | -0.27166 | 0.98575 | -0.27156 | 1.4369
99 | -0.0065634 | -0.0016449 | 0.006564 | 0.0016451 | 6.5811e-07 | 1.9325e-07 | 0.0099076 | 0.0099075 | 0.0099076 | 0.98575 | -0.27156 | 0.98586 | -0.26945 | 2.7219
100 | 0.29659 | 0.075822 | -0.29637 | -0.075684 | 0.00021659 | 0.00013802 | 0.44546 | 0.44546 | 0.44546 | 0.99193 | -0.15291 | 0.99114 | -0.16802 | 30.5945
101 | 0.27238 | 0.069129 | -0.27209 | -0.068942 | 0.00029406 | 0.00018726 | 0.41144 | 0.41144 | 0.41144 | 0.98586 | -0.26945 | 0.98469 | -0.29192 | 28.258
102 | -0.2814 | -0.071388 | 0.28175 | 0.071615 | 0.00035654 | 0.00022711 | 0.42504 | 0.42504 | 0.42504 | 0.98586 | -0.26945 | 0.98722 | -0.24314 | 29.1924
103 | -0.0028733 | -0.0007201 | 0.0028734 | 0.00071996 | 1.3388e-07 | -1.4575e-07 | 0.0043857 | 0.0043857 | 0.0043857 | 0.97485 | -0.48422 | 0.9749 | -0.48324 | 1.2049
104 | -0.0045161 | -0.0011317 | 0.0045161 | 0.0011317 | 1.6033e-08 | -9.591e-10 | 0.006893 | 0.006893 | 0.006893 | 0.9749 | -0.48324 | 0.9749 | -0.48317 | 1.8937
105 | -0.0082334 | -0.0020633 | 0.0082338 | 0.0020635 | 3.344e-07 | 1.436e-07 | 0.012567 | 0.012567 | 0.012567 | 0.9749 | -0.48317 | 0.97495 | -0.48231 | 3.4524
106 | -0.01004 | -0.0025161 | 0.01004 | 0.0025162 | 2.2899e-07 | 1.1412e-07 | 0.015323 | 0.015323 | 0.015323 | 0.97495 | -0.48231 | 0.97497 | -0.48184 | 4.2097
107 | -0.012201 | -0.0030577 | 0.012201 | 0.0030578 | 1.0071e-07 | 5.4796e-08 | 0.018621 | 0.018621 | 0.018621 | 0.97497 | -0.48184 | 0.97498 | -0.48166 | 5.1156
108 | -0.093831 | -0.023638 | 0.093833 | 0.02364 | 2.2207e-06 | 1.363e-06 | 0.14283 | 0.14283 | 0.14283 | 0.97786 | -0.42511 | 0.97788 | -0.42461 | 9.8096
109 | 0.29507 | 0.075358 | -0.29492 | -0.07526 | 0.00015349 | 9.7807e-05 | 0.4435 | 0.4435 | 0.4435 | 0.99114 | -0.16802 | 0.99057 | -0.17879 | 30.4604
110 | -0.27112 | -0.068698 | 0.27113 | 0.068701 | 4.2854e-06 | 2.7288e-06 | 0.40998 | 0.40998 | 0.40998 | 0.98468 | -0.29225 | 0.98469 | -0.29192 | 28.1583
111 | -0.04124 | -0.010342 | 0.041254 | 0.010351 | 1.3797e-05 | 8.7139e-06 | 0.062898 | 0.062898 | 0.062898 | 0.97567 | -0.46804 | 0.97603 | -0.46103 | 17.2797
112 | 0.02344 | 0.0058783 | -0.023433 | -0.0058739 | 7.1158e-06 | 4.3688e-06 | 0.03575 | 0.03575 | 0.03575 | 0.97567 | -0.46804 | 0.97535 | -0.47441 | 9.8215
113 | -0.0068239 | -0.0017089 | 0.0068249 | 0.0017092 | 9.7156e-07 | 3.1957e-07 | 0.010377 | 0.010377 | 0.010377 | 0.97845 | -0.41368 | 0.9786 | -0.41069 | 2.8509
114 | 0.0026619 | 0.00066576 | -0.0026618 | -0.00066589 | 9.1016e-08 | -1.2781e-07 | 0.0040476 | 0.0040477 | 0.0040477 | 0.97845 | -0.41368 | 0.97841 | -0.4144 | 1.112
115 | -0.015384 | -0.0038544 | 0.015385 | 0.0038545 | 2.2419e-07 | 1.2976e-07 | 0.023392 | 0.023392 | 0.023392 | 0.9786 | -0.41069 | 0.97862 | -0.41038 | 6.4265
116 | 0.00052427 | 0.00013019 | -0.00052426 | -0.00013087 | 1.3171e-08 | -6.8594e-07 | 0.00079691 | 0.00079715 | 0.00079715 | 0.97841 | -0.4144 | 0.97839 | -0.41493 | 0.219
117 | -0.018477 | -0.0046296 | 0.018478 | 0.0046299 | 4.2971e-07 | 2.5677e-07 | 0.028095 | 0.028095 | 0.028095 | 0.97862 | -0.41038 | 0.97864 | -0.40989 | 7.7184
118 | 0.00052426 | 0.00013087 | -0.00052425 | -0.00013139 | 9.9315e-09 | -5.1691e-07 | 0.00079715 | 0.00079734 | 0.00079734 | 0.97839 | -0.41493 | 0.97837 | -0.41533 | 0.21905
119 | -0.021225 | -0.0053183 | 0.021225 | 0.0053184 | 1.2838e-07 | 7.8035e-08 | 0.032272 | 0.032272 | 0.032272 | 0.97864 | -0.40989 | 0.97865 | -0.40977 | 8.8658
120 | -0.024344 | -0.0061003 | 0.024345 | 0.0061005 | 3.2183e-07 | 1.981e-07 | 0.037015 | 0.037015 | 0.037015 | 0.97865 | -0.40977 | 0.97866 | -0.40949 | 10.1689
121 | -0.02773 | -0.006949 | 0.02774 | 0.006955 | 9.7103e-06 | 6.0315e-06 | 0.042163 | 0.042163 | 0.042163 | 0.97866 | -0.40949 | 0.97904 | -0.40214 | 11.5832
122 | -0.030445 | -0.007633 | 0.030446 | 0.0076334 | 7.1113e-07 | 4.4399e-07 | 0.046274 | 0.046274 | 0.046274 | 0.97904 | -0.40214 | 0.97906 | -0.40165 | 12.7126
123 | 0.049237 | 0.012364 | -0.049209 | -0.012346 | 2.7936e-05 | 1.7713e-05 | 0.075021 | 0.075021 | 0.075021 | 0.97672 | -0.44736 | 0.97612 | -0.45926 | 20.6101
124 | 0.044922 | 0.011272 | -0.044919 | -0.01127 | 2.3367e-06 | 1.4789e-06 | 0.068484 | 0.068484 | 0.068484 | 0.97612 | -0.45926 | 0.97606 | -0.46035 | 18.8144
125 | -0.016789 | -0.0042076 | 0.016791 | 0.004209 | 2.2626e-06 | 1.3335e-06 | 0.025623 | 0.025623 | 0.025623 | 0.97498 | -0.48166 | 0.97512 | -0.47883 | 7.0393
126 | -0.018021 | -0.0045172 | 0.018024 | 0.0045188 | 2.6167e-06 | 1.5596e-06 | 0.0275 | 0.0275 | 0.0275 | 0.97512 | -0.47883 | 0.97528 | -0.47579 | 7.555
127 | 0.0043366 | 0.0010857 | -0.0043359 | -0.0010858 | 7.3545e-07 | -8.8289e-08 | 0.0066161 | 0.0066163 | 0.0066163 | 0.97528 | -0.47579 | 0.9751 | -0.47935 | 1.8177
128 | -0.02236 | -0.0056045 | 0.022362 | 0.0056054 | 1.462e-06 | 8.9386e-07 | 0.034116 | 0.034116 | 0.034116 | 0.97528 | -0.47579 | 0.97535 | -0.47441 | 9.3726
129 | -0.2837 | -0.072103 | 0.28382 | 0.072182 | 0.0001241 | 7.9053e-05 | 0.42797 | 0.42797 | 0.42797 | 0.98722 | -0.24314 | 0.98769 | -0.23406 | 29.3937
130 | -0.28579 | -0.072674 | 0.28627 | 0.07298 | 0.00048026 | 0.00030595 | 0.43093 | 0.43093 | 0.43093 | 0.98769 | -0.23406 | 0.9895 | -0.19924 | 29.5971
131 | 0.0019659 | 0.00049254 | -0.0019659 | -0.00049269 | 4.5321e-08 | -1.4732e-07 | 0.0029617 | 0.0029618 | 0.0029618 | 0.98769 | -0.23406 | 0.98767 | -0.23455 | 0.81368
132 | -0.043147 | -0.010825 | 0.043148 | 0.010826 | 1.3914e-06 | 8.7978e-07 | 0.065784 | 0.065784 | 0.065784 | 0.97603 | -0.46103 | 0.97606 | -0.46035 | 18.0726
133 | 0.0071714 | 0.0017972 | -0.0071695 | -0.0017965 | 1.8627e-06 | 6.4368e-07 | 0.010784 | 0.010784 | 0.010784 | 0.9895 | -0.19924 | 0.98922 | -0.2047 | 2.9628
134 | -0.29344 | -0.074777 | 0.29373 | 0.074962 | 0.00028998 | 0.00018477 | 0.44172 | 0.44172 | 0.44172 | 0.9895 | -0.19924 | 0.99057 | -0.17879 | 30.3377
135 | 0.00089831 | 0.00022513 | -0.00089831 | -0.00022514 | 5.5101e-10 | -9.9142e-09 | 0.0013534 | 0.0013534 | 0.0013534 | 0.98767 | -0.23455 | 0.98767 | -0.23456 | 0.37181
136 | 0.0047661 | 0.0011942 | -0.004766 | -0.0011942 | 3.7659e-08 | -9.8251e-10 | 0.0071691 | 0.0071691 | 0.0071691 | 0.98922 | -0.2047 | 0.98922 | -0.20486 | 1.9695
137 | 0.0024812 | 0.00062153 | -0.002481 | -0.00062175 | 1.2043e-07 | -2.1888e-07 | 0.0037322 | 0.0037323 | 0.0037323 | 0.98922 | -0.20486 | 0.98916 | -0.20588 | 1.0253
138 | 0.0038236 | 0.00095743 | -0.0038235 | -0.00095745 | 6.7921e-08 | -2.2897e-08 | 0.0058346 | 0.0058346 | 0.0058346 | 0.9751 | -0.47935 | 0.97508 | -0.47972 | 1.6029
139 | 0.0031224 | 0.00078174 | -0.0031223 | -0.00078187 | 1.6045e-07 | -1.3238e-07 | 0.0047647 | 0.0047648 | 0.0047648 | 0.97508 | -0.47972 | 0.97502 | -0.4808 | 1.309
140 | 0.0020665 | 0.00051728 | -0.0020665 | -0.00051735 | 2.5419e-08 | -6.8739e-08 | 0.0031536 | 0.0031536 | 0.0031536 | 0.97502 | -0.4808 | 0.97501 | -0.48106 | 0.86638
141 | -0.00029003 | -7.2689e-05 | 0.00029003 | 7.2466e-05 | 1.3165e-09 | -2.2265e-07 | 0.00044265 | 0.00044257 | 0.00044265 | 0.97498 | -0.48163 | 0.97499 | -0.48154 | 0.12161
142 | -0.00056905 | -0.00014239 | 0.00056905 | 0.00014227 | 2.766e-09 | -1.2022e-07 | 0.0008684 | 0.00086836 | 0.0008684 | 0.97499 | -0.48154 | 0.97499 | -0.48144 | 0.23857
143 | -0.00084798 | -0.00021218 | 0.00084798 | 0.00021207 | 5.6054e-09 | -1.0774e-07 | 0.001294 | 0.001294 | 0.001294 | 0.97499 | -0.48144 | 0.975 | -0.4813 | 0.35551
144 | -0.0090218 | -0.002261 | 0.0090219 | 0.0022611 | 1.5518e-07 | 7.2594e-08 | 0.013833 | 0.013833 | 0.013833 | 0.97045 | -0.57097 | 0.97047 | -0.57061 | 3.8004
145 | 0.0059103 | 0.0014812 | -0.0059098 | -0.0014811 | 5.6882e-07 | 1.3587e-07 | 0.0090624 | 0.0090625 | 0.0090625 | 0.97045 | -0.57097 | 0.97035 | -0.57299 | 2.4897
146 | -0.010438 | -0.002616 | 0.01044 | 0.0026168 | 1.5537e-06 | 7.9449e-07 | 0.016005 | 0.016005 | 0.016005 | 0.97047 | -0.57061 | 0.97063 | -0.56748 | 4.397
147 | 0.0029932 | 0.0007501 | -0.0029932 | -0.00075016 | 6.2208e-08 | -5.7446e-08 | 0.0045901 | 0.0045901 | 0.0045901 | 0.97035 | -0.57299 | 0.97033 | -0.57342 | 1.261
148 | -0.011811 | -0.0029604 | 0.011811 | 0.0029605 | 6.7671e-08 | 3.6506e-08 | 0.018107 | 0.018107 | 0.018107 | 0.97063 | -0.56748 | 0.97063 | -0.56736 | 4.9744
149 | -0.002481 | -0.0006218 | 0.002481 | 0.00062175 | 2.8586e-08 | -5.1949e-08 | 0.0037323 | 0.0037323 | 0.0037323 | 0.98915 | -0.20612 | 0.98916 | -0.20588 | 1.0254
150 | -0.0013031 | -0.00032613 | 0.0013031 | 0.00032602 | 1.4781e-08 | -1.1486e-07 | 0.0019886 | 0.0019885 | 0.0019886 | 0.975 | -0.4813 | 0.97501 | -0.48106 | 0.54632

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.33471 | 0.085879

## res_load
| p_mw | q_mvar
0 | 0.0020558 | 0.00051522
1 | 0.0028569 | 0.00071601
2 | 0.003225 | 0.00080826
3 | 0.0031956 | 0.00080089
4 | 0.0021836 | 0.00054727
5 | 0.0021078 | 0.00052825
6 | 0.0019507 | 0.0004889
7 | 0.001934 | 0.00048472
8 | 0.00064824 | 0.00016246
9 | 0.0028303 | 0.00070935
10 | 0.0011764 | 0.00029483
11 | 0.0019341 | 0.00048472
12 | 0.0010421 | 0.00026117
13 | 0.0021836 | 0.00054727
14 | 0.0056199 | 0.0014085
15 | 0.0028987 | 0.0007265
16 | 0.0028326 | 0.00070991
17 | 0.0021147 | 0.00052999
18 | 0.0083691 | 0.0020975
19 | 0.0011379 | 0.00028518
20 | 0.0031949 | 0.00080071
21 | 0.0014854 | 0.00037228
22 | 0.0039721 | 0.0009955
23 | 0.0031555 | 0.00079084
24 | 0.0014884 | 0.00037302
25 | 0.0040282 | 0.0010096
26 | 0.0032265 | 0.00080864
27 | 0.0014962 | 0.00037499
28 | 0.0023235 | 0.00058233
29 | 0.0029083 | 0.00072889
30 | 0.0022503 | 0.00056397
31 | 0.0039436 | 0.00098835
32 | 0.0029162 | 0.00073087
33 | 0.0045532 | 0.0011411
34 | 0.002114 | 0.00052982
35 | 0.0023411 | 0.00058674
36 | 0.0019214 | 0.00048154
37 | 0.0033125 | 0.00083018
38 | 0.001228 | 0.00030777
39 | 0.003811 | 0.00095513
40 | 0.0013365 | 0.00033497
41 | 0.0053787 | 0.001348
42 | 0.0028905 | 0.00072443
43 | 0.0010131 | 0.00025391
44 | 0.0020033 | 0.00050207
45 | 0.0031475 | 0.00078885
46 | 0.0010609 | 0.00026589
47 | 0.0011324 | 0.00028381
48 | 0.0010275 | 0.00025751
49 | 0.0023525 | 0.00058959
50 | 0.0031006 | 0.00077709
51 | 0.0028877 | 0.00072373
52 | 0.025777 | 0.0064604
53 | 0.0025183 | 0.00063115
54 | 0.001624 | 0.00040702
55 | 0.0031559 | 0.00079094
56 | 0.0036664 | 0.00091889
57 | 0.0023903 | 0.00059906
58 | 0.0022723 | 0.00056948
59 | 0.0055814 | 0.0013988
60 | 0.0014148 | 0.00035459
61 | 0.0022679 | 0.00056838
62 | 0.0011844 | 0.00029684
63 | 0.0010895 | 0.00027305
64 | 0.001501 | 0.00037619
65 | 0.0011813 | 0.00029607
66 | 0.0013632 | 0.00034166
67 | 0.0036985 | 0.00092692
68 | 0.0013235 | 0.00033171
69 | 0.0028197 | 0.00070667
70 | 0.0013727 | 0.00034403
71 | 0.0011163 | 0.00027977
72 | 0.0017568 | 0.00044031
73 | 0.0016681 | 0.00041806
74 | 0.0032306 | 0.00080965
75 | 0.0042104 | 0.0010552
76 | 0.0028057 | 0.00070319
77 | 0.0017894 | 0.00044847
78 | 0.0034649 | 0.00086839
79 | 0.0030984 | 0.00077653
80 | 0.0015437 | 0.00038689
81 | 0.0024495 | 0.00061391
82 | 0.0028733 | 0.0007201
83 | 0.0016427 | 0.0004117
84 | 0.0037173 | 0.00093165
85 | 0.0018062 | 0.00045267
86 | 0.0021605 | 0.00054147
87 | 0.0010748 | 0.00026937
88 | 0.0010794 | 0.00027053
89 | 0.0013006 | 0.00032596
90 | 0.00094317 | 0.00023638
91 | 0.000961 | 0.00024085
92 | 0.004162 | 0.0010431
93 | 0.0085595 | 0.0021452
94 | 0.0021375 | 0.00053571
95 | 0.0030927 | 0.0007751
96 | 0.0027469 | 0.00068845
97 | 0.00052425 | 0.00013139
98 | 0.0031196 | 0.00078184
99 | 0.0033857 | 0.00084854
100 | 0.0027051 | 0.00067795
101 | 0.0023239 | 0.00058243
102 | 0.0042877 | 0.0010746
103 | 0.004588 | 0.0011499
104 | 0.0012301 | 0.00030828
105 | 0.0019448 | 0.00048742
106 | 0.0018933 | 0.0004745
107 | 0.0010712 | 0.00026847
108 | 0.0017711 | 0.00044387
109 | 0.0010676 | 0.00026756
110 | 0.0024034 | 0.00060236
111 | 0.0011894 | 0.0002981
112 | 0.00089831 | 0.00022514
113 | 0.0022849 | 0.00057264
114 | 0.00051225 | 0.00012838
115 | 0.00070109 | 0.00017571
116 | 0.0010557 | 0.00026459
117 | 0.00029003 | 7.2689e-05
118 | 0.00027902 | 6.9928e-05
119 | 0.00027892 | 6.9905e-05
120 | 0.0031115 | 0.00077981
121 | 0.0014163 | 0.00035496
122 | 0.0029165 | 0.00073095
123 | 0.001371 | 0.00034361
124 | 0.0029932 | 0.00075016
125 | 0.0015314 | 0.0003838
126 | 0.002481 | 0.0006218
127 | 0.00045511 | 0.00011406
128 | 0.0007634 | 0.00019133
129 | 0.0030213 | 0.00075721

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1