## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_121-2_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_121-2_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_121-2_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_121-2_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_121-2_0_4_node_12 | 0.4 | n |  | TRUE
5 | bus_LV_121-2_0_4_node_3 | 0.4 | n |  | TRUE
6 | bus_LV_121-2_0_4_node_13 | 0.4 | n |  | TRUE
7 | bus_LV_121-2_0_4_node_32 | 0.4 | n |  | TRUE
8 | bus_LV_121-2_0_4_node_30 | 0.4 | n |  | TRUE
9 | bus_LV_121-2_0_4_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_121-2_0_4_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_121-2_0_4_node_41 | 0.4 | n |  | TRUE
12 | bus_LV_121-2_0_4_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_121-2_0_4_node_20 | 0.4 | n |  | TRUE
14 | bus_LV_121-2_0_4_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_121-2_0_4_node_17 | 0.4 | n |  | TRUE
16 | bus_LV_121-2_0_4_node_42 | 0.4 | n |  | TRUE
17 | bus_LV_121-2_0_4_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_121-2_0_4_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_121-2_0_4_node_23 | 0.4 | n |  | TRUE
20 | bus_LV_121-2_0_4_node_33 | 0.4 | n |  | TRUE
21 | bus_LV_121-2_0_4_node_31 | 0.4 | n |  | TRUE
22 | bus_LV_121-2_0_4_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_121-2_0_4_node_37 | 0.4 | n |  | TRUE
24 | bus_LV_121-2_0_4_node_18 | 0.4 | n |  | TRUE
25 | bus_LV_121-2_0_4_node_43 | 0.4 | n |  | TRUE
26 | bus_LV_121-2_0_4_node_24 | 0.4 | n |  | TRUE
27 | bus_LV_121-2_0_4_node_38 | 0.4 | n |  | TRUE
28 | bus_LV_121-2_0_4_node_45 | 0.4 | n |  | TRUE
29 | bus_LV_121-2_0_4_node_35 | 0.4 | n |  | TRUE
30 | bus_LV_121-2_0_4_node_36 | 0.4 | n |  | TRUE
31 | bus_LV_121-2_0_4_node_19 | 0.4 | n |  | TRUE
32 | bus_LV_121-2_0_4_node_21 | 0.4 | n |  | TRUE
33 | bus_LV_121-2_0_4_node_22 | 0.4 | n |  | TRUE
34 | bus_LV_121-2_0_4_node_25 | 0.4 | n |  | TRUE
35 | bus_LV_121-2_0_4_node_26 | 0.4 | n |  | TRUE
36 | bus_LV_121-2_0_4_node_28 | 0.4 | n |  | TRUE
37 | bus_LV_121-2_0_4_node_29 | 0.4 | n |  | TRUE
38 | bus_LV_121-2_0_4_node_27 | 0.4 | n |  | TRUE
39 | bus_LV_121-2_0_4_node_48 | 0.4 | n |  | TRUE
40 | bus_LV_121-2_0_4_node_47 | 0.4 | n |  | TRUE
41 | bus_LV_121-2_0_4_node_34 | 0.4 | n |  | TRUE
42 | bus_LV_121-2_0_4_node_39 | 0.4 | n |  | TRUE
43 | bus_LV_121-2_0_4_node_40 | 0.4 | n |  | TRUE
44 | bus_LV_121-2_0_4_node_44 | 0.4 | n |  | TRUE
45 | bus_LV_121-2_0_4_node_46 | 0.4 | n |  | TRUE
46 | bus_MV_6_0_node_74 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_121-2_0_4_load_0 | 0 | 0.00083593 | 0.0002095 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_121-2_0_4_load_12 | 4 | 0.00047393 | 0.00011878 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_121-2_0_4_load_13 | 6 | 0.045174 | 0.011322 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_121-2_0_4_load_32 | 7 | 0.0080622 | 0.0020206 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_121-2_0_4_load_30 | 8 | 0.0061489 | 0.0015411 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_121-2_0_4_load_41 | 11 | 0.045541 | 0.011414 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_121-2_0_4_load_20 | 13 | 0.0045096 | 0.0011302 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_121-2_0_4_load_17 | 15 | 0.082186 | 0.020598 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_121-2_0_4_load_42 | 16 | 0.017141 | 0.0042959 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_121-2_0_4_load_15 | 17 | 0.012991 | 0.0032558 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_121-2_0_4_load_23 | 19 | 0.0045757 | 0.0011468 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_121-2_0_4_load_33 | 20 | 0.007809 | 0.0019571 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_121-2_0_4_load_31 | 21 | 0.016639 | 0.0041702 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_121-2_0_4_load_16 | 22 | 0.0064571 | 0.0016183 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_121-2_0_4_load_37 | 23 | 0.046463 | 0.011645 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_121-2_0_4_load_18 | 24 | 0.001536 | 0.00038496 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_121-2_0_4_load_43 | 25 | 0.012909 | 0.0032352 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_121-2_0_4_load_24 | 26 | 0.0020167 | 0.00050544 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_121-2_0_4_load_38 | 27 | 0.0081749 | 0.0020488 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_121-2_0_4_load_35 | 29 | 0.041614 | 0.010429 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_121-2_0_4_load_36 | 30 | 0.01661 | 0.0041629 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_121-2_0_4_load_19 | 31 | 0.00093288 | 0.0002338 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_121-2_0_4_load_21 | 32 | 0.0020435 | 0.00051214 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_121-2_0_4_load_22 | 33 | 0.0014239 | 0.00035686 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_121-2_0_4_load_25 | 34 | 0.0021554 | 0.00054019 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_121-2_0_4_load_26 | 35 | 0.001866 | 0.00046767 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_121-2_0_4_load_29 | 37 | 0.00086618 | 0.00021709 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_121-2_0_4_load_27 | 38 | 0.0025033 | 0.0006274 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_121-2_0_4_load_48 | 39 | 0.0022281 | 0.00055841 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_121-2_0_4_load_47 | 40 | 0.0062204 | 0.001559 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_121-2_0_4_load_34 | 41 | 0.011867 | 0.0029742 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_121-2_0_4_load_39 | 42 | 0.010626 | 0.0026632 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_121-2_0_4_load_40 | 43 | 0.019897 | 0.0049866 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_121-2_0_4_load_46 | 45 | 0.017664 | 0.0044269 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 11 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_121-2_0_4_line_0 |  | 0 | 1 | 0.029833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_121-2_0_4_line_1 |  | 0 | 2 | 0.041815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_121-2_0_4_line_2 |  | 1 | 3 | 0.13968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_121-2_0_4_line_3 |  | 2 | 4 | 0.035074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_121-2_0_4_line_4 |  | 3 | 7 | 0.013679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_121-2_0_4_line_5 |  | 3 | 8 | 0.028078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_121-2_0_4_line_6 |  | 3 | 5 | 0.1456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_121-2_0_4_line_7 |  | 5 | 6 | 0.021853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_121-2_0_4_line_8 |  | 6 | 10 | 0.046905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_121-2_0_4_line_9 |  | 7 | 20 | 0.010172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_121-2_0_4_line_10 |  | 8 | 21 | 0.002594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_121-2_0_4_line_11 |  | 9 | 10 | 0.025684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_121-2_0_4_line_12 |  | 9 | 11 | 0.0093151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_121-2_0_4_line_13 |  | 10 | 17 | 0.087646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_121-2_0_4_line_14 |  | 10 | 12 | 0.036046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_121-2_0_4_line_15 |  | 11 | 23 | 0.023841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_121-2_0_4_line_16 |  | 12 | 13 | 0.053161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_121-2_0_4_line_17 |  | 12 | 14 | 0.016269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_121-2_0_4_line_18 |  | 12 | 15 | 0.02531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_121-2_0_4_line_19 |  | 13 | 18 | 0.043463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_121-2_0_4_line_20 |  | 14 | 16 | 0.017538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_121-2_0_4_line_21 |  | 15 | 24 | 0.0036467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_121-2_0_4_line_22 |  | 16 | 25 | 0.0056295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_121-2_0_4_line_23 |  | 17 | 22 | 0.037752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_121-2_0_4_line_24 |  | 18 | 19 | 0.062534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_121-2_0_4_line_25 |  | 19 | 26 | 0.0032795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_121-2_0_4_line_26 |  | 20 | 41 | 0.018247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_121-2_0_4_line_27 |  | 23 | 30 | 0.04965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_121-2_0_4_line_28 |  | 24 | 31 | 0.017668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_121-2_0_4_line_29 |  | 25 | 44 | 0.011503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_121-2_0_4_line_30 |  | 27 | 28 | 0.020148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_121-2_0_4_line_31 |  | 28 | 44 | 0.03464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_121-2_0_4_line_32 |  | 29 | 30 | 0.0058758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_121-2_0_4_line_33 |  | 31 | 32 | 0.020244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_121-2_0_4_line_34 |  | 32 | 33 | 0.0031242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_121-2_0_4_line_35 |  | 33 | 34 | 0.013117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_121-2_0_4_line_36 |  | 34 | 35 | 0.015666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_121-2_0_4_line_37 |  | 35 | 36 | 0.0023423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_121-2_0_4_line_38 |  | 36 | 37 | 0.023735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_121-2_0_4_line_39 |  | 36 | 38 | 0.016859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_121-2_0_4_line_40 |  | 37 | 39 | 0.0020845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_121-2_0_4_line_41 |  | 39 | 40 | 0.00023409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_121-2_0_4_line_42 |  | 41 | 42 | 0.0010625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_121-2_0_4_line_43 |  | 42 | 43 | 0.010531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_121-2_0_4_line_44 |  | 44 | 45 | 0.01991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_121-2_0_4_trafo_41 | 0.63 MVA 20/0.4 kV | 46 | 11 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2703051.7454 | 1243043.2916 | 2703054.6142 | 1243050.0467 | 2703073.1585 | 1243062.7788
1 | 2703074.012 | 1243098.8215 | 2703066.9514 | 1243087.0564 | 2703066.6154 | 1243082.9029 | 2703076.2032 | 1243068.0134 | 2703074.255 | 1243063.5316 | 2703073.1585 | 1243062.7788
2 | 2703051.7454 | 1243043.2916 | 2703068.4829 | 1243018.5186 | 2703077.1454 | 1243005.9816 | 2703089.6244 | 1242990.4752 | 2703108.323 | 1242965.9811 | 2703119.3487 | 1242950.1492 | 2703139.7664 | 1242963.7479
3 | 2703094.7112 | 1243070.548 | 2703079.5216 | 1243092.8236 | 2703074.012 | 1243098.8215
4 | 2703139.7664 | 1242963.7479 | 2703151.0706 | 1242971.4509
5 | 2703139.7664 | 1242963.7479 | 2703154.7887 | 1242940.0268
6 | 2703139.7664 | 1242963.7479 | 2703119.3487 | 1242950.1492 | 2703126.9148 | 1242938.9387 | 2703138.9552 | 1242923.4581 | 2703159.5425 | 1242899.931 | 2703165.971 | 1242906.3144 | 2703180.3907 | 1242920.9431 | 2703184.5676 | 1242916.8236 | 2703195.1255 | 1242928.3273 | 2703199.1618 | 1242924.4611
7 | 2703199.1618 | 1242924.4611 | 2703206.535 | 1242932.162 | 2703213.8773 | 1242940.6089
8 | 2703245.2143 | 1242975.4907 | 2703234.9959 | 1242964.9047 | 2703213.8773 | 1242940.6089
9 | 2703151.0706 | 1242971.4509 | 2703159.4763 | 1242977.1787 | 2703159.4763 | 1242977.1787
10 | 2703156.1766 | 1242937.8353 | 2703154.7887 | 1242940.0268
11 | 2703228.5498 | 1242971.2641 | 2703232.1521 | 1242967.5795 | 2703242.5525 | 1242979.4363 | 2703245.2143 | 1242975.4907
12 | 2703228.5498 | 1242971.2641 | 2703223.6658 | 1242979.1962
13 | 2703245.2143 | 1242975.4907 | 2703294.273 | 1242902.8607
14 | 2703245.2143 | 1242975.4907 | 2703269.7775 | 1243001.9386
15 | 2703223.6658 | 1242979.1962 | 2703219.276 | 1242986.3256 | 2703217.7807 | 1242991.0144 | 2703213.4213 | 1243000.6185
16 | 2703269.7775 | 1243001.9386 | 2703299.9456 | 1243034.7225 | 2703306.0875 | 1243040.7543
17 | 2703258.0983 | 1243004.0481 | 2703261.7628 | 1243000.6982 | 2703266.128 | 1243005.2999 | 2703269.7775 | 1243001.9386
18 | 2703269.7775 | 1243001.9386 | 2703288.3967 | 1242984.7946
19 | 2703338.2735 | 1243069.9393 | 2703315.4728 | 1243049.9713 | 2703306.0875 | 1243040.7543
20 | 2703258.0983 | 1243004.0481 | 2703256.264 | 1243006.0622 | 2703247.7067 | 1243018.154
21 | 2703288.3967 | 1242984.7946 | 2703291.0794 | 1242982.3244
22 | 2703247.7067 | 1243018.154 | 2703244.4547 | 1243022.7492
23 | 2703294.273 | 1242902.8607 | 2703300.1566 | 1242894.1503 | 2703316.8501 | 1242872.6246
24 | 2703338.2735 | 1243069.9393 | 2703376.7373 | 1243020.6343
25 | 2703378.7545 | 1243018.0485 | 2703376.7373 | 1243020.6343
26 | 2703159.4763 | 1242977.1787 | 2703149.379 | 1242992.3769
27 | 2703213.4213 | 1243000.6185 | 2703192.9001 | 1243045.8288
28 | 2703291.0794 | 1242982.3244 | 2703304.0766 | 1242970.3569
29 | 2703237.8095 | 1243032.1392 | 2703244.4547 | 1243022.7492
30 | 2703248.4628 | 1243062.0255 | 2703249.1834 | 1243064.9292 | 2703249.3503 | 1243067.9344 | 2703249.3736 | 1243070.0698 | 2703248.9434 | 1243072.1973 | 2703248.3307 | 1243074.3884 | 2703247.3706 | 1243076.5622 | 2703245.1419 | 1243081.2493
31 | 2703237.8095 | 1243032.1392 | 2703236.4129 | 1243035.0616 | 2703235.7105 | 1243038.4965 | 2703235.4343 | 1243042.2057 | 2703236.4775 | 1243045.6821 | 2703237.975 | 1243048.6882 | 2703240.4989 | 1243051.3564 | 2703246.2758 | 1243057.3727 | 2703247.7049 | 1243059.5326 | 2703248.4628 | 1243062.0255
32 | 2703190.4715 | 1243051.1793 | 2703192.9001 | 1243045.8288
33 | 2703318.9697 | 1242956.6447 | 2703312.4813 | 1242962.618 | 2703304.0766 | 1242970.3569
34 | 2703321.2682 | 1242954.5286 | 2703318.9697 | 1242956.6447
35 | 2703321.2682 | 1242954.5286 | 2703330.9188 | 1242945.6442
36 | 2703330.9188 | 1242945.6442 | 2703342.4444 | 1242935.0335
37 | 2703344.1676 | 1242933.447 | 2703342.4444 | 1242935.0335
38 | 2703344.1676 | 1242933.447 | 2703351.8502 | 1242926.4198 | 2703361.697 | 1242917.4453
39 | 2703344.1676 | 1242933.447 | 2703361.0256 | 1242933.6308
40 | 2703363.2376 | 1242916.0411 | 2703361.697 | 1242917.4453
41 | 2703363.4106 | 1242915.8834 | 2703363.2376 | 1242916.0411
42 | 2703148.7911 | 1242993.2619 | 2703149.379 | 1242992.3769
43 | 2703142.9637 | 1243002.0332 | 2703148.7911 | 1242993.2619
44 | 2703237.8095 | 1243032.1392 | 2703227.1668 | 1243036.8132 | 2703224.2459 | 1243038.2747 | 2703221.6608 | 1243038.6856 | 2703219.277 | 1243038.3883

## bus_geodata
| x | y | coords
0 | 2703073.1585 | 1243062.7788
1 | 2703051.7454 | 1243043.2916
2 | 2703074.012 | 1243098.8215
3 | 2703139.7664 | 1242963.7479
4 | 2703094.7112 | 1243070.548
5 | 2703199.1618 | 1242924.4611
6 | 2703213.8773 | 1242940.6089
7 | 2703151.0706 | 1242971.4509
8 | 2703154.7887 | 1242940.0268
9 | 2703228.5498 | 1242971.2641
10 | 2703245.2143 | 1242975.4907
11 | 2703223.6658 | 1242979.1962
12 | 2703269.7775 | 1243001.9386
13 | 2703306.0875 | 1243040.7543
14 | 2703258.0983 | 1243004.0481
15 | 2703288.3967 | 1242984.7946
16 | 2703247.7067 | 1243018.154
17 | 2703294.273 | 1242902.8607
18 | 2703338.2735 | 1243069.9393
19 | 2703376.7373 | 1243020.6343
20 | 2703159.4763 | 1242977.1787
21 | 2703156.1766 | 1242937.8353
22 | 2703316.8501 | 1242872.6246
23 | 2703213.4213 | 1243000.6185
24 | 2703291.0794 | 1242982.3244
25 | 2703244.4547 | 1243022.7492
26 | 2703378.7545 | 1243018.0485
27 | 2703245.1419 | 1243081.2493
28 | 2703248.4628 | 1243062.0255
29 | 2703190.4715 | 1243051.1793
30 | 2703192.9001 | 1243045.8288
31 | 2703304.0766 | 1242970.3569
32 | 2703318.9697 | 1242956.6447
33 | 2703321.2682 | 1242954.5286
34 | 2703330.9188 | 1242945.6442
35 | 2703342.4444 | 1242935.0335
36 | 2703344.1676 | 1242933.447
37 | 2703361.697 | 1242917.4453
38 | 2703361.0256 | 1242933.6308
39 | 2703363.2376 | 1242916.0411
40 | 2703363.4106 | 1242915.8834
41 | 2703149.379 | 1242992.3769
42 | 2703148.7911 | 1242993.2619
43 | 2703142.9637 | 1243002.0332
44 | 2703237.8095 | 1243032.1392
45 | 2703219.277 | 1243038.3883
46 | 2703228.5498 | 1242971.2641

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97805 | -0.42249 | 0.00083593 | 0.0002095
1 | 0.97808 | -0.42178 | 0 | 0
2 | 0.97803 | -0.42286 | 0 | 0
3 | 0.97825 | -0.41843 | 0 | 0
4 | 0.97801 | -0.42316 | 0.00047393 | 0.00011878
5 | 0.98939 | -0.20245 | 0 | 0
6 | 0.99106 | -0.17045 | 0.045174 | 0.011322
7 | 0.97751 | -0.43296 | 0.0080622 | 0.0020206
8 | 0.97766 | -0.43009 | 0.0061489 | 0.0015411
9 | 0.99909 | -0.017224 | 0 | 0
10 | 0.99659 | -0.064878 | 0 | 0
11 | 1 | 0 | -0.42824 | -0.10845
12 | 0.99377 | -0.11911 | 0 | 0
13 | 0.99323 | -0.12953 | 0.0045096 | 0.0011302
14 | 0.99294 | -0.13517 | 0 | 0
15 | 0.99137 | -0.16566 | 0.082186 | 0.020598
16 | 0.99205 | -0.15251 | 0.017141 | 0.0042959
17 | 0.99504 | -0.094841 | 0.012991 | 0.0032558
18 | 0.99297 | -0.1346 | 0 | 0
19 | 0.9926 | -0.14189 | 0.0045757 | 0.0011468
20 | 0.97704 | -0.44228 | 0.007809 | 0.0019571
21 | 0.97762 | -0.43088 | 0.016639 | 0.0041702
22 | 0.99482 | -0.099134 | 0.0064571 | 0.0016183
23 | 0.99773 | -0.043601 | 0.046463 | 0.011645
24 | 0.99129 | -0.16707 | 0.001536 | 0.00038496
25 | 0.99185 | -0.15637 | 0.012909 | 0.0032352
26 | 0.99259 | -0.14201 | 0.0020167 | 0.00050544
27 | 0.99116 | -0.16959 | 0.0081749 | 0.0020488
28 | 0.99132 | -0.16666 | 0 | 0
29 | 0.99487 | -0.098656 | 0.041614 | 0.010429
30 | 0.99509 | -0.094351 | 0.01661 | 0.0041629
31 | 0.99097 | -0.17341 | 0.00093288 | 0.0002338
32 | 0.99061 | -0.18035 | 0.0020435 | 0.00051214
33 | 0.99056 | -0.18131 | 0.0014239 | 0.00035686
34 | 0.99037 | -0.185 | 0.0021554 | 0.00054019
35 | 0.99017 | -0.18881 | 0.001866 | 0.00046767
36 | 0.99015 | -0.18931 | 0 | 0
37 | 0.98994 | -0.19324 | 0.00086618 | 0.00021709
38 | 0.99011 | -0.19006 | 0.0025033 | 0.0006274
39 | 0.98993 | -0.19355 | 0.0022281 | 0.00055841
40 | 0.98993 | -0.19358 | 0.0062204 | 0.001559
41 | 0.97632 | -0.45641 | 0.011867 | 0.0029742
42 | 0.97629 | -0.457 | 0.010626 | 0.0026632
43 | 0.97609 | -0.46084 | 0.019897 | 0.0049866
44 | 0.99157 | -0.16164 | 0 | 0
45 | 0.99125 | -0.16788 | 0.017664 | 0.0044269
46 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0013099 | -0.00032733 | 0.0013099 | 0.00032698 | 4.4413e-08 | -3.4598e-07 | 0.0019925 | 0.0019924 | 0.0019925 | 0.97805 | -0.42249 | 0.97808 | -0.42178 | 0.5474
1 | 0.00047395 | 0.00011782 | -0.00047394 | -0.00011834 | 8.1474e-09 | -5.1953e-07 | 0.00072073 | 0.00072092 | 0.00072092 | 0.97805 | -0.42249 | 0.97803 | -0.42286 | 0.19806
2 | -0.0013099 | -0.00032698 | 0.0013101 | 0.00032536 | 2.0786e-07 | -1.6203e-06 | 0.0019924 | 0.0019918 | 0.0019924 | 0.97808 | -0.42178 | 0.97825 | -0.41843 | 0.54736
3 | 0.00047394 | 0.00011834 | -0.00047393 | -0.00011878 | 6.8373e-09 | -4.3576e-07 | 0.00072092 | 0.00072108 | 0.00072108 | 0.97803 | -0.42286 | 0.97801 | -0.42316 | 0.1981
4 | 0.058358 | 0.014662 | -0.058317 | -0.014637 | 4.0432e-05 | 2.5705e-05 | 0.088781 | 0.088781 | 0.088781 | 0.97825 | -0.41843 | 0.97751 | -0.43296 | 24.3903
5 | 0.022801 | 0.0057194 | -0.022789 | -0.0057116 | 1.2667e-05 | 7.7547e-06 | 0.034685 | 0.034685 | 0.034685 | 0.97825 | -0.41843 | 0.97766 | -0.43009 | 9.5289
6 | -0.082469 | -0.020707 | 0.083329 | 0.021255 | 0.00085938 | 0.00054816 | 0.12546 | 0.12546 | 0.12546 | 0.97825 | -0.41843 | 0.98939 | -0.20245 | 34.4663
7 | -0.083329 | -0.021255 | 0.083457 | 0.021338 | 0.00012898 | 8.2269e-05 | 0.12546 | 0.12546 | 0.12546 | 0.98939 | -0.20245 | 0.99106 | -0.17045 | 34.4662
8 | -0.12863 | -0.032659 | 0.12929 | 0.033079 | 0.00065709 | 0.00041993 | 0.19328 | 0.19328 | 0.19328 | 0.99106 | -0.17045 | 0.99659 | -0.064878 | 53.0993
9 | 0.050255 | 0.012616 | -0.050233 | -0.012602 | 2.2327e-05 | 1.4162e-05 | 0.076508 | 0.076508 | 0.076508 | 0.97751 | -0.43296 | 0.97704 | -0.44228 | 21.0187
10 | 0.01664 | 0.0041706 | -0.016639 | -0.0041702 | 6.2395e-07 | 3.668e-07 | 0.025326 | 0.025326 | 0.025326 | 0.97766 | -0.43009 | 0.97762 | -0.43088 | 6.9578
11 | 0.32127 | 0.081803 | -0.32054 | -0.081332 | 0.00073647 | 0.00047033 | 0.47895 | 0.47895 | 0.47895 | 0.99909 | -0.017224 | 0.99659 | -0.064878 | 43.8597
12 | -0.32127 | -0.081803 | 0.32154 | 0.081973 | 0.0002671 | 0.00017058 | 0.47895 | 0.47895 | 0.47895 | 0.99909 | -0.017224 | 1 | 0 | 43.8596
13 | 0.019477 | 0.0048911 | -0.019449 | -0.0048744 | 2.7803e-05 | 1.6654e-05 | 0.029085 | 0.029085 | 0.029085 | 0.99659 | -0.064878 | 0.99504 | -0.094841 | 7.9904
14 | 0.17177 | 0.043362 | -0.17133 | -0.043078 | 0.00044495 | 0.00028383 | 0.25658 | 0.25658 | 0.25658 | 0.99659 | -0.064878 | 0.99377 | -0.11911 | 35.2449
15 | 0.10506 | 0.026472 | -0.10484 | -0.026332 | 0.00021862 | 0.0001396 | 0.15637 | 0.15637 | 0.15637 | 1 | 0 | 0.99773 | -0.043601 | 42.9599
16 | 0.011111 | 0.0027864 | -0.011106 | -0.0027835 | 5.5187e-06 | 2.8436e-06 | 0.016638 | 0.016638 | 0.016638 | 0.99377 | -0.11911 | 0.99323 | -0.12953 | 4.571
17 | 0.055999 | 0.014076 | -0.055956 | -0.014049 | 4.291e-05 | 2.7252e-05 | 0.083864 | 0.083865 | 0.083865 | 0.99377 | -0.11911 | 0.99294 | -0.13517 | 23.0397
18 | 0.10422 | 0.026216 | -0.10398 | -0.026068 | 0.00023121 | 0.00014765 | 0.15608 | 0.15608 | 0.15608 | 0.99377 | -0.11911 | 0.99137 | -0.16566 | 42.8791
19 | 0.0065964 | 0.0016533 | -0.0065948 | -0.0016529 | 1.5918e-06 | 4.5637e-07 | 0.0098824 | 0.0098826 | 0.0098826 | 0.99323 | -0.12953 | 0.99297 | -0.1346 | 2.715
20 | 0.055956 | 0.014049 | -0.05591 | -0.01402 | 4.6255e-05 | 2.9377e-05 | 0.083865 | 0.083865 | 0.083865 | 0.99294 | -0.13517 | 0.99205 | -0.15251 | 23.0397
21 | 0.021798 | 0.0054702 | -0.021796 | -0.0054693 | 1.4641e-06 | 8.9002e-07 | 0.032721 | 0.032721 | 0.032721 | 0.99137 | -0.16566 | 0.99129 | -0.16707 | 8.9892
22 | 0.038769 | 0.0097238 | -0.038762 | -0.0097193 | 7.1395e-06 | 4.4966e-06 | 0.058154 | 0.058154 | 0.058154 | 0.99205 | -0.15251 | 0.99185 | -0.15637 | 15.9765
23 | 0.0064584 | 0.0016187 | -0.0064571 | -0.0016183 | 1.3206e-06 | 3.549e-07 | 0.0096581 | 0.0096583 | 0.0096583 | 0.99504 | -0.094841 | 0.99482 | -0.099134 | 2.6534
24 | 0.0065948 | 0.0016529 | -0.0065925 | -0.0016522 | 2.2903e-06 | 6.5722e-07 | 0.0098826 | 0.0098829 | 0.0098829 | 0.99297 | -0.1346 | 0.9926 | -0.14189 | 2.7151
25 | 0.0020167 | 0.00050541 | -0.0020167 | -0.00050544 | 1.1241e-08 | -3.5195e-08 | 0.0030233 | 0.0030233 | 0.0030233 | 0.9926 | -0.14189 | 0.99259 | -0.14201 | 0.83059
26 | 0.042424 | 0.010645 | -0.042395 | -0.010627 | 2.8568e-05 | 1.8055e-05 | 0.064615 | 0.064615 | 0.064615 | 0.97704 | -0.44228 | 0.97632 | -0.45641 | 17.7515
27 | 0.058374 | 0.014687 | -0.058232 | -0.014598 | 0.00014118 | 8.9709e-05 | 0.087079 | 0.087079 | 0.087079 | 0.99773 | -0.043601 | 0.99509 | -0.094351 | 23.9229
28 | 0.02026 | 0.0050844 | -0.020254 | -0.0050807 | 6.129e-06 | 3.6949e-06 | 0.030415 | 0.030415 | 0.030415 | 0.99129 | -0.16707 | 0.99097 | -0.17341 | 8.3558
29 | 0.025853 | 0.0064841 | -0.025847 | -0.0064801 | 6.4902e-06 | 4.0053e-06 | 0.038788 | 0.038788 | 0.038788 | 0.99185 | -0.15637 | 0.99157 | -0.16164 | 10.6561
30 | -0.0081749 | -0.0020488 | 0.008176 | 0.0020493 | 1.138e-06 | 4.6861e-07 | 0.012273 | 0.012273 | 0.012273 | 0.99116 | -0.16959 | 0.99132 | -0.16666 | 3.3716
31 | -0.008176 | -0.0020493 | 0.008178 | 0.0020501 | 1.9565e-06 | 8.0546e-07 | 0.012273 | 0.012273 | 0.012273 | 0.99132 | -0.16666 | 0.99157 | -0.16164 | 3.3716
32 | -0.041614 | -0.010429 | 0.041622 | 0.010435 | 8.5361e-06 | 5.3868e-06 | 0.062241 | 0.062241 | 0.062241 | 0.99487 | -0.098656 | 0.99509 | -0.094351 | 17.0992
33 | 0.019321 | 0.0048469 | -0.019315 | -0.004843 | 6.3908e-06 | 3.8294e-06 | 0.029014 | 0.029014 | 0.029014 | 0.99097 | -0.17341 | 0.99061 | -0.18035 | 7.971
34 | 0.017272 | 0.0043309 | -0.017271 | -0.0043304 | 7.8863e-07 | 4.6451e-07 | 0.025945 | 0.025945 | 0.025945 | 0.99061 | -0.18035 | 0.99056 | -0.18131 | 7.1277
35 | 0.015847 | 0.0039736 | -0.015844 | -0.003972 | 2.7877e-06 | 1.6153e-06 | 0.023806 | 0.023806 | 0.023806 | 0.99056 | -0.18131 | 0.99037 | -0.185 | 6.5401
36 | 0.013689 | 0.0034318 | -0.013686 | -0.0034304 | 2.4852e-06 | 1.389e-06 | 0.020568 | 0.020568 | 0.020568 | 0.99037 | -0.185 | 0.99017 | -0.18881 | 5.6504
37 | 0.01182 | 0.0029627 | -0.01182 | -0.0029626 | 2.7715e-07 | 1.4725e-07 | 0.017763 | 0.017763 | 0.017763 | 0.99017 | -0.18881 | 0.99015 | -0.18931 | 4.88
38 | 0.0093165 | 0.0023353 | -0.0093148 | -0.0023345 | 1.7448e-06 | 8.1147e-07 | 0.014001 | 0.014001 | 0.014001 | 0.99015 | -0.18931 | 0.98994 | -0.19324 | 3.8465
39 | 0.0025034 | 0.00062724 | -0.0025033 | -0.0006274 | 8.9484e-08 | -1.5956e-07 | 0.0037622 | 0.0037622 | 0.0037622 | 0.99015 | -0.18931 | 0.99011 | -0.19006 | 1.0336
40 | 0.0084486 | 0.0021174 | -0.0084485 | -0.0021174 | 1.2607e-07 | 5.3883e-08 | 0.012699 | 0.012699 | 0.012699 | 0.98994 | -0.19324 | 0.98993 | -0.19355 | 3.4888
41 | 0.0062204 | 0.001559 | -0.0062204 | -0.001559 | 7.6745e-09 | 1.902e-09 | 0.0093502 | 0.0093502 | 0.0093502 | 0.98993 | -0.19355 | 0.98993 | -0.19358 | 2.5687
42 | 0.030528 | 0.0076526 | -0.030527 | -0.007652 | 8.6253e-07 | 5.3873e-07 | 0.046528 | 0.046528 | 0.046528 | 0.97632 | -0.45641 | 0.97629 | -0.457 | 12.7825
43 | 0.019901 | 0.0049888 | -0.019897 | -0.0049866 | 3.6332e-06 | 2.1936e-06 | 0.030332 | 0.030332 | 0.030332 | 0.97629 | -0.457 | 0.97609 | -0.46084 | 8.333
44 | 0.017669 | 0.00443 | -0.017664 | -0.0044269 | 5.2493e-06 | 3.1028e-06 | 0.026516 | 0.026516 | 0.026516 | 0.99157 | -0.16164 | 0.99125 | -0.16788 | 7.2845

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.47379 | 0.11986

## res_load
| p_mw | q_mvar
0 | 0.00083593 | 0.0002095
1 | 0.00047393 | 0.00011878
2 | 0.045174 | 0.011322
3 | 0.0080622 | 0.0020206
4 | 0.0061489 | 0.0015411
5 | 0.045541 | 0.011414
6 | 0.0045096 | 0.0011302
7 | 0.082186 | 0.020598
8 | 0.017141 | 0.0042959
9 | 0.012991 | 0.0032558
10 | 0.0045757 | 0.0011468
11 | 0.007809 | 0.0019571
12 | 0.016639 | 0.0041702
13 | 0.0064571 | 0.0016183
14 | 0.046463 | 0.011645
15 | 0.001536 | 0.00038496
16 | 0.012909 | 0.0032352
17 | 0.0020167 | 0.00050544
18 | 0.0081749 | 0.0020488
19 | 0.041614 | 0.010429
20 | 0.01661 | 0.0041629
21 | 0.00093288 | 0.0002338
22 | 0.0020435 | 0.00051214
23 | 0.0014239 | 0.00035686
24 | 0.0021554 | 0.00054019
25 | 0.001866 | 0.00046767
26 | 0.00086618 | 0.00021709
27 | 0.0025033 | 0.0006274
28 | 0.0022281 | 0.00055841
29 | 0.0062204 | 0.001559
30 | 0.011867 | 0.0029742
31 | 0.010626 | 0.0026632
32 | 0.019897 | 0.0049866
33 | 0.017664 | 0.0044269

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1