## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_121-35_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_121-35_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_121-35_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_121-35_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_121-35_0_4_node_10 | 0.4 | n |  | TRUE
5 | bus_LV_121-35_0_4_node_32 | 0.4 | n |  | TRUE
6 | bus_LV_121-35_0_4_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_121-35_0_4_node_31 | 0.4 | n |  | TRUE
8 | bus_LV_121-35_0_4_node_30 | 0.4 | n |  | TRUE
9 | bus_LV_121-35_0_4_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_121-35_0_4_node_11 | 0.4 | n |  | TRUE
11 | bus_LV_121-35_0_4_node_19 | 0.4 | n |  | TRUE
12 | bus_LV_121-35_0_4_node_15 | 0.4 | n |  | TRUE
13 | bus_LV_121-35_0_4_node_12 | 0.4 | n |  | TRUE
14 | bus_LV_121-35_0_4_node_17 | 0.4 | n |  | TRUE
15 | bus_LV_121-35_0_4_node_29 | 0.4 | n |  | TRUE
16 | bus_LV_121-35_0_4_node_14 | 0.4 | n |  | TRUE
17 | bus_LV_121-35_0_4_node_18 | 0.4 | n |  | TRUE
18 | bus_LV_121-35_0_4_node_20 | 0.4 | n |  | TRUE
19 | bus_LV_121-35_0_4_node_25 | 0.4 | n |  | TRUE
20 | bus_LV_121-35_0_4_node_24 | 0.4 | n |  | TRUE
21 | bus_LV_121-35_0_4_node_27 | 0.4 | n |  | TRUE
22 | bus_LV_121-35_0_4_node_26 | 0.4 | n |  | TRUE
23 | bus_LV_121-35_0_4_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_121-35_0_4_node_22 | 0.4 | n |  | TRUE
25 | bus_LV_121-35_0_4_node_13 | 0.4 | n |  | TRUE
26 | bus_LV_121-35_0_4_node_23 | 0.4 | n |  | TRUE
27 | bus_LV_121-35_0_4_node_21 | 0.4 | n |  | TRUE
28 | bus_LV_121-35_0_4_node_28 | 0.4 | n |  | TRUE
29 | bus_MV_357_0_node_73 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_121-35_0_4_load_0 | 0 | 0.011542 | 0.0028927 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_121-35_0_4_load_3 | 2 | 0.0062148 | 0.0015576 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_121-35_0_4_load_4 | 3 | 0.003459 | 0.0008669 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_121-35_0_4_load_32 | 5 | 0.03506 | 0.0087868 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_121-35_0_4_load_31 | 7 | 0.032371 | 0.008113 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_121-35_0_4_load_30 | 8 | 0.018913 | 0.0047402 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_121-35_0_4_load_19 | 11 | 0.01671 | 0.0041879 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_121-35_0_4_load_15 | 12 | 0.012778 | 0.0032025 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_121-35_0_4_load_12 | 13 | 0.071229 | 0.017852 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_121-35_0_4_load_29 | 15 | 0.051447 | 0.012894 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_121-35_0_4_load_18 | 17 | 0.0078647 | 0.0019711 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_121-35_0_4_load_20 | 18 | 0.017689 | 0.0044332 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_121-35_0_4_load_25 | 19 | 0.0025865 | 0.00064824 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_121-35_0_4_load_24 | 20 | 0.0049623 | 0.0012437 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_121-35_0_4_load_26 | 22 | 0.048604 | 0.012181 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_121-35_0_4_load_16 | 23 | 0.030086 | 0.0075402 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_121-35_0_4_load_22 | 24 | 0.027007 | 0.0067687 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_121-35_0_4_load_13 | 25 | 0.083328 | 0.020884 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_121-35_0_4_load_23 | 26 | 0.015315 | 0.0038382 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_121-35_0_4_load_21 | 27 | 0.013029 | 0.0032653 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_121-35_0_4_load_28 | 28 | 0.028083 | 0.0070383 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 23 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_121-35_0_4_line_0 |  | 0 | 1 | 0.015791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_121-35_0_4_line_1 |  | 1 | 2 | 0.011753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
2 | LV_121-35_0_4_line_2 |  | 1 | 3 | 0.018883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_121-35_0_4_line_3 |  | 1 | 4 | 0.015072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
4 | LV_121-35_0_4_line_4 |  | 2 | 5 | 0.011951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
5 | LV_121-35_0_4_line_5 |  | 4 | 12 | 0.013757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_121-35_0_4_line_6 |  | 4 | 13 | 0.014335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
7 | LV_121-35_0_4_line_7 |  | 5 | 7 | 0.028688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_121-35_0_4_line_8 |  | 6 | 7 | 0.029799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_121-35_0_4_line_9 |  | 6 | 8 | 0.008832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
10 | LV_121-35_0_4_line_10 |  | 8 | 10 | 0.0070765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_121-35_0_4_line_11 |  | 9 | 10 | 0.010769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
12 | LV_121-35_0_4_line_12 |  | 9 | 11 | 0.0091638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
13 | LV_121-35_0_4_line_13 |  | 11 | 18 | 0.01464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
14 | LV_121-35_0_4_line_14 |  | 12 | 17 | 0.022809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_121-35_0_4_line_15 |  | 13 | 25 | 0.021244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_121-35_0_4_line_16 |  | 14 | 15 | 0.054074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_121-35_0_4_line_17 |  | 14 | 16 | 0.044522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_121-35_0_4_line_18 |  | 15 | 21 | 0.006266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_121-35_0_4_line_19 |  | 16 | 25 | 0.018304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_121-35_0_4_line_20 |  | 18 | 27 | 0.0070292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_121-35_0_4_line_21 |  | 19 | 20 | 0.0074388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_121-35_0_4_line_22 |  | 20 | 22 | 0.014448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_121-35_0_4_line_23 |  | 21 | 22 | 0.01084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_121-35_0_4_line_24 |  | 23 | 24 | 0.0047225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_121-35_0_4_line_25 |  | 24 | 26 | 0.0052707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_121-35_0_4_line_26 |  | 26 | 28 | 0.013505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
27 | LV_121-35_0_4_line_27 |  | 27 | 28 | 0.0030196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_121-35_0_4_trafo_16 | 0.63 MVA 20/0.4 kV | 29 | 23 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2702608.7153 | 1242042.663 | 2702620.7121 | 1242052.9306
1 | 2702608.7153 | 1242042.663 | 2702602.3076 | 1242036.7366 | 2702599.9938 | 1242034.7881
2 | 2702608.7153 | 1242042.663 | 2702621.0647 | 1242028.3787
3 | 2702598.5379 | 1242047.4686 | 2702602.3207 | 1242042.9749 | 2702605.737 | 1242046.1142 | 2702608.7153 | 1242042.663
4 | 2702590.8521 | 1242027.0899 | 2702599.9938 | 1242034.7881
5 | 2702598.5379 | 1242047.4686 | 2702609.0847 | 1242056.3022
6 | 2702598.5379 | 1242047.4686 | 2702589.3061 | 1242058.4352
7 | 2702568.7295 | 1242008.826 | 2702584.8758 | 1242022.0572 | 2702590.8521 | 1242027.0899
8 | 2702546.0444 | 1241989.5055 | 2702563.5974 | 1242004.6205 | 2702568.7295 | 1242008.826
9 | 2702546.0444 | 1241989.5055 | 2702539.3476 | 1241983.7473
10 | 2702533.9819 | 1241979.1336 | 2702539.3476 | 1241983.7473
11 | 2702526.893 | 1241987.2396 | 2702530.7964 | 1241982.7591 | 2702533.9819 | 1241979.1336
12 | 2702526.893 | 1241987.2396 | 2702533.9761 | 1241993.0537
13 | 2702545.2922 | 1242002.3424 | 2702533.9761 | 1241993.0537
14 | 2702609.0847 | 1242056.3022 | 2702626.5703 | 1242070.9475
15 | 2702589.3061 | 1242058.4352 | 2702580.2882 | 1242069.1476 | 2702575.7158 | 1242074.7622
16 | 2702533.9469 | 1242121.5541 | 2702500.991 | 1242078.6831
17 | 2702533.9469 | 1242121.5541 | 2702547.7487 | 1242109.1496 | 2702564.1653 | 1242088.9621
18 | 2702497.1721 | 1242073.7153 | 2702500.991 | 1242078.6831
19 | 2702564.1653 | 1242088.9621 | 2702572.0994 | 1242079.2028 | 2702575.7158 | 1242074.7622
20 | 2702545.2922 | 1242002.3424 | 2702550.7254 | 1242006.8021
21 | 2702476.9668 | 1242047.9708 | 2702481.5595 | 1242053.8225
22 | 2702490.4798 | 1242065.1882 | 2702481.5595 | 1242053.8225
23 | 2702497.1721 | 1242073.7153 | 2702490.4798 | 1242065.1882
24 | 2702571.0731 | 1242023.8038 | 2702567.4955 | 1242020.7212
25 | 2702563.4979 | 1242017.2862 | 2702563.7305 | 1242017.4772 | 2702567.4955 | 1242020.7212
26 | 2702563.4979 | 1242017.2862 | 2702553.0595 | 1242008.718
27 | 2702553.0595 | 1242008.718 | 2702550.7254 | 1242006.8021

## bus_geodata
| x | y | coords
0 | 2702620.7121 | 1242052.9306
1 | 2702608.7153 | 1242042.663
2 | 2702599.9938 | 1242034.7881
3 | 2702621.0647 | 1242028.3787
4 | 2702598.5379 | 1242047.4686
5 | 2702590.8521 | 1242027.0899
6 | 2702546.0444 | 1241989.5055
7 | 2702568.7295 | 1242008.826
8 | 2702539.3476 | 1241983.7473
9 | 2702526.893 | 1241987.2396
10 | 2702533.9819 | 1241979.1336
11 | 2702533.9761 | 1241993.0537
12 | 2702609.0847 | 1242056.3022
13 | 2702589.3061 | 1242058.4352
14 | 2702533.9469 | 1242121.5541
15 | 2702500.991 | 1242078.6831
16 | 2702564.1653 | 1242088.9621
17 | 2702626.5703 | 1242070.9475
18 | 2702545.2922 | 1242002.3424
19 | 2702476.9668 | 1242047.9708
20 | 2702481.5595 | 1242053.8225
21 | 2702497.1721 | 1242073.7153
22 | 2702490.4798 | 1242065.1882
23 | 2702571.0731 | 1242023.8038
24 | 2702567.4955 | 1242020.7212
25 | 2702575.7158 | 1242074.7622
26 | 2702563.4979 | 1242017.2862
27 | 2702550.7254 | 1242006.8021
28 | 2702553.0595 | 1242008.718
29 | 2702598.5379 | 1242047.4686

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98521 | -0.28297 | 0.011542 | 0.0028927
1 | 0.98537 | -0.2797 | 0 | 0
2 | 0.98618 | -0.26401 | 0.0062148 | 0.0015576
3 | 0.98531 | -0.28087 | 0.003459 | 0.0008669
4 | 0.98439 | -0.29885 | 0 | 0
5 | 0.98703 | -0.24774 | 0.03506 | 0.0087868
6 | 0.99184 | -0.15517 | 0 | 0
7 | 0.98928 | -0.20433 | 0.032371 | 0.008113
8 | 0.9926 | -0.14065 | 0.018913 | 0.0047402
9 | 0.99421 | -0.10989 | 0 | 0
10 | 0.99324 | -0.12844 | 0 | 0
11 | 0.99504 | -0.094134 | 0.01671 | 0.0041879
12 | 0.98412 | -0.30396 | 0.012778 | 0.0032025
13 | 0.98351 | -0.31576 | 0.071229 | 0.017852
14 | 0.97718 | -0.43889 | 0 | 0
15 | 0.97174 | -0.54569 | 0.051447 | 0.012894
16 | 0.98165 | -0.35185 | 0 | 0
17 | 0.98396 | -0.30719 | 0.0078647 | 0.0019711
18 | 0.99641 | -0.067941 | 0.017689 | 0.0044332
19 | 0.97073 | -0.56581 | 0.0025865 | 0.00064824
20 | 0.97074 | -0.56546 | 0.0049623 | 0.0012437
21 | 0.97142 | -0.55219 | 0 | 0
22 | 0.97085 | -0.56344 | 0.048604 | 0.012181
23 | 1 | 0 | -0.51693 | -0.13188
24 | 0.99945 | -0.010464 | 0.027007 | 0.0067687
25 | 0.98257 | -0.33405 | 0.083328 | 0.020884
26 | 0.99886 | -0.021535 | 0.015315 | 0.0038382
27 | 0.9971 | -0.054845 | 0.013029 | 0.0032653
28 | 0.99741 | -0.049053 | 0.028083 | 0.0070383
29 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.011542 | -0.0028927 | 0.011544 | 0.0028936 | 1.7995e-06 | 9.5054e-07 | 0.017432 | 0.017432 | 0.017432 | 0.98521 | -0.28297 | 0.98537 | -0.2797 | 4.7891
1 | -0.2996 | -0.075781 | 0.29982 | 0.075925 | 0.00022578 | 0.0001439 | 0.45267 | 0.45267 | 0.45267 | 0.98537 | -0.2797 | 0.98618 | -0.26401 | 31.0902
2 | 0.0034592 | 0.00086679 | -0.003459 | -0.0008669 | 1.9322e-07 | -1.1686e-07 | 0.0052237 | 0.0052237 | 0.0052237 | 0.98537 | -0.2797 | 0.98531 | -0.28087 | 1.4351
3 | 0.2846 | 0.072021 | -0.28433 | -0.071854 | 0.00026129 | 0.00016646 | 0.43002 | 0.43002 | 0.43002 | 0.98537 | -0.2797 | 0.98439 | -0.29885 | 29.5342
4 | -0.30604 | -0.077482 | 0.30628 | 0.077635 | 0.0002392 | 0.00015248 | 0.46205 | 0.46205 | 0.46205 | 0.98618 | -0.26401 | 0.98703 | -0.24774 | 31.7342
5 | 0.020649 | 0.0051771 | -0.020644 | -0.0051741 | 5.0266e-06 | 3.0422e-06 | 0.031214 | 0.031214 | 0.031214 | 0.98439 | -0.29885 | 0.98412 | -0.30396 | 8.5754
6 | 0.26369 | 0.066677 | -0.26347 | -0.066541 | 0.00021374 | 0.00013607 | 0.3988 | 0.3988 | 0.3988 | 0.98439 | -0.29885 | 0.98351 | -0.31576 | 27.3904
7 | -0.34134 | -0.086422 | 0.34205 | 0.086877 | 0.00071306 | 0.00045489 | 0.5149 | 0.5149 | 0.5149 | 0.98703 | -0.24774 | 0.98928 | -0.20433 | 35.3643
8 | 0.37531 | 0.095556 | -0.37442 | -0.09499 | 0.00088738 | 0.00056639 | 0.56359 | 0.5636 | 0.5636 | 0.99184 | -0.15517 | 0.98928 | -0.20433 | 38.7084
9 | -0.37531 | -0.095556 | 0.37557 | 0.095724 | 0.000263 | 0.00016787 | 0.56359 | 0.56359 | 0.56359 | 0.99184 | -0.15517 | 0.9926 | -0.14065 | 38.7084
10 | -0.39449 | -0.10046 | 0.39472 | 0.10061 | 0.00023246 | 0.00014841 | 0.59195 | 0.59195 | 0.59195 | 0.9926 | -0.14065 | 0.99324 | -0.12844 | 40.6557
11 | 0.39507 | 0.10084 | -0.39472 | -0.10061 | 0.00035375 | 0.00022584 | 0.59195 | 0.59195 | 0.59195 | 0.99421 | -0.10989 | 0.99324 | -0.12844 | 40.6557
12 | -0.39507 | -0.10084 | 0.39537 | 0.10103 | 0.00030103 | 0.00019218 | 0.59195 | 0.59195 | 0.59195 | 0.99421 | -0.10989 | 0.99504 | -0.094134 | 40.6557
13 | -0.41208 | -0.10522 | 0.41261 | 0.10555 | 0.00052239 | 0.00033357 | 0.61694 | 0.61693 | 0.61694 | 0.99504 | -0.094134 | 0.99641 | -0.067941 | 42.3719
14 | 0.0078659 | 0.0019716 | -0.0078647 | -0.0019711 | 1.2099e-06 | 4.8458e-07 | 0.011893 | 0.011894 | 0.011894 | 0.98412 | -0.30396 | 0.98396 | -0.30719 | 3.2675
15 | 0.19224 | 0.048689 | -0.19207 | -0.048582 | 0.00016869 | 0.00010689 | 0.29104 | 0.29104 | 0.29104 | 0.98351 | -0.31576 | 0.98257 | -0.33405 | 19.9889
16 | 0.1082 | 0.027349 | -0.10765 | -0.026997 | 0.00055103 | 0.00035199 | 0.16485 | 0.16485 | 0.16485 | 0.97718 | -0.43889 | 0.97174 | -0.54569 | 45.2874
17 | -0.1082 | -0.027349 | 0.10865 | 0.027639 | 0.00045369 | 0.0002898 | 0.16485 | 0.16485 | 0.16485 | 0.97718 | -0.43889 | 0.98165 | -0.35185 | 45.2873
18 | 0.056201 | 0.014104 | -0.056184 | -0.014093 | 1.7406e-05 | 1.1062e-05 | 0.086067 | 0.086067 | 0.086067 | 0.97174 | -0.54569 | 0.97142 | -0.55219 | 23.6447
19 | -0.10865 | -0.027639 | 0.10875 | 0.027698 | 9.3264e-05 | 5.9225e-05 | 0.16485 | 0.16485 | 0.16485 | 0.98165 | -0.35185 | 0.98257 | -0.33405 | 22.6436
20 | -0.43029 | -0.10999 | 0.43057 | 0.11016 | 0.00027275 | 0.0001742 | 0.64335 | 0.64335 | 0.64335 | 0.99641 | -0.067941 | 0.9971 | -0.054845 | 44.1861
21 | -0.0025865 | -0.00064824 | 0.0025865 | 0.00064817 | 4.3851e-08 | -6.3899e-08 | 0.0039648 | 0.0039648 | 0.0039648 | 0.97073 | -0.56581 | 0.97074 | -0.56546 | 1.0892
22 | -0.0075488 | -0.0018918 | 0.0075495 | 0.0018921 | 7.2544e-07 | 2.8564e-07 | 0.011571 | 0.011571 | 0.011571 | 0.97074 | -0.56546 | 0.97085 | -0.56344 | 3.1789
23 | 0.056184 | 0.014093 | -0.056154 | -0.014073 | 3.011e-05 | 1.9136e-05 | 0.086067 | 0.086067 | 0.086067 | 0.97142 | -0.55219 | 0.97085 | -0.56344 | 23.6447
24 | 0.51528 | 0.13188 | -0.51502 | -0.13172 | 0.00026094 | 0.00016675 | 0.76771 | 0.76771 | 0.76771 | 1 | 0 | 0.99945 | -0.010464 | 52.7275
25 | 0.48801 | 0.12495 | -0.48775 | -0.12478 | 0.00026153 | 0.0001671 | 0.7275 | 0.7275 | 0.7275 | 0.99945 | -0.010464 | 0.99886 | -0.021535 | 49.9659
26 | 0.47243 | 0.12094 | -0.4718 | -0.12054 | 0.00062871 | 0.00040167 | 0.70469 | 0.70469 | 0.70469 | 0.99886 | -0.021535 | 0.99741 | -0.049053 | 48.399
27 | -0.4436 | -0.11342 | 0.44372 | 0.1135 | 0.00012436 | 7.9433e-05 | 0.66279 | 0.66279 | 0.66279 | 0.9971 | -0.054845 | 0.99741 | -0.049053 | 45.5215

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.54701 | 0.13943

## res_load
| p_mw | q_mvar
0 | 0.011542 | 0.0028927
1 | 0.0062148 | 0.0015576
2 | 0.003459 | 0.0008669
3 | 0.03506 | 0.0087868
4 | 0.032371 | 0.008113
5 | 0.018913 | 0.0047402
6 | 0.01671 | 0.0041879
7 | 0.012778 | 0.0032025
8 | 0.071229 | 0.017852
9 | 0.051447 | 0.012894
10 | 0.0078647 | 0.0019711
11 | 0.017689 | 0.0044332
12 | 0.0025865 | 0.00064824
13 | 0.0049623 | 0.0012437
14 | 0.048604 | 0.012181
15 | 0.030086 | 0.0075402
16 | 0.027007 | 0.0067687
17 | 0.083328 | 0.020884
18 | 0.015315 | 0.0038382
19 | 0.013029 | 0.0032653
20 | 0.028083 | 0.0070383

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1