## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_121-43_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_121-43_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_121-43_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_121-43_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_121-43_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_121-43_0_2_node_20 | 0.4 | n |  | TRUE
6 | bus_LV_121-43_0_2_node_43 | 0.4 | n |  | TRUE
7 | bus_LV_121-43_0_2_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_121-43_0_2_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_121-43_0_2_node_21 | 0.4 | n |  | TRUE
10 | bus_LV_121-43_0_2_node_24 | 0.4 | n |  | TRUE
11 | bus_LV_121-43_0_2_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_121-43_0_2_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_121-43_0_2_node_13 | 0.4 | n |  | TRUE
14 | bus_LV_121-43_0_2_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_121-43_0_2_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_121-43_0_2_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_121-43_0_2_node_115 | 0.4 | n |  | TRUE
18 | bus_LV_121-43_0_2_node_129 | 0.4 | n |  | TRUE
19 | bus_LV_121-43_0_2_node_37 | 0.4 | n |  | TRUE
20 | bus_LV_121-43_0_2_node_130 | 0.4 | n |  | TRUE
21 | bus_LV_121-43_0_2_node_127 | 0.4 | n |  | TRUE
22 | bus_LV_121-43_0_2_node_138 | 0.4 | n |  | TRUE
23 | bus_LV_121-43_0_2_node_29 | 0.4 | n |  | TRUE
24 | bus_LV_121-43_0_2_node_23 | 0.4 | n |  | TRUE
25 | bus_LV_121-43_0_2_node_22 | 0.4 | n |  | TRUE
26 | bus_LV_121-43_0_2_node_72 | 0.4 | n |  | TRUE
27 | bus_LV_121-43_0_2_node_25 | 0.4 | n |  | TRUE
28 | bus_LV_121-43_0_2_node_26 | 0.4 | n |  | TRUE
29 | bus_LV_121-43_0_2_node_27 | 0.4 | n |  | TRUE
30 | bus_LV_121-43_0_2_node_28 | 0.4 | n |  | TRUE
31 | bus_LV_121-43_0_2_node_110 | 0.4 | n |  | TRUE
32 | bus_LV_121-43_0_2_node_132 | 0.4 | n |  | TRUE
33 | bus_LV_121-43_0_2_node_131 | 0.4 | n |  | TRUE
34 | bus_LV_121-43_0_2_node_133 | 0.4 | n |  | TRUE
35 | bus_LV_121-43_0_2_node_35 | 0.4 | n |  | TRUE
36 | bus_LV_121-43_0_2_node_86 | 0.4 | n |  | TRUE
37 | bus_LV_121-43_0_2_node_38 | 0.4 | n |  | TRUE
38 | bus_LV_121-43_0_2_node_39 | 0.4 | n |  | TRUE
39 | bus_LV_121-43_0_2_node_40 | 0.4 | n |  | TRUE
40 | bus_LV_121-43_0_2_node_41 | 0.4 | n |  | TRUE
41 | bus_LV_121-43_0_2_node_42 | 0.4 | n |  | TRUE
42 | bus_LV_121-43_0_2_node_82 | 0.4 | n |  | TRUE
43 | bus_LV_121-43_0_2_node_83 | 0.4 | n |  | TRUE
44 | bus_LV_121-43_0_2_node_88 | 0.4 | n |  | TRUE
45 | bus_LV_121-43_0_2_node_84 | 0.4 | n |  | TRUE
46 | bus_LV_121-43_0_2_node_85 | 0.4 | n |  | TRUE
47 | bus_LV_121-43_0_2_node_87 | 0.4 | n |  | TRUE
48 | bus_LV_121-43_0_2_node_89 | 0.4 | n |  | TRUE
49 | bus_LV_121-43_0_2_node_90 | 0.4 | n |  | TRUE
50 | bus_LV_121-43_0_2_node_111 | 0.4 | n |  | TRUE
51 | bus_LV_121-43_0_2_node_112 | 0.4 | n |  | TRUE
52 | bus_LV_121-43_0_2_node_113 | 0.4 | n |  | TRUE
53 | bus_LV_121-43_0_2_node_114 | 0.4 | n |  | TRUE
54 | bus_LV_121-43_0_2_node_122 | 0.4 | n |  | TRUE
55 | bus_LV_121-43_0_2_node_123 | 0.4 | n |  | TRUE
56 | bus_MV_6_0_node_94 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_121-43_0_2_load_0 | 0 | 0.083013 | 0.020805 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_121-43_0_2_load_43 | 6 | 0.039584 | 0.0099208 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_121-43_0_2_load_6 | 7 | 0.019653 | 0.0049256 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_121-43_0_2_load_21 | 9 | 0.0023242 | 0.0005825 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_121-43_0_2_load_24 | 10 | 0.0036758 | 0.00092124 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_121-43_0_2_load_7 | 11 | 0.010444 | 0.0026176 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_121-43_0_2_load_13 | 13 | 0.0010455 | 0.00026203 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_121-43_0_2_load_9 | 14 | 0.031914 | 0.0079984 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_121-43_0_2_load_12 | 16 | 0.0010073 | 0.00025246 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_121-43_0_2_load_115 | 17 | 0.00096094 | 0.00024083 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_121-43_0_2_load_129 | 18 | 0.0025293 | 0.00063391 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_121-43_0_2_load_130 | 20 | 0.0017037 | 0.00042699 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_121-43_0_2_load_127 | 21 | 0.0012617 | 0.0003162 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_121-43_0_2_load_138 | 22 | 0.0018146 | 0.00045477 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_121-43_0_2_load_22 | 25 | 0.014752 | 0.0036973 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_121-43_0_2_load_72 | 26 | 0.00097056 | 0.00024325 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_121-43_0_2_load_25 | 27 | 0.0032909 | 0.00082479 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_121-43_0_2_load_26 | 28 | 0.0018931 | 0.00047445 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_121-43_0_2_load_110 | 31 | 0.0021664 | 0.00054294 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_121-43_0_2_load_132 | 32 | 0.0024598 | 0.00061648 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_121-43_0_2_load_131 | 33 | 0.0016109 | 0.00040373 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_121-43_0_2_load_133 | 34 | 0.0022431 | 0.00056217 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_121-43_0_2_load_38 | 37 | 0.0049553 | 0.0012419 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_121-43_0_2_load_39 | 38 | 0.016482 | 0.0041308 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_121-43_0_2_load_41 | 40 | 0.0012987 | 0.00032549 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_121-43_0_2_load_42 | 41 | 0.00084919 | 0.00021283 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_121-43_0_2_load_82 | 42 | 0.0011843 | 0.00029682 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_121-43_0_2_load_88 | 44 | 0.0028504 | 0.00071439 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_121-43_0_2_load_84 | 45 | 0.00088135 | 0.00022089 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_121-43_0_2_load_85 | 46 | 0.00095395 | 0.00023908 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_121-43_0_2_load_87 | 47 | 0.00053961 | 0.00013524 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_121-43_0_2_load_89 | 48 | 0.0014774 | 0.00037027 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_121-43_0_2_load_90 | 49 | 0.0010443 | 0.00026171 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_121-43_0_2_load_111 | 50 | 0.0020339 | 0.00050976 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_121-43_0_2_load_112 | 51 | 0.0021664 | 0.00054294 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_121-43_0_2_load_113 | 52 | 0.001277 | 0.00032006 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_121-43_0_2_load_114 | 53 | 0.0010929 | 0.00027389 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_121-43_0_2_load_122 | 54 | 0.0066671 | 0.0016709 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_121-43_0_2_load_123 | 55 | 0.0074102 | 0.0018572 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 0 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_121-43_0_2_line_0 |  | 0 | 1 | 0.046369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_121-43_0_2_line_1 |  | 0 | 2 | 0.061232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_121-43_0_2_line_2 |  | 1 | 3 | 0.03657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_121-43_0_2_line_3 |  | 2 | 4 | 0.016534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_121-43_0_2_line_4 |  | 3 | 5 | 0.051167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_121-43_0_2_line_5 |  | 3 | 6 | 0.02115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_121-43_0_2_line_6 |  | 4 | 7 | 0.0080324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_121-43_0_2_line_7 |  | 5 | 24 | 0.046016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_121-43_0_2_line_8 |  | 5 | 25 | 0.051859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_121-43_0_2_line_9 |  | 6 | 39 | 0.037622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_121-43_0_2_line_10 |  | 7 | 11 | 0.014343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_121-43_0_2_line_11 |  | 8 | 9 | 0.029554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_121-43_0_2_line_12 |  | 8 | 10 | 0.040545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_121-43_0_2_line_13 |  | 9 | 12 | 0.0040752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_121-43_0_2_line_14 |  | 10 | 27 | 0.015463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_121-43_0_2_line_15 |  | 11 | 12 | 0.026628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_121-43_0_2_line_16 |  | 12 | 13 | 0.0065885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_121-43_0_2_line_17 |  | 13 | 15 | 0.026223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_121-43_0_2_line_18 |  | 14 | 15 | 0.018977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_121-43_0_2_line_19 |  | 15 | 16 | 0.013797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_121-43_0_2_line_20 |  | 16 | 17 | 0.014792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_121-43_0_2_line_21 |  | 17 | 53 | 0.0060596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_121-43_0_2_line_22 |  | 18 | 19 | 0.013799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_121-43_0_2_line_23 |  | 19 | 20 | 0.01858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_121-43_0_2_line_24 |  | 19 | 35 | 0.011575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_121-43_0_2_line_25 |  | 20 | 21 | 0.027693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_121-43_0_2_line_26 |  | 21 | 55 | 0.029947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_121-43_0_2_line_27 |  | 22 | 23 | 0.058679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_121-43_0_2_line_28 |  | 23 | 30 | 0.18818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_121-43_0_2_line_29 |  | 24 | 26 | 0.01189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_121-43_0_2_line_30 |  | 27 | 28 | 0.019349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_121-43_0_2_line_31 |  | 28 | 29 | 0.01003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_121-43_0_2_line_32 |  | 29 | 30 | 0.13047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_121-43_0_2_line_33 |  | 30 | 31 | 0.073349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_121-43_0_2_line_34 |  | 31 | 50 | 0.01461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_121-43_0_2_line_35 |  | 32 | 33 | 0.0080913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_121-43_0_2_line_36 |  | 32 | 34 | 0.012472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_121-43_0_2_line_37 |  | 34 | 35 | 0.094631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_121-43_0_2_line_38 |  | 35 | 36 | 0.016347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_121-43_0_2_line_39 |  | 36 | 47 | 0.017665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_121-43_0_2_line_40 |  | 36 | 45 | 0.0046632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_121-43_0_2_line_41 |  | 37 | 38 | 0.00932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_121-43_0_2_line_42 |  | 37 | 39 | 0.024102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_121-43_0_2_line_43 |  | 38 | 40 | 0.022513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_121-43_0_2_line_44 |  | 39 | 41 | 0.019805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_121-43_0_2_line_45 |  | 40 | 42 | 0.0080321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_121-43_0_2_line_46 |  | 41 | 43 | 0.0128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_121-43_0_2_line_47 |  | 42 | 44 | 0.061329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_121-43_0_2_line_48 |  | 43 | 45 | 0.023887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_121-43_0_2_line_49 |  | 43 | 46 | 0.021484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_121-43_0_2_line_50 |  | 47 | 48 | 0.0079906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_121-43_0_2_line_51 |  | 48 | 49 | 0.0079832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_121-43_0_2_line_52 |  | 50 | 51 | 0.007028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_121-43_0_2_line_53 |  | 52 | 53 | 0.0091104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_121-43_0_2_line_54 |  | 54 | 55 | 0.037165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_121-43_0_2_trafo_0 | 0.63 MVA 20/0.4 kV | 56 | 0 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19
0 | 2704026.2909 | 1243453.5147 | 2704030.9318 | 1243458.7223 | 2704057.1285 | 1243488.1425
1 | 2704032.5873 | 1243530.2405 | 2704067.0423 | 1243499.2761 | 2704057.1285 | 1243488.1425
2 | 2704001.7455 | 1243426.341 | 2704026.2909 | 1243453.5147
3 | 2704019.927 | 1243540.9158 | 2704032.5873 | 1243530.2405
4 | 2703968.4497 | 1243464.921 | 2703976.9215 | 1243452.9823 | 2703993.2359 | 1243433.5308 | 2704001.7455 | 1243426.341
5 | 2704001.7455 | 1243426.341 | 2704018.0989 | 1243412.928
6 | 2704019.927 | 1243540.9158 | 2704020.8809 | 1243545.1469 | 2704021.8248 | 1243548.7194
7 | 2703954.5686 | 1243430.9624 | 2703976.9215 | 1243452.9823 | 2703968.4497 | 1243464.921
8 | 2703968.4497 | 1243464.921 | 2703996.8007 | 1243480.6968 | 2703997.4154 | 1243500.1014
9 | 2704049.7164 | 1243394.1458 | 2704041.2253 | 1243395.965 | 2704033.9335 | 1243399.2285 | 2704027.9076 | 1243404.8829 | 2704018.0989 | 1243412.928
10 | 2704021.8248 | 1243548.7194 | 2704023.5108 | 1243555.1008 | 2704026.4564 | 1243562.2611
11 | 2704065.3006 | 1243562.7617 | 2704059.2214 | 1243568.4484 | 2704051.5046 | 1243572.2494 | 2704050.4405 | 1243573.4428 | 2704043.1037 | 1243581.6772
12 | 2704065.3006 | 1243562.7617 | 2704074.193 | 1243554.4334 | 2704077.2493 | 1243548.7048 | 2704083.6204 | 1243542.7563 | 2704093.2304 | 1243533.7773
13 | 2704040.3927 | 1243584.7199 | 2704043.1037 | 1243581.6772
14 | 2704104.5293 | 1243523.2202 | 2704093.2304 | 1243533.7773
15 | 2704040.3927 | 1243584.7199 | 2704035.6216 | 1243578.7538 | 2704030.7719 | 1243571.2407 | 2704029.6299 | 1243569.9752 | 2704026.4564 | 1243562.2611
16 | 2704040.3927 | 1243584.7199 | 2704035.6615 | 1243589.305
17 | 2704018.0949 | 1243608.7255 | 2704028.2885 | 1243596.4501 | 2704035.6615 | 1243589.305
18 | 2704018.0949 | 1243608.7255 | 2704017.7472 | 1243609.153 | 2704012.1674 | 1243616.1051 | 2704006.2123 | 1243623.5219
19 | 2704018.0949 | 1243608.7255 | 2704018.5914 | 1243611.4474 | 2704019.2124 | 1243614.8276 | 2704019.2139 | 1243622.4206
20 | 2704019.2139 | 1243622.4206 | 2704019.2154 | 1243629.7393 | 2704019.4366 | 1243637.209
21 | 2704019.6159 | 1243643.266 | 2704019.4366 | 1243637.209
22 | 2704072.303 | 1243329.1912 | 2704085.5557 | 1243325.3462
23 | 2704072.303 | 1243329.1912 | 2704054.1007 | 1243332.919
24 | 2704072.303 | 1243329.1912 | 2704073.597 | 1243334.7182 | 2704075.1982 | 1243340.3951
25 | 2704026.587 | 1243335.8385 | 2704035.5166 | 1243335.2842 | 2704050.7485 | 1243333.6055 | 2704054.1007 | 1243332.919
26 | 2704026.587 | 1243335.8385 | 2704018.3375 | 1243336.3505 | 2704003.9256 | 1243336.0977 | 2703996.6791 | 1243335.5454
27 | 2704204.3776 | 1243613.9646 | 2704202.5283 | 1243619.4031 | 2704156.0137 | 1243644.9175
28 | 2704185.0031 | 1243512.434 | 2704191.2368 | 1243507.0059 | 2704200.5937 | 1243498.9306 | 2704203.635 | 1243505.2445 | 2704200.1256 | 1243507.9294 | 2704217.2767 | 1243526.067 | 2704226.3483 | 1243535.5115 | 2704229.0552 | 1243538.4835 | 2704230.1231 | 1243539.6588 | 2704230.5035 | 1243540.8108 | 2704233.3224 | 1243545.5863 | 2704239.3743 | 1243555.656 | 2704246.1479 | 1243566.3834 | 2704215.6729 | 1243584.1953 | 2704216.8437 | 1243586.3954 | 2704219.8368 | 1243592.0079 | 2704222.9253 | 1243597.7889 | 2704225.2744 | 1243602.1891 | 2704226.0135 | 1243603.581 | 2704204.3776 | 1243613.9646
29 | 2703954.5686 | 1243430.9624 | 2703950.0867 | 1243441.9749
30 | 2704104.5293 | 1243523.2202 | 2704118.667 | 1243510.0107
31 | 2704126.5389 | 1243503.8011 | 2704119.3195 | 1243509.401 | 2704118.667 | 1243510.0107
32 | 2704126.5389 | 1243503.8011 | 2704135.8313 | 1243508.0008 | 2704144.0716 | 1243502.808 | 2704182.2545 | 1243466.6612 | 2704191.6327 | 1243479.3135 | 2704193.0843 | 1243481.8854 | 2704200.5937 | 1243498.9306 | 2704191.2368 | 1243507.0059 | 2704185.0031 | 1243512.434
33 | 2704185.0031 | 1243512.434 | 2704194.314 | 1243522.4609 | 2704151.098 | 1243563.6
34 | 2704151.098 | 1243563.6 | 2704140.5159 | 1243573.6735
35 | 2703960.5597 | 1243342.5063 | 2703968.6224 | 1243343.1856
36 | 2703981.0546 | 1243344.1849 | 2703973.9404 | 1243343.6337 | 2703968.6224 | 1243343.1856
37 | 2704075.1982 | 1243340.3951 | 2704062.3169 | 1243342.9601 | 2704051.2924 | 1243344.4013 | 2704039.826 | 1243345.6011 | 2704029.2657 | 1243346.0052 | 2704016.4029 | 1243346.2243 | 2704005.4837 | 1243345.9661 | 2703988.7825 | 1243344.7836 | 2703981.0546 | 1243344.1849
38 | 2704077.9549 | 1243356.4782 | 2704077.568 | 1243354.4032 | 2704076.3203 | 1243344.518 | 2704075.1982 | 1243340.3951
39 | 2704077.9549 | 1243356.4782 | 2704094.6484 | 1243354.2249 | 2704095.4652 | 1243354.15
40 | 2704077.9549 | 1243356.4782 | 2704073.3031 | 1243356.8035
41 | 2704059.0171 | 1243423.5692 | 2704052.468 | 1243416.9382
42 | 2704049.7164 | 1243394.1458 | 2704049.2897 | 1243413.7202 | 2704052.468 | 1243416.9382
43 | 2704059.0171 | 1243423.5692 | 2704062.3994 | 1243426.9938 | 2704074.4275 | 1243439.9783
44 | 2704049.7164 | 1243394.1458 | 2704050.1902 | 1243382.2225 | 2704049.8867 | 1243374.3562
45 | 2704074.4275 | 1243439.9783 | 2704079.8859 | 1243445.8707
46 | 2704050.859 | 1243361.7739 | 2704049.7433 | 1243364.6121 | 2704049.6394 | 1243367.9462 | 2704049.8867 | 1243374.3562
47 | 2704105.3931 | 1243474.6406 | 2704108.2557 | 1243477.7933 | 2704100.7126 | 1243484.1771 | 2704079.2677 | 1243460.8494 | 2704077.7206 | 1243457.2528 | 2704079.8859 | 1243445.8707
48 | 2704050.859 | 1243361.7739 | 2704052.9589 | 1243359.2865 | 2704056.217 | 1243357.9982 | 2704073.3031 | 1243356.8035
49 | 2704050.859 | 1243361.7739 | 2704046.6903 | 1243361.1002 | 2704029.4962 | 1243362.6187
50 | 2704095.4652 | 1243354.15 | 2704102.0839 | 1243353.5437 | 2704103.428 | 1243353.5294
51 | 2704111.4108 | 1243353.4448 | 2704103.428 | 1243353.5294
52 | 2704140.5159 | 1243573.6735 | 2704135.4255 | 1243578.5192
53 | 2704019.8856 | 1243652.3724 | 2704019.6159 | 1243643.266
54 | 2703959.6099 | 1243332.8795 | 2703980.6201 | 1243334.3213 | 2703996.6791 | 1243335.5454

## bus_geodata
| x | y | coords
0 | 2704057.1285 | 1243488.1425
1 | 2704026.2909 | 1243453.5147
2 | 2704032.5873 | 1243530.2405
3 | 2704001.7455 | 1243426.341
4 | 2704019.927 | 1243540.9158
5 | 2703968.4497 | 1243464.921
6 | 2704018.0989 | 1243412.928
7 | 2704021.8248 | 1243548.7194
8 | 2704065.3006 | 1243562.7617
9 | 2704043.1037 | 1243581.6772
10 | 2704093.2304 | 1243533.7773
11 | 2704026.4564 | 1243562.2611
12 | 2704040.3927 | 1243584.7199
13 | 2704035.6615 | 1243589.305
14 | 2704006.2123 | 1243623.5219
15 | 2704018.0949 | 1243608.7255
16 | 2704019.2139 | 1243622.4206
17 | 2704019.4366 | 1243637.209
18 | 2704085.5557 | 1243325.3462
19 | 2704072.303 | 1243329.1912
20 | 2704054.1007 | 1243332.919
21 | 2704026.587 | 1243335.8385
22 | 2704156.0137 | 1243644.9175
23 | 2704204.3776 | 1243613.9646
24 | 2703954.5686 | 1243430.9624
25 | 2703997.4154 | 1243500.1014
26 | 2703950.0867 | 1243441.9749
27 | 2704104.5293 | 1243523.2202
28 | 2704118.667 | 1243510.0107
29 | 2704126.5389 | 1243503.8011
30 | 2704185.0031 | 1243512.434
31 | 2704151.098 | 1243563.6
32 | 2703968.6224 | 1243343.1856
33 | 2703960.5597 | 1243342.5063
34 | 2703981.0546 | 1243344.1849
35 | 2704075.1982 | 1243340.3951
36 | 2704077.9549 | 1243356.4782
37 | 2704052.468 | 1243416.9382
38 | 2704059.0171 | 1243423.5692
39 | 2704049.7164 | 1243394.1458
40 | 2704074.4275 | 1243439.9783
41 | 2704049.8867 | 1243374.3562
42 | 2704079.8859 | 1243445.8707
43 | 2704050.859 | 1243361.7739
44 | 2704105.3931 | 1243474.6406
45 | 2704073.3031 | 1243356.8035
46 | 2704029.4962 | 1243362.6187
47 | 2704095.4652 | 1243354.15
48 | 2704103.428 | 1243353.5294
49 | 2704111.4108 | 1243353.4448
50 | 2704140.5159 | 1243573.6735
51 | 2704135.4255 | 1243578.5192
52 | 2704019.8856 | 1243652.3724
53 | 2704019.6159 | 1243643.266
54 | 2703959.6099 | 1243332.8795
55 | 2703996.6791 | 1243335.5454
56 | 2704057.1285 | 1243488.1425

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 1 | 0 | -0.2042 | -0.051553
1 | 0.99515 | -0.092366 | 0 | 0
2 | 0.99513 | -0.093074 | 0 | 0
3 | 0.99133 | -0.16585 | 0 | 0
4 | 0.99382 | -0.11836 | 0 | 0
5 | 0.9906 | -0.18013 | 0 | 0
6 | 0.98943 | -0.20268 | 0.039584 | 0.0099208
7 | 0.99318 | -0.13067 | 0.019653 | 0.0049256
8 | 0.99038 | -0.18481 | 0 | 0
9 | 0.99085 | -0.17586 | 0.0023242 | 0.0005825
10 | 0.98975 | -0.19711 | 0.0036758 | 0.00092124
11 | 0.9923 | -0.1477 | 0.010444 | 0.0026176
12 | 0.99092 | -0.17445 | 0 | 0
13 | 0.99069 | -0.17882 | 0.0010455 | 0.00026203
14 | 0.98927 | -0.2065 | 0.031914 | 0.0079984
15 | 0.98982 | -0.19572 | 0 | 0
16 | 0.98977 | -0.19678 | 0.0010073 | 0.00025246
17 | 0.98972 | -0.19766 | 0.00096094 | 0.00024083
18 | 0.98506 | -0.28765 | 0.0025293 | 0.00063391
19 | 0.98509 | -0.28702 | 0 | 0
20 | 0.9848 | -0.29271 | 0.0017037 | 0.00042699
21 | 0.98441 | -0.30035 | 0.0012617 | 0.0003162
22 | 0.98792 | -0.23281 | 0.0018146 | 0.00045477
23 | 0.98801 | -0.2309 | 0 | 0
24 | 0.99056 | -0.18093 | 0 | 0
25 | 0.9899 | -0.19373 | 0.014752 | 0.0036973
26 | 0.99055 | -0.18113 | 0.00097056 | 0.00024325
27 | 0.98956 | -0.20079 | 0.0032909 | 0.00082479
28 | 0.98938 | -0.20427 | 0.0018931 | 0.00047445
29 | 0.98931 | -0.20573 | 0 | 0
30 | 0.98833 | -0.22479 | 0 | 0
31 | 0.9879 | -0.23313 | 0.0021664 | 0.00054294
32 | 0.9847 | -0.2946 | 0.0024598 | 0.00061648
33 | 0.98469 | -0.29484 | 0.0016109 | 0.00040373
34 | 0.98475 | -0.29369 | 0.0022431 | 0.00056217
35 | 0.9853 | -0.28295 | 0 | 0
36 | 0.98569 | -0.27536 | 0 | 0
37 | 0.98682 | -0.25344 | 0.0049553 | 0.0012419
38 | 0.98663 | -0.25708 | 0.016482 | 0.0041308
39 | 0.98741 | -0.24189 | 0 | 0
40 | 0.98652 | -0.25923 | 0.0012987 | 0.00032549
41 | 0.98683 | -0.2531 | 0.00084919 | 0.00021283
42 | 0.98649 | -0.25981 | 0.0011843 | 0.00029682
43 | 0.98647 | -0.26016 | 0 | 0
44 | 0.98633 | -0.26294 | 0.0028504 | 0.00071439
45 | 0.98581 | -0.27293 | 0.00088135 | 0.00022089
46 | 0.98645 | -0.26053 | 0.00095395 | 0.00023908
47 | 0.98564 | -0.27633 | 0.00053961 | 0.00013524
48 | 0.98562 | -0.27669 | 0.0014774 | 0.00037027
49 | 0.98561 | -0.27684 | 0.0010443 | 0.00026171
50 | 0.98784 | -0.23423 | 0.0020339 | 0.00050976
51 | 0.98783 | -0.2345 | 0.0021664 | 0.00054294
52 | 0.9897 | -0.19812 | 0.001277 | 0.00032006
53 | 0.98971 | -0.19791 | 0.0010929 | 0.00027389
54 | 0.98379 | -0.3124 | 0.0066671 | 0.0016709
55 | 0.98402 | -0.30794 | 0.0074102 | 0.0018572
56 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.11503 | 0.029332 | -0.11452 | -0.029005 | 0.00051048 | 0.0003261 | 0.17134 | 0.17134 | 0.17134 | 1 | 0 | 0.99515 | -0.092366 | 47.0718
1 | 0.087522 | 0.022221 | -0.087132 | -0.021972 | 0.00039006 | 0.00024884 | 0.13034 | 0.13034 | 0.13034 | 1 | 0 | 0.99513 | -0.093074 | 35.8065
2 | 0.11452 | 0.029005 | -0.11411 | -0.028748 | 0.00040261 | 0.0002572 | 0.17134 | 0.17134 | 0.17134 | 0.99515 | -0.092366 | 0.99133 | -0.16585 | 47.0719
3 | 0.087132 | 0.021972 | -0.087027 | -0.021905 | 0.00010533 | 6.7194e-05 | 0.13034 | 0.13034 | 0.13034 | 0.99513 | -0.093074 | 0.99382 | -0.11836 | 35.8065
4 | 0.015743 | 0.0039515 | -0.015733 | -0.0039453 | 1.0717e-05 | 6.1995e-06 | 0.023633 | 0.023633 | 0.023633 | 0.99133 | -0.16585 | 0.9906 | -0.18013 | 6.4927
5 | 0.098372 | 0.024797 | -0.098199 | -0.024686 | 0.00017305 | 0.00011048 | 0.14771 | 0.14771 | 0.14771 | 0.99133 | -0.16585 | 0.98943 | -0.20268 | 40.5793
6 | 0.087027 | 0.021905 | -0.086976 | -0.021873 | 5.1168e-05 | 3.2644e-05 | 0.13034 | 0.13034 | 0.13034 | 0.99382 | -0.11836 | 0.99318 | -0.13067 | 35.8065
7 | 0.00097061 | 0.00024253 | -0.00097057 | -0.0002431 | 3.6674e-08 | -5.6891e-07 | 0.0014577 | 0.0014579 | 0.0014579 | 0.9906 | -0.18013 | 0.99056 | -0.18093 | 0.40053
8 | 0.014762 | 0.0037027 | -0.014752 | -0.0036973 | 9.5633e-06 | 5.4534e-06 | 0.022176 | 0.022176 | 0.022176 | 0.9906 | -0.18013 | 0.9899 | -0.19373 | 6.0922
9 | 0.058614 | 0.014766 | -0.058505 | -0.014696 | 0.0001097 | 6.9723e-05 | 0.088177 | 0.088178 | 0.088178 | 0.98943 | -0.20268 | 0.98741 | -0.24189 | 24.2246
10 | 0.067322 | 0.016947 | -0.067267 | -0.016912 | 5.4748e-05 | 3.4853e-05 | 0.10089 | 0.10089 | 0.10089 | 0.99318 | -0.13067 | 0.9923 | -0.1477 | 27.7172
11 | -0.017067 | -0.00428 | 0.017074 | 0.0042843 | 7.2875e-06 | 4.2835e-06 | 0.025643 | 0.025643 | 0.025643 | 0.99038 | -0.18481 | 0.99085 | -0.17586 | 7.0447
12 | 0.017067 | 0.00428 | -0.017057 | -0.0042742 | 9.9977e-06 | 5.8771e-06 | 0.025643 | 0.025643 | 0.025643 | 0.99038 | -0.18481 | 0.98975 | -0.19711 | 7.0448
13 | -0.019398 | -0.0048668 | 0.019399 | 0.0048676 | 1.297e-06 | 7.7762e-07 | 0.029133 | 0.029133 | 0.029133 | 0.99085 | -0.17586 | 0.99092 | -0.17445 | 8.0036
14 | 0.013381 | 0.0033529 | -0.013378 | -0.0033516 | 2.3467e-06 | 1.3032e-06 | 0.020117 | 0.020117 | 0.020117 | 0.98975 | -0.19711 | 0.98956 | -0.20079 | 5.5266
15 | 0.056823 | 0.014295 | -0.056751 | -0.014248 | 7.2533e-05 | 4.6078e-05 | 0.085229 | 0.085229 | 0.085229 | 0.9923 | -0.1477 | 0.99092 | -0.17445 | 23.4145
16 | 0.037351 | 0.0093809 | -0.037344 | -0.009376 | 7.7746e-06 | 4.8909e-06 | 0.056096 | 0.056096 | 0.056096 | 0.99092 | -0.17445 | 0.99069 | -0.17882 | 15.411
17 | 0.036298 | 0.0091139 | -0.036269 | -0.0090956 | 2.9236e-05 | 1.8374e-05 | 0.054526 | 0.054526 | 0.054526 | 0.99069 | -0.17882 | 0.98982 | -0.19572 | 14.9796
18 | -0.031914 | -0.0079984 | 0.03193 | 0.0080086 | 1.6399e-05 | 1.0251e-05 | 0.048004 | 0.048004 | 0.048004 | 0.98927 | -0.2065 | 0.98982 | -0.19572 | 13.1878
19 | 0.0043386 | 0.0010869 | -0.0043384 | -0.001087 | 2.2008e-07 | -3.6473e-08 | 0.0065221 | 0.0065222 | 0.0065222 | 0.98982 | -0.19572 | 0.98977 | -0.19678 | 1.7918
20 | 0.003331 | 0.00083452 | -0.0033309 | -0.00083462 | 1.391e-07 | -1.0107e-07 | 0.0050077 | 0.0050078 | 0.0050078 | 0.98977 | -0.19678 | 0.98972 | -0.19766 | 1.3758
21 | 0.0023699 | 0.00059378 | -0.0023699 | -0.00059384 | 2.8849e-08 | -5.9407e-08 | 0.0035631 | 0.0035631 | 0.0035631 | 0.98972 | -0.19766 | 0.98971 | -0.19791 | 0.97887
22 | -0.0025293 | -0.00063391 | 0.0025294 | 0.00063378 | 7.554e-08 | -1.2733e-07 | 0.0038207 | 0.0038207 | 0.0038207 | 0.98506 | -0.28765 | 0.98509 | -0.28702 | 1.0497
23 | 0.017059 | 0.0042806 | -0.017055 | -0.0042778 | 4.6273e-06 | 2.725e-06 | 0.025771 | 0.025771 | 0.025771 | 0.98509 | -0.28702 | 0.9848 | -0.29271 | 7.0799
24 | -0.019589 | -0.0049143 | 0.019593 | 0.0049166 | 3.8008e-06 | 2.2851e-06 | 0.029591 | 0.029591 | 0.029591 | 0.98509 | -0.28702 | 0.9853 | -0.28295 | 8.1295
25 | 0.015351 | 0.0038508 | -0.015345 | -0.0038476 | 5.5878e-06 | 3.224e-06 | 0.023196 | 0.023197 | 0.023197 | 0.9848 | -0.29271 | 0.98441 | -0.30035 | 6.3727
26 | 0.014084 | 0.0035314 | -0.014079 | -0.0035285 | 5.09e-06 | 2.877e-06 | 0.021289 | 0.02129 | 0.02129 | 0.98441 | -0.30035 | 0.98402 | -0.30794 | 5.8488
27 | -0.0018146 | -0.00045477 | 0.0018147 | 0.00045413 | 1.6436e-07 | -6.4622e-07 | 0.0027331 | 0.0027329 | 0.0027331 | 0.98792 | -0.23281 | 0.98801 | -0.2309 | 0.75086
28 | -0.0018147 | -0.00045413 | 0.0018153 | 0.00045205 | 5.2687e-07 | -2.0735e-06 | 0.0027329 | 0.002732 | 0.0027329 | 0.98801 | -0.2309 | 0.98833 | -0.22479 | 0.75079
29 | 0.00097057 | 0.0002431 | -0.00097056 | -0.00024325 | 9.4775e-09 | -1.4698e-07 | 0.0014579 | 0.001458 | 0.001458 | 0.99056 | -0.18093 | 0.99055 | -0.18113 | 0.40055
30 | 0.010087 | 0.0025268 | -0.010086 | -0.002526 | 1.6694e-06 | 8.1987e-07 | 0.015168 | 0.015168 | 0.015168 | 0.98956 | -0.20079 | 0.98938 | -0.20427 | 4.1671
31 | 0.0081927 | 0.0020516 | -0.0081921 | -0.0020513 | 5.7098e-07 | 2.3663e-07 | 0.012321 | 0.012321 | 0.012321 | 0.98938 | -0.20427 | 0.98931 | -0.20573 | 3.3849
32 | 0.0081921 | 0.0020513 | -0.0081847 | -0.0020483 | 7.4279e-06 | 3.0802e-06 | 0.012321 | 0.012322 | 0.012322 | 0.98931 | -0.20573 | 0.98833 | -0.22479 | 3.3851
33 | 0.0063694 | 0.0015962 | -0.0063669 | -0.0015955 | 2.5296e-06 | 6.7941e-07 | 0.0095897 | 0.0095901 | 0.0095901 | 0.98833 | -0.22479 | 0.9879 | -0.23313 | 2.6346
34 | 0.0042006 | 0.0010526 | -0.0042003 | -0.0010526 | 2.1932e-07 | -4.6686e-08 | 0.006327 | 0.0063271 | 0.0063271 | 0.9879 | -0.23313 | 0.98784 | -0.23423 | 1.7382
35 | 0.0016109 | 0.00040364 | -0.0016109 | -0.00040373 | 1.798e-08 | -9.142e-08 | 0.0024343 | 0.0024343 | 0.0024343 | 0.9847 | -0.2946 | 0.98469 | -0.29484 | 0.66876
36 | -0.0040707 | -0.0010201 | 0.0040709 | 0.0010201 | 1.7698e-07 | -4.5404e-08 | 0.0061513 | 0.0061513 | 0.0061513 | 0.9847 | -0.2946 | 0.98475 | -0.29369 | 1.6899
37 | -0.006314 | -0.0015822 | 0.0063172 | 0.0015831 | 3.23e-06 | 8.6264e-07 | 0.0095407 | 0.0095403 | 0.0095407 | 0.98475 | -0.29369 | 0.9853 | -0.28295 | 2.6211
38 | -0.02591 | -0.0064997 | 0.025919 | 0.0065055 | 9.3869e-06 | 5.7993e-06 | 0.039132 | 0.039132 | 0.039132 | 0.9853 | -0.28295 | 0.98569 | -0.27536 | 10.7504
39 | 0.0030615 | 0.00076692 | -0.0030613 | -0.00076705 | 1.4149e-07 | -1.346e-07 | 0.0046215 | 0.0046216 | 0.0046216 | 0.98569 | -0.27536 | 0.98564 | -0.27633 | 1.2697
40 | -0.028981 | -0.0072724 | 0.028984 | 0.0072745 | 3.3476e-06 | 2.083e-06 | 0.043753 | 0.043753 | 0.043753 | 0.98569 | -0.27536 | 0.98581 | -0.27293 | 12.0201
41 | 0.02182 | 0.0054693 | -0.021817 | -0.005467 | 3.7838e-06 | 2.3026e-06 | 0.032903 | 0.032903 | 0.032903 | 0.98682 | -0.25344 | 0.98663 | -0.25708 | 9.0394
42 | -0.026776 | -0.0067112 | 0.026791 | 0.0067204 | 1.4734e-05 | 9.1215e-06 | 0.040375 | 0.040375 | 0.040375 | 0.98682 | -0.25344 | 0.98741 | -0.24189 | 11.0921
43 | 0.0053346 | 0.0013362 | -0.005334 | -0.0013362 | 5.4644e-07 | 6.225e-08 | 0.0080453 | 0.0080454 | 0.0080454 | 0.98663 | -0.25708 | 0.98652 | -0.25923 | 2.2103
44 | 0.031714 | 0.0079755 | -0.031697 | -0.0079649 | 1.6971e-05 | 1.0608e-05 | 0.047802 | 0.047803 | 0.047803 | 0.98741 | -0.24189 | 0.98683 | -0.2531 | 13.1326
45 | 0.0040353 | 0.0010107 | -0.0040352 | -0.0010107 | 1.1158e-07 | -3.1139e-08 | 0.0060864 | 0.0060864 | 0.0060864 | 0.98652 | -0.25923 | 0.98649 | -0.25981 | 1.6721
46 | 0.030848 | 0.0077521 | -0.030837 | -0.0077456 | 1.0389e-05 | 6.4854e-06 | 0.046522 | 0.046522 | 0.046522 | 0.98683 | -0.2531 | 0.98647 | -0.26016 | 12.7808
47 | 0.0028509 | 0.00071388 | -0.0028504 | -0.00071439 | 4.2527e-07 | -5.1069e-07 | 0.0043 | 0.0043003 | 0.0043003 | 0.98649 | -0.25981 | 0.98633 | -0.26294 | 1.1814
48 | 0.029884 | 0.0075068 | -0.029865 | -0.0074954 | 1.8206e-05 | 1.1347e-05 | 0.045083 | 0.045083 | 0.045083 | 0.98647 | -0.26016 | 0.98581 | -0.27293 | 12.3855
49 | 0.00095397 | 0.00023882 | -0.00095395 | -0.00023908 | 1.6681e-08 | -2.6359e-07 | 0.0014389 | 0.001439 | 0.001439 | 0.98647 | -0.26016 | 0.98645 | -0.26053 | 0.39533
50 | 0.0025217 | 0.00063181 | -0.0025217 | -0.00063189 | 4.3428e-08 | -7.4046e-08 | 0.0038069 | 0.003807 | 0.003807 | 0.98564 | -0.27633 | 0.98562 | -0.27669 | 1.0459
51 | 0.0010443 | 0.00026162 | -0.0010443 | -0.00026171 | 7.4406e-09 | -9.698e-08 | 0.0015765 | 0.0015765 | 0.0015765 | 0.98562 | -0.27669 | 0.98561 | -0.27684 | 0.43312
52 | 0.0021664 | 0.00054287 | -0.0021664 | -0.00054294 | 2.8066e-08 | -7.2011e-08 | 0.0032633 | 0.0032633 | 0.0032633 | 0.98784 | -0.23423 | 0.98783 | -0.2345 | 0.89651
53 | -0.001277 | -0.00032006 | 0.0012771 | 0.00031995 | 1.2594e-08 | -1.0901e-07 | 0.00192 | 0.00192 | 0.00192 | 0.9897 | -0.19812 | 0.98971 | -0.19791 | 0.52748
54 | -0.0066671 | -0.0016709 | 0.0066685 | 0.0016714 | 1.4172e-06 | 4.3502e-07 | 0.010084 | 0.010084 | 0.010084 | 0.98379 | -0.3124 | 0.98402 | -0.30794 | 2.7704

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.28721 | 0.072358

## res_load
| p_mw | q_mvar
0 | 0.083013 | 0.020805
1 | 0.039584 | 0.0099208
2 | 0.019653 | 0.0049256
3 | 0.0023242 | 0.0005825
4 | 0.0036758 | 0.00092124
5 | 0.010444 | 0.0026176
6 | 0.0010455 | 0.00026203
7 | 0.031914 | 0.0079984
8 | 0.0010073 | 0.00025246
9 | 0.00096094 | 0.00024083
10 | 0.0025293 | 0.00063391
11 | 0.0017037 | 0.00042699
12 | 0.0012617 | 0.0003162
13 | 0.0018146 | 0.00045477
14 | 0.014752 | 0.0036973
15 | 0.00097056 | 0.00024325
16 | 0.0032909 | 0.00082479
17 | 0.0018931 | 0.00047445
18 | 0.0021664 | 0.00054294
19 | 0.0024598 | 0.00061648
20 | 0.0016109 | 0.00040373
21 | 0.0022431 | 0.00056217
22 | 0.0049553 | 0.0012419
23 | 0.016482 | 0.0041308
24 | 0.0012987 | 0.00032549
25 | 0.00084919 | 0.00021283
26 | 0.0011843 | 0.00029682
27 | 0.0028504 | 0.00071439
28 | 0.00088135 | 0.00022089
29 | 0.00095395 | 0.00023908
30 | 0.00053961 | 0.00013524
31 | 0.0014774 | 0.00037027
32 | 0.0010443 | 0.00026171
33 | 0.0020339 | 0.00050976
34 | 0.0021664 | 0.00054294
35 | 0.001277 | 0.00032006
36 | 0.0010929 | 0.00027389
37 | 0.0066671 | 0.0016709
38 | 0.0074102 | 0.0018572

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1