## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_121-9_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_121-9_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_121-9_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_121-9_0_4_node_136 | 0.4 | n |  | TRUE
4 | bus_LV_121-9_0_4_node_134 | 0.4 | n |  | TRUE
5 | bus_LV_121-9_0_4_node_109 | 0.4 | n |  | TRUE
6 | bus_LV_121-9_0_4_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_121-9_0_4_node_135 | 0.4 | n |  | TRUE
8 | bus_LV_121-9_0_4_node_42 | 0.4 | n |  | TRUE
9 | bus_LV_121-9_0_4_node_3 | 0.4 | n |  | TRUE
10 | bus_LV_121-9_0_4_node_4 | 0.4 | n |  | TRUE
11 | bus_LV_121-9_0_4_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_121-9_0_4_node_89 | 0.4 | n |  | TRUE
13 | bus_LV_121-9_0_4_node_90 | 0.4 | n |  | TRUE
14 | bus_LV_121-9_0_4_node_107 | 0.4 | n |  | TRUE
15 | bus_LV_121-9_0_4_node_106 | 0.4 | n |  | TRUE
16 | bus_LV_121-9_0_4_node_7 | 0.4 | n |  | TRUE
17 | bus_LV_121-9_0_4_node_8 | 0.4 | n |  | TRUE
18 | bus_LV_121-9_0_4_node_9 | 0.4 | n |  | TRUE
19 | bus_LV_121-9_0_4_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_121-9_0_4_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_121-9_0_4_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_121-9_0_4_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_121-9_0_4_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_121-9_0_4_node_24 | 0.4 | n |  | TRUE
25 | bus_LV_121-9_0_4_node_43 | 0.4 | n |  | TRUE
26 | bus_LV_121-9_0_4_node_28 | 0.4 | n |  | TRUE
27 | bus_LV_121-9_0_4_node_26 | 0.4 | n |  | TRUE
28 | bus_LV_121-9_0_4_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_121-9_0_4_node_29 | 0.4 | n |  | TRUE
30 | bus_LV_121-9_0_4_node_15 | 0.4 | n |  | TRUE
31 | bus_LV_121-9_0_4_node_16 | 0.4 | n |  | TRUE
32 | bus_LV_121-9_0_4_node_17 | 0.4 | n |  | TRUE
33 | bus_LV_121-9_0_4_node_18 | 0.4 | n |  | TRUE
34 | bus_LV_121-9_0_4_node_19 | 0.4 | n |  | TRUE
35 | bus_LV_121-9_0_4_node_21 | 0.4 | n |  | TRUE
36 | bus_LV_121-9_0_4_node_25 | 0.4 | n |  | TRUE
37 | bus_LV_121-9_0_4_node_23 | 0.4 | n |  | TRUE
38 | bus_LV_121-9_0_4_node_30 | 0.4 | n |  | TRUE
39 | bus_LV_121-9_0_4_node_31 | 0.4 | n |  | TRUE
40 | bus_LV_121-9_0_4_node_60 | 0.4 | n |  | TRUE
41 | bus_LV_121-9_0_4_node_62 | 0.4 | n |  | TRUE
42 | bus_LV_121-9_0_4_node_61 | 0.4 | n |  | TRUE
43 | bus_LV_121-9_0_4_node_59 | 0.4 | n |  | TRUE
44 | bus_LV_121-9_0_4_node_57 | 0.4 | n |  | TRUE
45 | bus_LV_121-9_0_4_node_66 | 0.4 | n |  | TRUE
46 | bus_LV_121-9_0_4_node_32 | 0.4 | n |  | TRUE
47 | bus_LV_121-9_0_4_node_33 | 0.4 | n |  | TRUE
48 | bus_LV_121-9_0_4_node_34 | 0.4 | n |  | TRUE
49 | bus_LV_121-9_0_4_node_35 | 0.4 | n |  | TRUE
50 | bus_LV_121-9_0_4_node_36 | 0.4 | n |  | TRUE
51 | bus_LV_121-9_0_4_node_37 | 0.4 | n |  | TRUE
52 | bus_LV_121-9_0_4_node_38 | 0.4 | n |  | TRUE
53 | bus_LV_121-9_0_4_node_39 | 0.4 | n |  | TRUE
54 | bus_LV_121-9_0_4_node_40 | 0.4 | n |  | TRUE
55 | bus_LV_121-9_0_4_node_137 | 0.4 | n |  | TRUE
56 | bus_LV_121-9_0_4_node_68 | 0.4 | n |  | TRUE
57 | bus_LV_121-9_0_4_node_88 | 0.4 | n |  | TRUE
58 | bus_LV_121-9_0_4_node_138 | 0.4 | n |  | TRUE
59 | bus_LV_121-9_0_4_node_58 | 0.4 | n |  | TRUE
60 | bus_LV_121-9_0_4_node_91 | 0.4 | n |  | TRUE
61 | bus_LV_121-9_0_4_node_92 | 0.4 | n |  | TRUE
62 | bus_LV_121-9_0_4_node_86 | 0.4 | n |  | TRUE
63 | bus_LV_121-9_0_4_node_45 | 0.4 | n |  | TRUE
64 | bus_LV_121-9_0_4_node_46 | 0.4 | n |  | TRUE
65 | bus_LV_121-9_0_4_node_47 | 0.4 | n |  | TRUE
66 | bus_LV_121-9_0_4_node_48 | 0.4 | n |  | TRUE
67 | bus_LV_121-9_0_4_node_49 | 0.4 | n |  | TRUE
68 | bus_LV_121-9_0_4_node_50 | 0.4 | n |  | TRUE
69 | bus_LV_121-9_0_4_node_63 | 0.4 | n |  | TRUE
70 | bus_LV_121-9_0_4_node_51 | 0.4 | n |  | TRUE
71 | bus_LV_121-9_0_4_node_64 | 0.4 | n |  | TRUE
72 | bus_LV_121-9_0_4_node_52 | 0.4 | n |  | TRUE
73 | bus_LV_121-9_0_4_node_53 | 0.4 | n |  | TRUE
74 | bus_LV_121-9_0_4_node_54 | 0.4 | n |  | TRUE
75 | bus_LV_121-9_0_4_node_55 | 0.4 | n |  | TRUE
76 | bus_LV_121-9_0_4_node_56 | 0.4 | n |  | TRUE
77 | bus_LV_121-9_0_4_node_67 | 0.4 | n |  | TRUE
78 | bus_LV_121-9_0_4_node_69 | 0.4 | n |  | TRUE
79 | bus_LV_121-9_0_4_node_65 | 0.4 | n |  | TRUE
80 | bus_LV_121-9_0_4_node_70 | 0.4 | n |  | TRUE
81 | bus_LV_121-9_0_4_node_71 | 0.4 | n |  | TRUE
82 | bus_LV_121-9_0_4_node_72 | 0.4 | n |  | TRUE
83 | bus_LV_121-9_0_4_node_73 | 0.4 | n |  | TRUE
84 | bus_LV_121-9_0_4_node_74 | 0.4 | n |  | TRUE
85 | bus_LV_121-9_0_4_node_75 | 0.4 | n |  | TRUE
86 | bus_LV_121-9_0_4_node_76 | 0.4 | n |  | TRUE
87 | bus_LV_121-9_0_4_node_77 | 0.4 | n |  | TRUE
88 | bus_LV_121-9_0_4_node_78 | 0.4 | n |  | TRUE
89 | bus_LV_121-9_0_4_node_79 | 0.4 | n |  | TRUE
90 | bus_LV_121-9_0_4_node_80 | 0.4 | n |  | TRUE
91 | bus_LV_121-9_0_4_node_81 | 0.4 | n |  | TRUE
92 | bus_LV_121-9_0_4_node_103 | 0.4 | n |  | TRUE
93 | bus_LV_121-9_0_4_node_104 | 0.4 | n |  | TRUE
94 | bus_LV_121-9_0_4_node_82 | 0.4 | n |  | TRUE
95 | bus_LV_121-9_0_4_node_83 | 0.4 | n |  | TRUE
96 | bus_LV_121-9_0_4_node_84 | 0.4 | n |  | TRUE
97 | bus_LV_121-9_0_4_node_85 | 0.4 | n |  | TRUE
98 | bus_LV_121-9_0_4_node_87 | 0.4 | n |  | TRUE
99 | bus_LV_121-9_0_4_node_93 | 0.4 | n |  | TRUE
100 | bus_LV_121-9_0_4_node_108 | 0.4 | n |  | TRUE
101 | bus_LV_121-9_0_4_node_130 | 0.4 | n |  | TRUE
102 | bus_LV_121-9_0_4_node_131 | 0.4 | n |  | TRUE
103 | bus_LV_121-9_0_4_node_94 | 0.4 | n |  | TRUE
104 | bus_LV_121-9_0_4_node_95 | 0.4 | n |  | TRUE
105 | bus_LV_121-9_0_4_node_96 | 0.4 | n |  | TRUE
106 | bus_LV_121-9_0_4_node_97 | 0.4 | n |  | TRUE
107 | bus_LV_121-9_0_4_node_99 | 0.4 | n |  | TRUE
108 | bus_LV_121-9_0_4_node_100 | 0.4 | n |  | TRUE
109 | bus_LV_121-9_0_4_node_101 | 0.4 | n |  | TRUE
110 | bus_LV_121-9_0_4_node_102 | 0.4 | n |  | TRUE
111 | bus_LV_121-9_0_4_node_125 | 0.4 | n |  | TRUE
112 | bus_LV_121-9_0_4_node_126 | 0.4 | n |  | TRUE
113 | bus_LV_121-9_0_4_node_127 | 0.4 | n |  | TRUE
114 | bus_LV_121-9_0_4_node_105 | 0.4 | n |  | TRUE
115 | bus_LV_121-9_0_4_node_110 | 0.4 | n |  | TRUE
116 | bus_LV_121-9_0_4_node_111 | 0.4 | n |  | TRUE
117 | bus_LV_121-9_0_4_node_112 | 0.4 | n |  | TRUE
118 | bus_LV_121-9_0_4_node_113 | 0.4 | n |  | TRUE
119 | bus_LV_121-9_0_4_node_114 | 0.4 | n |  | TRUE
120 | bus_LV_121-9_0_4_node_115 | 0.4 | n |  | TRUE
121 | bus_LV_121-9_0_4_node_116 | 0.4 | n |  | TRUE
122 | bus_LV_121-9_0_4_node_117 | 0.4 | n |  | TRUE
123 | bus_LV_121-9_0_4_node_118 | 0.4 | n |  | TRUE
124 | bus_LV_121-9_0_4_node_119 | 0.4 | n |  | TRUE
125 | bus_LV_121-9_0_4_node_122 | 0.4 | n |  | TRUE
126 | bus_LV_121-9_0_4_node_120 | 0.4 | n |  | TRUE
127 | bus_LV_121-9_0_4_node_121 | 0.4 | n |  | TRUE
128 | bus_LV_121-9_0_4_node_133 | 0.4 | n |  | TRUE
129 | bus_LV_121-9_0_4_node_123 | 0.4 | n |  | TRUE
130 | bus_LV_121-9_0_4_node_124 | 0.4 | n |  | TRUE
131 | bus_LV_121-9_0_4_node_128 | 0.4 | n |  | TRUE
132 | bus_LV_121-9_0_4_node_129 | 0.4 | n |  | TRUE
133 | bus_LV_121-9_0_4_node_132 | 0.4 | n |  | TRUE
134 | bus_LV_121-9_0_4_node_139 | 0.4 | n |  | TRUE
135 | bus_LV_121-9_0_4_node_140 | 0.4 | n |  | TRUE
136 | bus_MV_357_0_node_101 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_121-9_0_4_load_0 | 0 | 0.0042639 | 0.0010686 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_121-9_0_4_load_1 | 1 | 0.00037966 | 9.5152e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_121-9_0_4_load_2 | 2 | 0.00092294 | 0.00023131 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_121-9_0_4_load_136 | 3 | 0.0022934 | 0.00057479 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_121-9_0_4_load_134 | 4 | 0.00050076 | 0.0001255 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_121-9_0_4_load_109 | 5 | 0.0025339 | 0.00063506 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_121-9_0_4_load_135 | 7 | 0.00050718 | 0.00012711 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_121-9_0_4_load_42 | 8 | 0.0004596 | 0.00011519 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_121-9_0_4_load_3 | 9 | 0.002054 | 0.00051477 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_121-9_0_4_load_4 | 10 | 0.0016112 | 0.00040381 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_121-9_0_4_load_89 | 12 | 0.003557 | 0.00089147 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_121-9_0_4_load_90 | 13 | 0.0031742 | 0.00079552 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_121-9_0_4_load_107 | 14 | 0.0021529 | 0.00053957 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_121-9_0_4_load_106 | 15 | 0.0017096 | 0.00042847 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_121-9_0_4_load_7 | 16 | 0.002738 | 0.0006862 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_121-9_0_4_load_8 | 17 | 0.0018688 | 0.00046837 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_121-9_0_4_load_9 | 18 | 0.0084255 | 0.0021116 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_121-9_0_4_load_11 | 20 | 0.0076963 | 0.0019289 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_121-9_0_4_load_12 | 21 | 0.0027345 | 0.00068532 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_121-9_0_4_load_13 | 22 | 0.0027723 | 0.00069481 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_121-9_0_4_load_14 | 23 | 0.0035394 | 0.00088705 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_121-9_0_4_load_43 | 25 | 0.0031128 | 0.00078014 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_121-9_0_4_load_28 | 26 | 0.002527 | 0.00063333 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_121-9_0_4_load_26 | 27 | 0.021935 | 0.0054973 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_121-9_0_4_load_22 | 28 | 0.0029215 | 0.0007322 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_121-9_0_4_load_15 | 30 | 0.0021728 | 0.00054456 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_121-9_0_4_load_16 | 31 | 0.0054575 | 0.0013678 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_121-9_0_4_load_17 | 32 | 0.0023408 | 0.00058666 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_121-9_0_4_load_18 | 33 | 0.01083 | 0.0027144 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_121-9_0_4_load_19 | 34 | 0.002117 | 0.00053056 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_121-9_0_4_load_21 | 35 | 0.0023437 | 0.00058739 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_121-9_0_4_load_25 | 36 | 0.016685 | 0.0041818 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_121-9_0_4_load_23 | 37 | 0.0087755 | 0.0021994 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_121-9_0_4_load_31 | 39 | 0.0016275 | 0.0004079 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_121-9_0_4_load_60 | 40 | 0.0018158 | 0.00045508 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_121-9_0_4_load_62 | 41 | 0.0034804 | 0.00087226 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_121-9_0_4_load_61 | 42 | 0.0014145 | 0.0003545 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_121-9_0_4_load_59 | 43 | 0.0013262 | 0.00033237 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_121-9_0_4_load_57 | 44 | 0.0028888 | 0.00072401 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_121-9_0_4_load_66 | 45 | 0.00224 | 0.0005614 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_121-9_0_4_load_32 | 46 | 0.017922 | 0.0044917 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_121-9_0_4_load_33 | 47 | 0.0043546 | 0.0010914 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_121-9_0_4_load_35 | 49 | 0.0021944 | 0.00054997 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_121-9_0_4_load_36 | 50 | 0.0033807 | 0.00084728 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_121-9_0_4_load_37 | 51 | 0.0011489 | 0.00028794 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_121-9_0_4_load_38 | 52 | 0.0023192 | 0.00058123 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_121-9_0_4_load_40 | 54 | 0.0017575 | 0.00044048 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_121-9_0_4_load_137 | 55 | 0.0021926 | 0.0005495 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_121-9_0_4_load_68 | 56 | 0.001393 | 0.00034911 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_121-9_0_4_load_138 | 58 | 0.002321 | 0.0005817 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_121-9_0_4_load_91 | 60 | 0.0010918 | 0.00027362 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_121-9_0_4_load_92 | 61 | 0.0015073 | 0.00037777 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_121-9_0_4_load_86 | 62 | 0.001362 | 0.00034134 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_121-9_0_4_load_45 | 63 | 0.0059563 | 0.0014928 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_121-9_0_4_load_46 | 64 | 0.0032274 | 0.00080887 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_121-9_0_4_load_47 | 65 | 0.0065501 | 0.0016416 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_121-9_0_4_load_48 | 66 | 0.0043958 | 0.0011017 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_121-9_0_4_load_49 | 67 | 0.0016979 | 0.00042554 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_121-9_0_4_load_50 | 68 | 0.0033006 | 0.0008272 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_121-9_0_4_load_63 | 69 | 0.0020294 | 0.00050862 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_121-9_0_4_load_51 | 70 | 0.0022997 | 0.00057637 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_121-9_0_4_load_64 | 71 | 0.0037365 | 0.00093646 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_121-9_0_4_load_52 | 72 | 0.0025508 | 0.00063929 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_121-9_0_4_load_53 | 73 | 0.0030213 | 0.00075721 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_121-9_0_4_load_54 | 74 | 0.0027667 | 0.0006934 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_121-9_0_4_load_55 | 75 | 0.0027772 | 0.00069603 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_121-9_0_4_load_67 | 77 | 0.0008335 | 0.00020889 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_121-9_0_4_load_69 | 78 | 0.0012608 | 0.00031598 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_121-9_0_4_load_65 | 79 | 0.0018369 | 0.00046038 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_121-9_0_4_load_70 | 80 | 0.00083819 | 0.00021007 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_121-9_0_4_load_71 | 81 | 0.0017289 | 0.00043331 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_121-9_0_4_load_72 | 82 | 0.0038538 | 0.00096585 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_121-9_0_4_load_73 | 83 | 0.0032529 | 0.00081526 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_121-9_0_4_load_75 | 85 | 0.0031384 | 0.00078655 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_121-9_0_4_load_77 | 87 | 0.0024422 | 0.00061207 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_121-9_0_4_load_78 | 88 | 0.0025737 | 0.00064502 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_121-9_0_4_load_79 | 89 | 0.0016219 | 0.00040649 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_121-9_0_4_load_80 | 90 | 0.0029522 | 0.0007399 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_121-9_0_4_load_81 | 91 | 0.006485 | 0.0016253 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_121-9_0_4_load_103 | 92 | 0.0030821 | 0.00077244 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_121-9_0_4_load_104 | 93 | 0.0032246 | 0.00080816 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_121-9_0_4_load_82 | 94 | 0.0028008 | 0.00070194 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_121-9_0_4_load_83 | 95 | 0.0011932 | 0.00029905 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_121-9_0_4_load_84 | 96 | 0.0020398 | 0.00051122 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_121-9_0_4_load_85 | 97 | 0.00194 | 0.00048621 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_121-9_0_4_load_87 | 98 | 0.0007683 | 0.00019255 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_121-9_0_4_load_93 | 99 | 0.0016544 | 0.00041464 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_121-9_0_4_load_108 | 100 | 0.0020626 | 0.00051694 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_121-9_0_4_load_130 | 101 | 0.0012653 | 0.00031712 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_121-9_0_4_load_131 | 102 | 0.0014033 | 0.00035169 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_121-9_0_4_load_94 | 103 | 0.0075802 | 0.0018998 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_121-9_0_4_load_95 | 104 | 0.003787 | 0.0009491 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_121-9_0_4_load_96 | 105 | 0.0012944 | 0.00032441 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_121-9_0_4_load_99 | 107 | 0.0036277 | 0.00090918 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_121-9_0_4_load_100 | 108 | 0.0046444 | 0.001164 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_121-9_0_4_load_101 | 109 | 0.0028245 | 0.00070788 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_121-9_0_4_load_102 | 110 | 0.0042066 | 0.0010543 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_121-9_0_4_load_125 | 111 | 0.0073646 | 0.0018458 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_121-9_0_4_load_126 | 112 | 0.0027542 | 0.00069026 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_121-9_0_4_load_127 | 113 | 0.002055 | 0.00051504 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_121-9_0_4_load_105 | 114 | 0.0064336 | 0.0016124 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_121-9_0_4_load_110 | 115 | 0.0032207 | 0.00080718 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_121-9_0_4_load_111 | 116 | 0.0029038 | 0.00072775 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_121-9_0_4_load_112 | 117 | 0.0022157 | 0.00055532 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_121-9_0_4_load_113 | 118 | 0.0037101 | 0.00092985 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_121-9_0_4_load_115 | 120 | 0.0031516 | 0.00078988 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_121-9_0_4_load_116 | 121 | 0.0012067 | 0.00030243 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_121-9_0_4_load_117 | 122 | 0.00085553 | 0.00021442 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_121-9_0_4_load_118 | 123 | 0.00072033 | 0.00018053 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_121-9_0_4_load_122 | 125 | 0.0025813 | 0.00064694 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_121-9_0_4_load_120 | 126 | 0.00072293 | 0.00018118 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_121-9_0_4_load_121 | 127 | 0.0046475 | 0.0011648 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_121-9_0_4_load_133 | 128 | 0.00074416 | 0.0001865 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_121-9_0_4_load_123 | 129 | 0.0007378 | 0.00018491 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_121-9_0_4_load_124 | 130 | 0.00077596 | 0.00019447 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_121-9_0_4_load_128 | 131 | 0.0011279 | 0.00028268 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_121-9_0_4_load_129 | 132 | 0.0010831 | 0.00027145 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_121-9_0_4_load_132 | 133 | 0.0010907 | 0.00027335 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_121-9_0_4_load_140 | 135 | 0.0021908 | 0.00054907 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 75 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_121-9_0_4_line_0 |  | 0 | 1 | 0.004006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_121-9_0_4_line_1 |  | 1 | 2 | 0.029022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_121-9_0_4_line_2 |  | 2 | 6 | 0.014395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_121-9_0_4_line_3 |  | 3 | 4 | 0.021886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_121-9_0_4_line_4 |  | 3 | 5 | 0.018081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_121-9_0_4_line_5 |  | 4 | 7 | 0.004655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_121-9_0_4_line_6 |  | 5 | 100 | 0.0072045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_121-9_0_4_line_7 |  | 6 | 8 | 0.058384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_121-9_0_4_line_8 |  | 7 | 8 | 0.022217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_121-9_0_4_line_9 |  | 9 | 10 | 0.0412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_121-9_0_4_line_10 |  | 10 | 11 | 0.023485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_121-9_0_4_line_11 |  | 11 | 12 | 0.0044236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_121-9_0_4_line_12 |  | 11 | 13 | 0.0045025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_121-9_0_4_line_13 |  | 12 | 14 | 0.024703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_121-9_0_4_line_14 |  | 13 | 15 | 0.011413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_121-9_0_4_line_15 |  | 14 | 100 | 0.0062865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_121-9_0_4_line_16 |  | 15 | 89 | 0.0028928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_121-9_0_4_line_17 |  | 16 | 17 | 0.0067432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_121-9_0_4_line_18 |  | 16 | 18 | 0.023032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_121-9_0_4_line_19 |  | 17 | 19 | 0.0079967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_121-9_0_4_line_20 |  | 18 | 20 | 0.00082661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_121-9_0_4_line_21 |  | 19 | 21 | 0.015537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_121-9_0_4_line_22 |  | 19 | 22 | 0.020368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_121-9_0_4_line_23 |  | 20 | 23 | 0.024439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_121-9_0_4_line_24 |  | 21 | 24 | 0.012678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_121-9_0_4_line_25 |  | 22 | 25 | 0.022714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_121-9_0_4_line_26 |  | 23 | 26 | 0.0064215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_121-9_0_4_line_27 |  | 24 | 27 | 0.021747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_121-9_0_4_line_28 |  | 24 | 28 | 0.0018415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_121-9_0_4_line_29 |  | 26 | 29 | 0.0096368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_121-9_0_4_line_30 |  | 28 | 37 | 0.017319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_121-9_0_4_line_31 |  | 29 | 38 | 0.009041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
32 | LV_121-9_0_4_line_32 |  | 29 | 39 | 0.022976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_121-9_0_4_line_33 |  | 30 | 31 | 0.027735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_121-9_0_4_line_34 |  | 30 | 32 | 0.010548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_121-9_0_4_line_35 |  | 31 | 33 | 0.00049947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_121-9_0_4_line_36 |  | 32 | 34 | 0.010512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_121-9_0_4_line_37 |  | 34 | 35 | 0.0050177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_121-9_0_4_line_38 |  | 35 | 36 | 0.031358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_121-9_0_4_line_39 |  | 36 | 37 | 0.0071585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_121-9_0_4_line_40 |  | 38 | 40 | 0.013233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
41 | LV_121-9_0_4_line_41 |  | 39 | 41 | 0.0055795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_121-9_0_4_line_42 |  | 40 | 44 | 0.0059137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
43 | LV_121-9_0_4_line_43 |  | 41 | 45 | 0.01443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_121-9_0_4_line_44 |  | 42 | 43 | 0.018884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_121-9_0_4_line_45 |  | 43 | 76 | 0.026927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_121-9_0_4_line_46 |  | 44 | 75 | 0.018347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
47 | LV_121-9_0_4_line_47 |  | 45 | 79 | 0.0091435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_121-9_0_4_line_48 |  | 46 | 47 | 0.043539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_121-9_0_4_line_49 |  | 46 | 48 | 0.031705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_121-9_0_4_line_50 |  | 47 | 49 | 0.012715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_121-9_0_4_line_51 |  | 48 | 50 | 0.0087792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
52 | LV_121-9_0_4_line_52 |  | 48 | 51 | 0.023366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
53 | LV_121-9_0_4_line_53 |  | 49 | 52 | 0.0073537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_121-9_0_4_line_54 |  | 50 | 53 | 0.02611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
55 | LV_121-9_0_4_line_55 |  | 51 | 54 | 0.0043831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
56 | LV_121-9_0_4_line_56 |  | 52 | 55 | 0.0094833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_121-9_0_4_line_57 |  | 53 | 56 | 0.013359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
58 | LV_121-9_0_4_line_58 |  | 54 | 57 | 0.013184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
59 | LV_121-9_0_4_line_59 |  | 55 | 58 | 0.0073537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_121-9_0_4_line_60 |  | 56 | 59 | 0.01503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
61 | LV_121-9_0_4_line_61 |  | 57 | 60 | 0.010558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_121-9_0_4_line_62 |  | 57 | 61 | 0.036163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_121-9_0_4_line_63 |  | 57 | 62 | 0.032772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_121-9_0_4_line_64 |  | 58 | 134 | 0.011602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_121-9_0_4_line_65 |  | 59 | 77 | 0.012044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_121-9_0_4_line_66 |  | 59 | 76 | 0.009916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
67 | LV_121-9_0_4_line_67 |  | 60 | 88 | 0.015183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_121-9_0_4_line_68 |  | 61 | 99 | 0.019822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_121-9_0_4_line_69 |  | 62 | 96 | 0.0066558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_121-9_0_4_line_70 |  | 63 | 64 | 0.020634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_121-9_0_4_line_71 |  | 63 | 65 | 0.017652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_121-9_0_4_line_72 |  | 64 | 66 | 0.0025397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_121-9_0_4_line_73 |  | 65 | 67 | 0.017503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_121-9_0_4_line_74 |  | 66 | 68 | 0.023292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_121-9_0_4_line_75 |  | 67 | 69 | 0.014111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_121-9_0_4_line_76 |  | 68 | 70 | 0.028666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_121-9_0_4_line_77 |  | 69 | 71 | 0.032262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_121-9_0_4_line_78 |  | 70 | 72 | 0.0018929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_121-9_0_4_line_79 |  | 71 | 79 | 0.028077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_121-9_0_4_line_80 |  | 73 | 74 | 0.018123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
81 | LV_121-9_0_4_line_81 |  | 73 | 75 | 0.025815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
82 | LV_121-9_0_4_line_82 |  | 74 | 76 | 0.013866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
83 | LV_121-9_0_4_line_83 |  | 77 | 78 | 0.013084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_121-9_0_4_line_84 |  | 78 | 80 | 0.00081614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_121-9_0_4_line_85 |  | 80 | 81 | 0.0036285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_121-9_0_4_line_86 |  | 82 | 83 | 0.0020877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_121-9_0_4_line_87 |  | 82 | 84 | 0.020247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_121-9_0_4_line_88 |  | 83 | 85 | 0.0037323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_121-9_0_4_line_89 |  | 84 | 86 | 0.005482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_121-9_0_4_line_90 |  | 84 | 87 | 0.033309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_121-9_0_4_line_91 |  | 85 | 88 | 0.017531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_121-9_0_4_line_92 |  | 86 | 89 | 0.038828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_121-9_0_4_line_93 |  | 86 | 90 | 0.017699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_121-9_0_4_line_94 |  | 87 | 91 | 0.0055718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_121-9_0_4_line_95 |  | 90 | 92 | 0.010275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_121-9_0_4_line_96 |  | 92 | 93 | 0.020457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_121-9_0_4_line_97 |  | 93 | 114 | 0.00070167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_121-9_0_4_line_98 |  | 94 | 95 | 0.00050444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_121-9_0_4_line_99 |  | 94 | 96 | 0.013997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_121-9_0_4_line_100 |  | 95 | 97 | 0.0036785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_121-9_0_4_line_101 |  | 97 | 98 | 0.025824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_121-9_0_4_line_102 |  | 99 | 101 | 0.0065823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_121-9_0_4_line_103 |  | 101 | 102 | 0.0064359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_121-9_0_4_line_104 |  | 102 | 133 | 0.0066338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_121-9_0_4_line_105 |  | 103 | 104 | 0.027654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_121-9_0_4_line_106 |  | 103 | 105 | 0.01 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_121-9_0_4_line_107 |  | 104 | 106 | 0.0063037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_121-9_0_4_line_108 |  | 106 | 107 | 0.015322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_121-9_0_4_line_109 |  | 106 | 108 | 0.035694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_121-9_0_4_line_110 |  | 107 | 109 | 0.019469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_121-9_0_4_line_111 |  | 108 | 110 | 0.011107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_121-9_0_4_line_112 |  | 109 | 111 | 0.015003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_121-9_0_4_line_113 |  | 110 | 112 | 0.0015769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_121-9_0_4_line_114 |  | 112 | 113 | 0.02296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_121-9_0_4_line_115 |  | 113 | 131 | 0.0066858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_121-9_0_4_line_116 |  | 114 | 115 | 0.0095876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_121-9_0_4_line_117 |  | 115 | 116 | 0.0054806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_121-9_0_4_line_118 |  | 116 | 117 | 0.01564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_121-9_0_4_line_119 |  | 117 | 118 | 0.0015204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_121-9_0_4_line_120 |  | 118 | 119 | 0.029222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_121-9_0_4_line_121 |  | 119 | 120 | 0.013273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_121-9_0_4_line_122 |  | 119 | 121 | 0.011098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_121-9_0_4_line_123 |  | 120 | 122 | 0.0092477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_121-9_0_4_line_124 |  | 121 | 123 | 0.0060123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_121-9_0_4_line_125 |  | 122 | 124 | 0.0090827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_121-9_0_4_line_126 |  | 123 | 125 | 0.0070333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_121-9_0_4_line_127 |  | 124 | 126 | 0.003519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_121-9_0_4_line_128 |  | 125 | 127 | 0.0042796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_121-9_0_4_line_129 |  | 126 | 128 | 0.0060695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_121-9_0_4_line_130 |  | 127 | 129 | 0.020737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_121-9_0_4_line_131 |  | 129 | 130 | 0.0076482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_121-9_0_4_line_132 |  | 131 | 132 | 0.0066122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_121-9_0_4_line_133 |  | 132 | 133 | 0.0064696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_121-9_0_4_line_134 |  | 134 | 135 | 0.0046971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_121-9_0_4_trafo_55 | 0.63 MVA 20/0.4 kV | 136 | 75 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2702180.6851 | 1242267.0386 | 2702182.3966 | 1242263.4166
1 | 2702195.1044 | 1242237.329 | 2702190.3625 | 1242246.5583 | 2702182.3966 | 1242263.4166
2 | 2702201.683 | 1242224.5251 | 2702195.1044 | 1242237.329
3 | 2702241.253 | 1242278.6156 | 2702232.4424 | 1242298.6498
4 | 2702225.1636 | 1242315.201 | 2702232.4424 | 1242298.6498
5 | 2702241.253 | 1242278.6156 | 2702243.1269 | 1242274.3544
6 | 2702222.2633 | 1242321.796 | 2702225.1636 | 1242315.201
7 | 2702252.0707 | 1242254.0174 | 2702201.683 | 1242224.5251
8 | 2702243.1269 | 1242274.3544 | 2702252.0707 | 1242254.0174
9 | 2702152.0266 | 1242327.8722 | 2702152.0266 | 1242327.8722 | 2702189.3833 | 1242345.2475
10 | 2702210.6433 | 1242355.2247 | 2702204.6593 | 1242352.3528 | 2702189.3833 | 1242345.2475
11 | 2702210.6433 | 1242355.2247 | 2702211.9637 | 1242351.0027
12 | 2702210.6433 | 1242355.2247 | 2702209.8512 | 1242359.6569
13 | 2702211.9637 | 1242351.0027 | 2702216.0046 | 1242338.0816 | 2702219.9091 | 1242327.6223
14 | 2702208.192 | 1242370.9312 | 2702208.3254 | 1242368.1948 | 2702209.8512 | 1242359.6569
15 | 2702219.9091 | 1242327.6223 | 2702221.0777 | 1242324.4918 | 2702222.2633 | 1242321.796
16 | 2702208.051 | 1242373.8205 | 2702208.192 | 1242370.9312
17 | 2702247.5942 | 1242611.8245 | 2702248.9613 | 1242612.6502 | 2702253.6381 | 1242614.7974
18 | 2702247.5942 | 1242611.8245 | 2702241.7032 | 1242608.2662 | 2702230.7045 | 1242599.8258 | 2702228.8978 | 1242598.4264
19 | 2702260.958 | 1242618.0166 | 2702254.4221 | 1242615.1573 | 2702253.6381 | 1242614.7974
20 | 2702228.8978 | 1242598.4264 | 2702228.2443 | 1242597.9203
21 | 2702260.958 | 1242618.0166 | 2702255.5692 | 1242632.5889
22 | 2702260.958 | 1242618.0166 | 2702267.9873 | 1242619.8836 | 2702277.4141 | 1242621.703 | 2702280.9006 | 1242621.9283
23 | 2702228.2443 | 1242597.9203 | 2702208.9232 | 1242582.9556
24 | 2702251.172 | 1242644.4796 | 2702255.5692 | 1242632.5889
25 | 2702303.5658 | 1242623.4104 | 2702298.0765 | 1242623.038 | 2702280.9006 | 1242621.9283
26 | 2702203.8464 | 1242579.0235 | 2702208.9232 | 1242582.9556
27 | 2702251.172 | 1242644.4796 | 2702261.5918 | 1242649.2183 | 2702264.8907 | 1242651.2656 | 2702266.8317 | 1242654.0123 | 2702268.1047 | 1242656.7884
28 | 2702251.172 | 1242644.4796 | 2702250.3023 | 1242646.1028
29 | 2702196.2275 | 1242573.1225 | 2702203.8464 | 1242579.0235
30 | 2702250.3023 | 1242646.1028 | 2702246.7505 | 1242652.732 | 2702244.0521 | 1242657.0777 | 2702241.417 | 1242660.9486
31 | 2702196.2275 | 1242573.1225 | 2702189.0263 | 1242567.6276
32 | 2702196.2275 | 1242573.1225 | 2702189.2005 | 1242579.0171 | 2702185.1723 | 1242581.5609 | 2702176.9366 | 1242585.287
33 | 2702198.6661 | 1242709.1645 | 2702198.1985 | 1242709.6953 | 2702180.3746 | 1242730.0135
34 | 2702198.6661 | 1242709.1645 | 2702205.6386 | 1242701.2503
35 | 2702180.3746 | 1242730.0135 | 2702180.0452 | 1242730.3889
36 | 2702212.5876 | 1242693.3629 | 2702205.6386 | 1242701.2503
37 | 2702215.9046 | 1242689.5979 | 2702212.5876 | 1242693.3629
38 | 2702237.2685 | 1242666.7816 | 2702235.984 | 1242668.5476 | 2702232.1229 | 1242673.2403 | 2702228.3996 | 1242677.3905 | 2702221.9183 | 1242682.7719 | 2702215.9046 | 1242689.5979
39 | 2702237.2685 | 1242666.7816 | 2702240.0418 | 1242662.9688 | 2702241.417 | 1242660.9486
40 | 2702189.0263 | 1242567.6276 | 2702194.8411 | 1242555.7407 | 2702194.8411 | 1242555.7407
41 | 2702176.9366 | 1242585.287 | 2702171.8532 | 1242587.587
42 | 2702190.0242 | 1242552.31 | 2702194.8411 | 1242555.7407
43 | 2702158.7061 | 1242593.5352 | 2702171.8532 | 1242587.587
44 | 2702149.6056 | 1242537.5461 | 2702164.6182 | 1242549.002
45 | 2702128.1996 | 1242521.2114 | 2702149.6056 | 1242537.5461
46 | 2702190.0242 | 1242552.31 | 2702175.0802 | 1242541.6665
47 | 2702150.3752 | 1242597.3036 | 2702153.3286 | 1242595.9682 | 2702158.7061 | 1242593.5352
48 | 2702056.6841 | 1242419.5123 | 2702090.2229 | 1242447.2751
49 | 2702114.646 | 1242467.4922 | 2702090.2229 | 1242447.2751
50 | 2702056.6841 | 1242419.5123 | 2702046.8897 | 1242411.4046
51 | 2702114.646 | 1242467.4922 | 2702110.1112 | 1242475.0095
52 | 2702114.646 | 1242467.4922 | 2702119.3362 | 1242460.7566 | 2702126.7314 | 1242451.4878 | 2702129.0199 | 1242449.1097
53 | 2702046.8897 | 1242411.4046 | 2702041.225 | 1242406.7154
54 | 2702097.7375 | 1242497.9582 | 2702102.6294 | 1242487.412 | 2702110.1112 | 1242475.0095
55 | 2702129.0199 | 1242449.1097 | 2702132.0593 | 1242445.9515
56 | 2702041.225 | 1242406.7154 | 2702033.9198 | 1242400.6683
57 | 2702097.7375 | 1242497.9582 | 2702108.3548 | 1242506.0654
58 | 2702143.7751 | 1242440.4059 | 2702133.9526 | 1242443.9841 | 2702132.0593 | 1242445.9515
59 | 2702033.9198 | 1242400.6683 | 2702028.2551 | 1242395.9792
60 | 2702120.3043 | 1242515.182 | 2702110.2223 | 1242507.4914 | 2702108.3548 | 1242506.0654
61 | 2702143.7751 | 1242440.4059 | 2702153.5424 | 1242436.3971
62 | 2702143.7751 | 1242440.4059 | 2702151.7993 | 1242449.9291 | 2702161.1049 | 1242455.7271 | 2702172.7193 | 1242460.9759
63 | 2702143.7751 | 1242440.4059 | 2702125.9612 | 1242412.8982
64 | 2702019.3176 | 1242388.5808 | 2702028.2551 | 1242395.9792
65 | 2702120.3043 | 1242515.182 | 2702112.7382 | 1242524.281 | 2702112.7293 | 1242524.491
66 | 2702128.1996 | 1242521.2114 | 2702120.3043 | 1242515.182
67 | 2702153.5424 | 1242436.3971 | 2702167.588 | 1242430.6324
68 | 2702172.7193 | 1242460.9759 | 2702175.2767 | 1242462.1316 | 2702191.756 | 1242466.3679
69 | 2702122.3433 | 1242407.3116 | 2702122.3433 | 1242407.3116 | 2702125.9612 | 1242412.8982
70 | 2702058.7128 | 1242655.0416 | 2702058.7128 | 1242655.0416 | 2702064.0646 | 1242674.9695
71 | 2702058.7128 | 1242655.0416 | 2702070.2272 | 1242641.6618
72 | 2702064.7233 | 1242677.4223 | 2702064.0646 | 1242674.9695
73 | 2702070.2272 | 1242641.6618 | 2702072.1596 | 1242639.4163 | 2702084.2474 | 1242631.3355
74 | 2702064.7233 | 1242677.4223 | 2702070.7645 | 1242699.9176
75 | 2702096.2986 | 1242624.0371 | 2702091.4567 | 1242626.5161 | 2702084.2474 | 1242631.3355
76 | 2702070.7645 | 1242699.9176 | 2702075.4025 | 1242717.1877 | 2702077.5395 | 1242724.8082 | 2702078.3148 | 1242727.5712
77 | 2702096.2986 | 1242624.0371 | 2702125.0153 | 1242609.3342
78 | 2702078.3148 | 1242727.5712 | 2702078.8263 | 1242729.3937
79 | 2702125.0153 | 1242609.3342 | 2702134.4466 | 1242604.5054 | 2702150.3752 | 1242597.3036
80 | 2702154.0532 | 1242526.6905 | 2702139.2919 | 1242516.1771
81 | 2702154.0532 | 1242526.6905 | 2702175.0802 | 1242541.6665
82 | 2702128.1996 | 1242521.2114 | 2702136.9866 | 1242514.5352 | 2702139.2919 | 1242516.1771
83 | 2702112.1752 | 1242537.5633 | 2702112.7293 | 1242524.491
84 | 2702112.1406 | 1242538.3787 | 2702112.1752 | 1242537.5633
85 | 2702111.987 | 1242542.004 | 2702112.1406 | 1242538.3787
86 | 2702189.19 | 1242421.7663 | 2702187.2586 | 1242422.559
87 | 2702207.9203 | 1242414.0788 | 2702189.19 | 1242421.7663
88 | 2702187.2586 | 1242422.559 | 2702183.8058 | 1242423.9761
89 | 2702213.0067 | 1242411.9981 | 2702207.9203 | 1242414.0788
90 | 2702207.9203 | 1242414.0788 | 2702214.1536 | 1242423.5379 | 2702222.8256 | 1242431.8826 | 2702232.6926 | 1242433.1307
91 | 2702167.588 | 1242430.6324 | 2702183.8058 | 1242423.9761
92 | 2702213.0067 | 1242411.9981 | 2702208.9606 | 1242398.4624 | 2702207.6707 | 1242381.6161 | 2702208.051 | 1242373.8205
93 | 2702213.0067 | 1242411.9981 | 2702229.3525 | 1242405.2109
94 | 2702238.2547 | 1242433.3495 | 2702233.8176 | 1242433.273 | 2702232.6926 | 1242433.1307
95 | 2702229.3525 | 1242405.2109 | 2702238.8419 | 1242401.2707
96 | 2702257.7349 | 1242393.4259 | 2702238.8419 | 1242401.2707
97 | 2702258.383 | 1242393.1568 | 2702257.7349 | 1242393.4259
98 | 2702115.3411 | 1242395.1924 | 2702115.0887 | 1242394.7557
99 | 2702115.3411 | 1242395.1924 | 2702122.3433 | 1242407.3116
100 | 2702115.0887 | 1242394.7557 | 2702113.2484 | 1242391.5706
101 | 2702113.2484 | 1242391.5706 | 2702106.6975 | 1242380.2326 | 2702101.3746 | 1242368.6689
102 | 2702198.1311 | 1242468.0067 | 2702191.756 | 1242466.3679
103 | 2702204.3643 | 1242469.6091 | 2702198.1311 | 1242468.0067
104 | 2702210.7893 | 1242471.2607 | 2702204.3643 | 1242469.6091
105 | 2702331.915 | 1242502.3949 | 2702305.131 | 1242495.5123
106 | 2702341.6005 | 1242504.8838 | 2702331.915 | 1242502.3949
107 | 2702299.0257 | 1242493.9434 | 2702305.131 | 1242495.5123
108 | 2702299.0257 | 1242493.9434 | 2702304.9555 | 1242479.8149
109 | 2702299.0257 | 1242493.9434 | 2702264.4559 | 1242485.0567
110 | 2702304.9555 | 1242479.8149 | 2702312.4898 | 1242461.8633
111 | 2702264.4559 | 1242485.0567 | 2702253.6989 | 1242482.2914
112 | 2702318.2961 | 1242448.0291 | 2702312.4898 | 1242461.8633
113 | 2702252.1717 | 1242481.8988 | 2702253.6989 | 1242482.2914
114 | 2702229.9345 | 1242476.1823 | 2702252.1717 | 1242481.8988
115 | 2702229.9345 | 1242476.1823 | 2702223.4592 | 1242474.5177
116 | 2702267.2376 | 1242389.4801 | 2702258.383 | 1242393.1568
117 | 2702267.2376 | 1242389.4801 | 2702272.2992 | 1242387.3784
118 | 2702286.7436 | 1242381.3808 | 2702272.2992 | 1242387.3784
119 | 2702288.1478 | 1242380.7977 | 2702286.7436 | 1242381.3808
120 | 2702315.1356 | 1242369.5918 | 2702288.1478 | 1242380.7977
121 | 2702315.1356 | 1242369.5918 | 2702326.9109 | 1242363.7125 | 2702327.0059 | 1242363.6538
122 | 2702315.1356 | 1242369.5918 | 2702312.6382 | 1242360.9643 | 2702312.1543 | 1242358.9044
123 | 2702327.0059 | 1242363.6538 | 2702334.8734 | 1242358.7935
124 | 2702312.1543 | 1242358.9044 | 2702311.0252 | 1242354.0978 | 2702310.9161 | 1242353.0284
125 | 2702342.6006 | 1242354.0199 | 2702334.8734 | 1242358.7935
126 | 2702310.2023 | 1242346.0314 | 2702310.9161 | 1242353.0284
127 | 2702342.6006 | 1242354.0199 | 2702345.5523 | 1242352.1041
128 | 2702310.1284 | 1242341.7598 | 2702310.0616 | 1242344.6517 | 2702310.2023 | 1242346.0314
129 | 2702350.6434 | 1242348.7997 | 2702345.5523 | 1242352.1041
130 | 2702313.1592 | 1242321.3004 | 2702311.3537 | 1242329.7958 | 2702310.2404 | 1242336.9155 | 2702310.1284 | 1242341.7598
131 | 2702313.1592 | 1242321.3004 | 2702313.7154 | 1242318.6835 | 2702315.0902 | 1242313.9044
132 | 2702223.4592 | 1242474.5177 | 2702217.0551 | 1242472.8715
133 | 2702217.0551 | 1242472.8715 | 2702210.7893 | 1242471.2607
134 | 2702019.3176 | 1242388.5808 | 2702014.6944 | 1242387.7505

## bus_geodata
| x | y | coords
0 | 2702180.6851 | 1242267.0386
1 | 2702182.3966 | 1242263.4166
2 | 2702195.1044 | 1242237.329
3 | 2702232.4424 | 1242298.6498
4 | 2702241.253 | 1242278.6156
5 | 2702225.1636 | 1242315.201
6 | 2702201.683 | 1242224.5251
7 | 2702243.1269 | 1242274.3544
8 | 2702252.0707 | 1242254.0174
9 | 2702152.0266 | 1242327.8722
10 | 2702189.3833 | 1242345.2475
11 | 2702210.6433 | 1242355.2247
12 | 2702211.9637 | 1242351.0027
13 | 2702209.8512 | 1242359.6569
14 | 2702219.9091 | 1242327.6223
15 | 2702208.192 | 1242370.9312
16 | 2702247.5942 | 1242611.8245
17 | 2702253.6381 | 1242614.7974
18 | 2702228.8978 | 1242598.4264
19 | 2702260.958 | 1242618.0166
20 | 2702228.2443 | 1242597.9203
21 | 2702255.5692 | 1242632.5889
22 | 2702280.9006 | 1242621.9283
23 | 2702208.9232 | 1242582.9556
24 | 2702251.172 | 1242644.4796
25 | 2702303.5658 | 1242623.4104
26 | 2702203.8464 | 1242579.0235
27 | 2702268.1047 | 1242656.7884
28 | 2702250.3023 | 1242646.1028
29 | 2702196.2275 | 1242573.1225
30 | 2702198.6661 | 1242709.1645
31 | 2702180.3746 | 1242730.0135
32 | 2702205.6386 | 1242701.2503
33 | 2702180.0452 | 1242730.3889
34 | 2702212.5876 | 1242693.3629
35 | 2702215.9046 | 1242689.5979
36 | 2702237.2685 | 1242666.7816
37 | 2702241.417 | 1242660.9486
38 | 2702189.0263 | 1242567.6276
39 | 2702176.9366 | 1242585.287
40 | 2702194.8411 | 1242555.7407
41 | 2702171.8532 | 1242587.587
42 | 2702164.6182 | 1242549.002
43 | 2702149.6056 | 1242537.5461
44 | 2702190.0242 | 1242552.31
45 | 2702158.7061 | 1242593.5352
46 | 2702090.2229 | 1242447.2751
47 | 2702056.6841 | 1242419.5123
48 | 2702114.646 | 1242467.4922
49 | 2702046.8897 | 1242411.4046
50 | 2702110.1112 | 1242475.0095
51 | 2702129.0199 | 1242449.1097
52 | 2702041.225 | 1242406.7154
53 | 2702097.7375 | 1242497.9582
54 | 2702132.0593 | 1242445.9515
55 | 2702033.9198 | 1242400.6683
56 | 2702108.3548 | 1242506.0654
57 | 2702143.7751 | 1242440.4059
58 | 2702028.2551 | 1242395.9792
59 | 2702120.3043 | 1242515.182
60 | 2702153.5424 | 1242436.3971
61 | 2702172.7193 | 1242460.9759
62 | 2702125.9612 | 1242412.8982
63 | 2702058.7128 | 1242655.0416
64 | 2702064.0646 | 1242674.9695
65 | 2702070.2272 | 1242641.6618
66 | 2702064.7233 | 1242677.4223
67 | 2702084.2474 | 1242631.3355
68 | 2702070.7645 | 1242699.9176
69 | 2702096.2986 | 1242624.0371
70 | 2702078.3148 | 1242727.5712
71 | 2702125.0153 | 1242609.3342
72 | 2702078.8263 | 1242729.3937
73 | 2702154.0532 | 1242526.6905
74 | 2702139.2919 | 1242516.1771
75 | 2702175.0802 | 1242541.6665
76 | 2702128.1996 | 1242521.2114
77 | 2702112.7293 | 1242524.491
78 | 2702112.1752 | 1242537.5633
79 | 2702150.3752 | 1242597.3036
80 | 2702112.1406 | 1242538.3787
81 | 2702111.987 | 1242542.004
82 | 2702189.19 | 1242421.7663
83 | 2702187.2586 | 1242422.559
84 | 2702207.9203 | 1242414.0788
85 | 2702183.8058 | 1242423.9761
86 | 2702213.0067 | 1242411.9981
87 | 2702232.6926 | 1242433.1307
88 | 2702167.588 | 1242430.6324
89 | 2702208.051 | 1242373.8205
90 | 2702229.3525 | 1242405.2109
91 | 2702238.2547 | 1242433.3495
92 | 2702238.8419 | 1242401.2707
93 | 2702257.7349 | 1242393.4259
94 | 2702115.3411 | 1242395.1924
95 | 2702115.0887 | 1242394.7557
96 | 2702122.3433 | 1242407.3116
97 | 2702113.2484 | 1242391.5706
98 | 2702101.3746 | 1242368.6689
99 | 2702191.756 | 1242466.3679
100 | 2702222.2633 | 1242321.796
101 | 2702198.1311 | 1242468.0067
102 | 2702204.3643 | 1242469.6091
103 | 2702331.915 | 1242502.3949
104 | 2702305.131 | 1242495.5123
105 | 2702341.6005 | 1242504.8838
106 | 2702299.0257 | 1242493.9434
107 | 2702304.9555 | 1242479.8149
108 | 2702264.4559 | 1242485.0567
109 | 2702312.4898 | 1242461.8633
110 | 2702253.6989 | 1242482.2914
111 | 2702318.2961 | 1242448.0291
112 | 2702252.1717 | 1242481.8988
113 | 2702229.9345 | 1242476.1823
114 | 2702258.383 | 1242393.1568
115 | 2702267.2376 | 1242389.4801
116 | 2702272.2992 | 1242387.3784
117 | 2702286.7436 | 1242381.3808
118 | 2702288.1478 | 1242380.7977
119 | 2702315.1356 | 1242369.5918
120 | 2702327.0059 | 1242363.6538
121 | 2702312.1543 | 1242358.9044
122 | 2702334.8734 | 1242358.7935
123 | 2702310.9161 | 1242353.0284
124 | 2702342.6006 | 1242354.0199
125 | 2702310.2023 | 1242346.0314
126 | 2702345.5523 | 1242352.1041
127 | 2702310.1284 | 1242341.7598
128 | 2702350.6434 | 1242348.7997
129 | 2702313.1592 | 1242321.3004
130 | 2702315.0902 | 1242313.9044
131 | 2702223.4592 | 1242474.5177
132 | 2702217.0551 | 1242472.8715
133 | 2702210.7893 | 1242471.2607
134 | 2702019.3176 | 1242388.5808
135 | 2702014.6944 | 1242387.7505
136 | 2702175.0802 | 1242541.6665

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97547 | -0.47289 | 0.0042639 | 0.0010686
1 | 0.97548 | -0.47258 | 0.00037966 | 9.5152e-05
2 | 0.97561 | -0.47011 | 0.00092294 | 0.00023131
3 | 0.97628 | -0.45687 | 0.0022934 | 0.00057479
4 | 0.97614 | -0.45968 | 0.00050076 | 0.0001255
5 | 0.97644 | -0.45378 | 0.0025339 | 0.00063506
6 | 0.97568 | -0.46864 | 0 | 0
7 | 0.97611 | -0.46024 | 0.00050718 | 0.00012711
8 | 0.97599 | -0.46269 | 0.0004596 | 0.00011519
9 | 0.97689 | -0.44489 | 0.002054 | 0.00051477
10 | 0.97697 | -0.44335 | 0.0016112 | 0.00040381
11 | 0.97705 | -0.44177 | 0 | 0
12 | 0.97697 | -0.44336 | 0.003557 | 0.00089147
13 | 0.97715 | -0.43986 | 0.0031742 | 0.00079552
14 | 0.9766 | -0.45062 | 0.0021529 | 0.00053957
15 | 0.97743 | -0.43434 | 0.0017096 | 0.00042847
16 | 0.9907 | -0.17828 | 0.002738 | 0.0006862
17 | 0.99016 | -0.18859 | 0.0018688 | 0.00046837
18 | 0.99258 | -0.14202 | 0.0084255 | 0.0021116
19 | 0.98954 | -0.20057 | 0 | 0
20 | 0.99265 | -0.1406 | 0.0076963 | 0.0019289
21 | 0.98843 | -0.22225 | 0.0027345 | 0.00068532
22 | 0.98943 | -0.2027 | 0.0027723 | 0.00069481
23 | 0.99501 | -0.095347 | 0.0035394 | 0.00088705
24 | 0.98754 | -0.23936 | 0 | 0
25 | 0.98937 | -0.20396 | 0.0031128 | 0.00078014
26 | 0.99565 | -0.083092 | 0.002527 | 0.00063333
27 | 0.98711 | -0.24789 | 0.021935 | 0.0054973
28 | 0.98745 | -0.24113 | 0.0029215 | 0.0007322
29 | 0.99663 | -0.064302 | 0 | 0
30 | 0.98515 | -0.28591 | 0.0021728 | 0.00054456
31 | 0.98474 | -0.29403 | 0.0054575 | 0.0013678
32 | 0.98533 | -0.28242 | 0.0023408 | 0.00058666
33 | 0.98473 | -0.29413 | 0.01083 | 0.0027144
34 | 0.98553 | -0.27849 | 0.002117 | 0.00053056
35 | 0.98564 | -0.27643 | 0.0023437 | 0.00058739
36 | 0.98637 | -0.26222 | 0.016685 | 0.0041818
37 | 0.98665 | -0.25685 | 0.0087755 | 0.0021994
38 | 0.99727 | -0.051941 | 0 | 0
39 | 0.99568 | -0.082437 | 0.0016275 | 0.0004079
40 | 0.99822 | -0.033876 | 0.0018158 | 0.00045508
41 | 0.99546 | -0.086686 | 0.0034804 | 0.00087226
42 | 0.99434 | -0.10713 | 0.0014145 | 0.0003545
43 | 0.99437 | -0.10666 | 0.0013262 | 0.00033237
44 | 0.99865 | -0.02572 | 0.0028888 | 0.00072401
45 | 0.99494 | -0.0968 | 0.00224 | 0.0005614
46 | 0.9868 | -0.2519 | 0.017922 | 0.0044917
47 | 0.98618 | -0.26404 | 0.0043546 | 0.0010914
48 | 0.98778 | -0.23291 | 0 | 0
49 | 0.98605 | -0.2666 | 0.0021944 | 0.00054997
50 | 0.98856 | -0.21784 | 0.0033807 | 0.00084728
51 | 0.98606 | -0.26612 | 0.0011489 | 0.00028794
52 | 0.98599 | -0.26779 | 0.0023192 | 0.00058123
53 | 0.99093 | -0.17237 | 0 | 0
54 | 0.98574 | -0.27231 | 0.0017575 | 0.00044048
55 | 0.98593 | -0.26893 | 0.0021926 | 0.0005495
56 | 0.99214 | -0.1492 | 0.001393 | 0.00034911
57 | 0.98479 | -0.29077 | 0 | 0
58 | 0.9859 | -0.26953 | 0.002321 | 0.0005817
59 | 0.99351 | -0.123 | 0 | 0
60 | 0.98384 | -0.30911 | 0.0010918 | 0.00027362
61 | 0.98314 | -0.32285 | 0.0015073 | 0.00037777
62 | 0.98448 | -0.29672 | 0.001362 | 0.00034134
63 | 0.99157 | -0.16185 | 0.0059563 | 0.0014928
64 | 0.99127 | -0.16762 | 0.0032274 | 0.00080887
65 | 0.99192 | -0.15505 | 0.0065501 | 0.0016416
66 | 0.99125 | -0.16819 | 0.0043958 | 0.0011017
67 | 0.99238 | -0.14629 | 0.0016979 | 0.00042554
68 | 0.99107 | -0.17156 | 0.0033006 | 0.0008272
69 | 0.99276 | -0.1388 | 0.0020294 | 0.00050862
70 | 0.99094 | -0.17402 | 0.0022997 | 0.00057637
71 | 0.99371 | -0.12055 | 0.0037365 | 0.00093646
72 | 0.99094 | -0.17411 | 0.0025508 | 0.00063929
73 | 0.99749 | -0.047434 | 0.0030213 | 0.00075721
74 | 0.99575 | -0.080396 | 0.0027667 | 0.0006934
75 | 1 | 0 | -0.37781 | -0.096297
76 | 0.99444 | -0.10535 | 0 | 0
77 | 0.99346 | -0.124 | 0.0008335 | 0.00020889
78 | 0.99341 | -0.12488 | 0.0012608 | 0.00031598
79 | 0.99462 | -0.10285 | 0.0018369 | 0.00046038
80 | 0.99341 | -0.12492 | 0.00083819 | 0.00021007
81 | 0.99341 | -0.12503 | 0.0017289 | 0.00043331
82 | 0.98051 | -0.37403 | 0.0038538 | 0.00096585
83 | 0.98067 | -0.37076 | 0.0032529 | 0.00081526
84 | 0.97895 | -0.40441 | 0 | 0
85 | 0.98098 | -0.36469 | 0.0031384 | 0.00078655
86 | 0.97858 | -0.41176 | 0 | 0
87 | 0.97868 | -0.40982 | 0.0024422 | 0.00061207
88 | 0.9825 | -0.33524 | 0.0025737 | 0.00064502
89 | 0.9775 | -0.43285 | 0.0016219 | 0.00040649
90 | 0.97786 | -0.42591 | 0.0029522 | 0.0007399
91 | 0.97864 | -0.41048 | 0.006485 | 0.0016253
92 | 0.97746 | -0.43358 | 0.0030821 | 0.00077244
93 | 0.97675 | -0.44772 | 0.0032246 | 0.00080816
94 | 0.98434 | -0.29946 | 0.0028008 | 0.00070194
95 | 0.98434 | -0.29949 | 0.0011932 | 0.00029905
96 | 0.98443 | -0.29777 | 0.0020398 | 0.00051122
97 | 0.98433 | -0.29967 | 0.00194 | 0.00048621
98 | 0.98431 | -0.30003 | 0.0007683 | 0.00019255
99 | 0.98226 | -0.33994 | 0.0016544 | 0.00041464
100 | 0.97652 | -0.45222 | 0.0020626 | 0.00051694
101 | 0.98198 | -0.34543 | 0.0012653 | 0.00031712
102 | 0.98171 | -0.35064 | 0.0014033 | 0.00035169
103 | 0.97833 | -0.41688 | 0.0075802 | 0.0018998
104 | 0.97856 | -0.41241 | 0.003787 | 0.0009491
105 | 0.97832 | -0.41712 | 0.0012944 | 0.00032441
106 | 0.97863 | -0.41096 | 0 | 0
107 | 0.97844 | -0.41481 | 0.0036277 | 0.00090918
108 | 0.97951 | -0.39377 | 0.0046444 | 0.001164
109 | 0.97825 | -0.41843 | 0.0028245 | 0.00070788
110 | 0.97983 | -0.38749 | 0.0042066 | 0.0010543
111 | 0.97815 | -0.42044 | 0.0073646 | 0.0018458
112 | 0.97988 | -0.38648 | 0.0027542 | 0.00069026
113 | 0.98069 | -0.37062 | 0.002055 | 0.00051504
114 | 0.97672 | -0.44816 | 0.0064336 | 0.0016124
115 | 0.97647 | -0.4531 | 0.0032207 | 0.00080718
116 | 0.97634 | -0.45561 | 0.0029038 | 0.00072775
117 | 0.97602 | -0.46192 | 0.0022157 | 0.00055532
118 | 0.976 | -0.46247 | 0.0037101 | 0.00092985
119 | 0.97556 | -0.47111 | 0 | 0
120 | 0.97549 | -0.47244 | 0.0031516 | 0.00078988
121 | 0.97545 | -0.47328 | 0.0012067 | 0.00030243
122 | 0.97547 | -0.47284 | 0.00085553 | 0.00021442
123 | 0.97539 | -0.47432 | 0.00072033 | 0.00018053
124 | 0.97546 | -0.47308 | 0 | 0
125 | 0.97534 | -0.47545 | 0.0025813 | 0.00064694
126 | 0.97545 | -0.47318 | 0.00072293 | 0.00018118
127 | 0.97531 | -0.47593 | 0.0046475 | 0.0011648
128 | 0.97545 | -0.47326 | 0.00074416 | 0.0001865
129 | 0.97528 | -0.47651 | 0.0007378 | 0.00018491
130 | 0.97528 | -0.47662 | 0.00077596 | 0.00019447
131 | 0.98094 | -0.36576 | 0.0011279 | 0.00028268
132 | 0.98119 | -0.36082 | 0.0010831 | 0.00027145
133 | 0.98144 | -0.35586 | 0.0010907 | 0.00027335
134 | 0.98588 | -0.26998 | 0 | 0
135 | 0.98587 | -0.27017 | 0.0021908 | 0.00054907
136 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0042639 | -0.0010686 | 0.004264 | 0.0010686 | 6.3555e-08 | -9.3349e-09 | 0.0065043 | 0.0065043 | 0.0065043 | 0.97547 | -0.47289 | 0.97548 | -0.47258 | 1.7869
1 | -0.0046436 | -0.0011638 | 0.0046442 | 0.0011638 | 5.4606e-07 | -1.2876e-08 | 0.0070835 | 0.0070833 | 0.0070835 | 0.97548 | -0.47258 | 0.97561 | -0.47011 | 1.946
2 | -0.0055671 | -0.0013951 | 0.0055675 | 0.0013951 | 3.8919e-07 | 6.9314e-08 | 0.008491 | 0.0084909 | 0.008491 | 0.97561 | -0.47011 | 0.97568 | -0.46864 | 2.3327
3 | 0.0070385 | 0.0017638 | -0.0070375 | -0.0017635 | 9.4453e-07 | 3.3087e-07 | 0.010728 | 0.010728 | 0.010728 | 0.97628 | -0.45687 | 0.97614 | -0.45968 | 2.9472
4 | -0.0093319 | -0.0023386 | 0.0093333 | 0.0023392 | 1.3717e-06 | 6.5175e-07 | 0.014223 | 0.014223 | 0.014223 | 0.97628 | -0.45687 | 0.97644 | -0.45378 | 3.9075
5 | 0.0065367 | 0.001638 | -0.0065366 | -0.0016379 | 1.7332e-07 | 5.2738e-08 | 0.0099644 | 0.0099645 | 0.0099645 | 0.97614 | -0.45968 | 0.97611 | -0.46024 | 2.7375
6 | -0.011867 | -0.0029743 | 0.011868 | 0.0029748 | 8.8361e-07 | 4.7538e-07 | 0.018085 | 0.018085 | 0.018085 | 0.97644 | -0.45378 | 0.97652 | -0.45222 | 4.9683
7 | -0.0055675 | -0.0013951 | 0.0055691 | 0.0013954 | 1.5784e-06 | 2.8081e-07 | 0.0084909 | 0.0084907 | 0.0084909 | 0.97568 | -0.46864 | 0.97599 | -0.46269 | 2.3327
8 | 0.0060294 | 0.0015108 | -0.0060287 | -0.0015106 | 7.0383e-07 | 1.7278e-07 | 0.0091913 | 0.0091914 | 0.0091914 | 0.97611 | -0.46024 | 0.97599 | -0.46269 | 2.5251
9 | -0.002054 | -0.00051477 | 0.0020541 | 0.00051435 | 1.5122e-07 | -4.1908e-07 | 0.0031286 | 0.0031285 | 0.0031286 | 0.97689 | -0.44489 | 0.97697 | -0.44335 | 0.85952
10 | -0.0036653 | -0.00091816 | 0.0036656 | 0.00091804 | 2.7445e-07 | -1.1845e-07 | 0.0055825 | 0.0055824 | 0.0055825 | 0.97697 | -0.44335 | 0.97705 | -0.44177 | 1.5336
11 | 0.019649 | 0.0049275 | -0.019647 | -0.0049266 | 1.4856e-06 | 8.9537e-07 | 0.029926 | 0.029926 | 0.029926 | 0.97705 | -0.44177 | 0.97697 | -0.44336 | 8.2213
12 | -0.023314 | -0.0058455 | 0.023316 | 0.0058468 | 2.1288e-06 | 1.306e-06 | 0.035508 | 0.035508 | 0.035508 | 0.97705 | -0.44177 | 0.97715 | -0.43986 | 9.7549
13 | 0.01609 | 0.0040351 | -0.016085 | -0.0040319 | 5.564e-06 | 3.2518e-06 | 0.024508 | 0.024508 | 0.024508 | 0.97697 | -0.44336 | 0.9766 | -0.45062 | 6.733
14 | -0.026491 | -0.0066424 | 0.026498 | 0.0066467 | 6.9651e-06 | 4.3147e-06 | 0.040342 | 0.040341 | 0.040342 | 0.97715 | -0.43986 | 0.97743 | -0.43434 | 11.0828
15 | 0.013932 | 0.0034923 | -0.013931 | -0.0034917 | 1.0623e-06 | 6.0122e-07 | 0.021228 | 0.021228 | 0.021228 | 0.9766 | -0.45062 | 0.97652 | -0.45222 | 5.8318
16 | -0.028207 | -0.0070751 | 0.028209 | 0.0070764 | 2.0006e-06 | 1.2441e-06 | 0.042944 | 0.042944 | 0.042944 | 0.97743 | -0.43434 | 0.9775 | -0.43285 | 11.7978
17 | 0.086398 | 0.021779 | -0.086355 | -0.021752 | 4.2612e-05 | 2.7185e-05 | 0.12981 | 0.12981 | 0.12981 | 0.9907 | -0.17828 | 0.99016 | -0.18859 | 35.6629
18 | -0.089136 | -0.022465 | 0.08929 | 0.022564 | 0.00015491 | 9.8845e-05 | 0.13393 | 0.13393 | 0.13393 | 0.9907 | -0.17828 | 0.99258 | -0.14202 | 36.7927
19 | 0.084486 | 0.021283 | -0.084438 | -0.021253 | 4.837e-05 | 3.0854e-05 | 0.127 | 0.127 | 0.127 | 0.99016 | -0.18859 | 0.98954 | -0.20057 | 34.8914
20 | -0.097716 | -0.024676 | 0.097723 | 0.02468 | 6.6579e-06 | 4.2504e-06 | 0.14656 | 0.14656 | 0.14656 | 0.99258 | -0.14202 | 0.99265 | -0.1406 | 40.2627
21 | 0.078552 | 0.019778 | -0.078471 | -0.019726 | 8.1337e-05 | 5.1856e-05 | 0.11815 | 0.11815 | 0.11815 | 0.98954 | -0.20057 | 0.98843 | -0.22225 | 32.4599
22 | 0.0058859 | 0.0014749 | -0.0058853 | -0.0014748 | 5.9832e-07 | 1.2131e-07 | 0.0088507 | 0.0088508 | 0.0088508 | 0.98954 | -0.20057 | 0.98943 | -0.2027 | 2.4315
23 | -0.10542 | -0.026609 | 0.10565 | 0.026755 | 0.00022905 | 0.00014628 | 0.15809 | 0.15809 | 0.15809 | 0.99265 | -0.1406 | 0.99501 | -0.095347 | 43.4322
24 | 0.075736 | 0.01904 | -0.075674 | -0.019001 | 6.1825e-05 | 3.9406e-05 | 0.11404 | 0.11404 | 0.11404 | 0.98843 | -0.22225 | 0.98754 | -0.23936 | 31.329
25 | 0.003113 | 0.00077997 | -0.0031128 | -0.00078014 | 1.8668e-07 | -1.7223e-07 | 0.0046816 | 0.0046817 | 0.0046817 | 0.98943 | -0.2027 | 0.98937 | -0.20396 | 1.2862
26 | -0.10919 | -0.027642 | 0.10925 | 0.027683 | 6.4283e-05 | 4.1058e-05 | 0.16339 | 0.16339 | 0.16339 | 0.99501 | -0.095347 | 0.99565 | -0.083092 | 44.8863
27 | 0.021943 | 0.0055027 | -0.021935 | -0.0054973 | 8.9159e-06 | 5.4281e-06 | 0.033065 | 0.033065 | 0.033065 | 0.98754 | -0.23936 | 0.98711 | -0.24789 | 9.0839
28 | 0.053731 | 0.013498 | -0.053726 | -0.013495 | 4.5278e-06 | 2.8742e-06 | 0.080972 | 0.080972 | 0.080972 | 0.98754 | -0.23936 | 0.98745 | -0.24113 | 22.2451
29 | -0.11178 | -0.028316 | 0.11188 | 0.028381 | 0.00010098 | 6.4503e-05 | 0.16716 | 0.16716 | 0.16716 | 0.99565 | -0.083092 | 0.99663 | -0.064302 | 45.9238
30 | 0.050805 | 0.012763 | -0.050767 | -0.012739 | 3.8077e-05 | 2.4148e-05 | 0.07657 | 0.07657 | 0.07657 | 0.98745 | -0.24113 | 0.98665 | -0.25685 | 21.0357
31 | -0.15698 | -0.039749 | 0.15707 | 0.039808 | 9.3238e-05 | 5.9437e-05 | 0.23452 | 0.23452 | 0.23452 | 0.99663 | -0.064302 | 0.99727 | -0.051941 | 32.2149
32 | 0.045102 | 0.011368 | -0.045063 | -0.011343 | 3.9096e-05 | 2.4722e-05 | 0.067362 | 0.067362 | 0.067362 | 0.99663 | -0.064302 | 0.99568 | -0.082437 | 18.5061
33 | 0.016294 | 0.0040859 | -0.016288 | -0.0040822 | 6.3005e-06 | 3.6793e-06 | 0.024612 | 0.024613 | 0.024613 | 0.98515 | -0.28591 | 0.98474 | -0.29403 | 6.7617
34 | -0.018467 | -0.0046304 | 0.01847 | 0.0046323 | 3.0776e-06 | 1.8353e-06 | 0.027894 | 0.027894 | 0.027894 | 0.98515 | -0.28591 | 0.98533 | -0.28242 | 7.6633
35 | 0.010831 | 0.0027144 | -0.01083 | -0.0027144 | 5.0166e-08 | 2.5752e-08 | 0.016366 | 0.016366 | 0.016366 | 0.98474 | -0.29403 | 0.98473 | -0.29413 | 4.4961
36 | -0.020811 | -0.0052189 | 0.020815 | 0.0052213 | 3.8939e-06 | 2.3582e-06 | 0.031429 | 0.031429 | 0.031429 | 0.98533 | -0.28242 | 0.98553 | -0.27849 | 8.6344
37 | -0.022932 | -0.0057518 | 0.022934 | 0.0057532 | 2.256e-06 | 1.3799e-06 | 0.034626 | 0.034626 | 0.034626 | 0.98553 | -0.27849 | 0.98564 | -0.27643 | 9.5125
38 | -0.025278 | -0.0063406 | 0.025295 | 0.0063512 | 1.7127e-05 | 1.0561e-05 | 0.038164 | 0.038164 | 0.038164 | 0.98564 | -0.27643 | 0.98637 | -0.26222 | 10.4846
39 | -0.04198 | -0.010533 | 0.041991 | 0.01054 | 1.0768e-05 | 6.8002e-06 | 0.063335 | 0.063335 | 0.063335 | 0.98637 | -0.26222 | 0.98665 | -0.25685 | 17.3997
40 | -0.15707 | -0.039808 | 0.15721 | 0.039895 | 0.00013647 | 8.6994e-05 | 0.23452 | 0.23452 | 0.23452 | 0.99727 | -0.051941 | 0.99822 | -0.033876 | 32.2149
41 | 0.043435 | 0.010935 | -0.043426 | -0.010929 | 8.8209e-06 | 5.5728e-06 | 0.06493 | 0.06493 | 0.06493 | 0.99568 | -0.082437 | 0.99546 | -0.086686 | 17.8379
42 | -0.15903 | -0.04035 | 0.15909 | 0.04039 | 6.2403e-05 | 3.9783e-05 | 0.23723 | 0.23723 | 0.23723 | 0.99822 | -0.033876 | 0.99865 | -0.02572 | 32.5867
43 | 0.039946 | 0.010057 | -0.039927 | -0.010045 | 1.9304e-05 | 1.2167e-05 | 0.059727 | 0.059727 | 0.059727 | 0.99546 | -0.086686 | 0.99494 | -0.0968 | 16.4086
44 | -0.0014145 | -0.0003545 | 0.0014145 | 0.00035428 | 3.1729e-08 | -2.2465e-07 | 0.0021167 | 0.0021167 | 0.0021167 | 0.99434 | -0.10713 | 0.99437 | -0.10666 | 0.58152
45 | -0.0027407 | -0.00068665 | 0.0027409 | 0.00068641 | 1.6983e-07 | -2.4062e-07 | 0.0041012 | 0.0041011 | 0.0041012 | 0.99437 | -0.10666 | 0.99444 | -0.10535 | 1.1267
46 | -0.16198 | -0.041114 | 0.16218 | 0.041242 | 0.00020069 | 0.00012796 | 0.24154 | 0.24154 | 0.24154 | 0.99865 | -0.02572 | 1 | 0 | 33.178
47 | 0.037687 | 0.0094836 | -0.037676 | -0.0094768 | 1.0898e-05 | 6.8561e-06 | 0.056377 | 0.056377 | 0.056377 | 0.99494 | -0.0968 | 0.99462 | -0.10285 | 15.4883
48 | 0.015584 | 0.003909 | -0.015575 | -0.0039037 | 9.0171e-06 | 5.2151e-06 | 0.023501 | 0.023501 | 0.023501 | 0.9868 | -0.2519 | 0.98618 | -0.26404 | 6.4563
49 | -0.033506 | -0.0084006 | 0.033536 | 0.0084197 | 3.0352e-05 | 1.902e-05 | 0.050525 | 0.050525 | 0.050525 | 0.9868 | -0.2519 | 0.98778 | -0.23291 | 13.8806
50 | 0.01122 | 0.0028124 | -0.011219 | -0.0028117 | 1.3667e-06 | 7.1246e-07 | 0.01693 | 0.01693 | 0.01693 | 0.98618 | -0.26404 | 0.98605 | -0.2666 | 4.6512
51 | -0.19372 | -0.049086 | 0.19386 | 0.049176 | 0.00014037 | 8.961e-05 | 0.29201 | 0.29201 | 0.29201 | 0.98778 | -0.23291 | 0.98856 | -0.21784 | 40.1119
52 | 0.16018 | 0.040666 | -0.15993 | -0.040503 | 0.00025549 | 0.00016292 | 0.24149 | 0.24149 | 0.24149 | 0.98778 | -0.23291 | 0.98606 | -0.26612 | 33.1716
53 | 0.0090246 | 0.0022617 | -0.0090241 | -0.0022614 | 5.1146e-07 | 2.3354e-07 | 0.013619 | 0.013619 | 0.013619 | 0.98605 | -0.2666 | 0.98599 | -0.26779 | 3.7414
54 | -0.19724 | -0.050023 | 0.19767 | 0.050299 | 0.00043214 | 0.0002759 | 0.2971 | 0.2971 | 0.2971 | 0.98856 | -0.21784 | 0.99093 | -0.17237 | 40.8109
55 | 0.15878 | 0.040216 | -0.15873 | -0.040185 | 4.7242e-05 | 3.0123e-05 | 0.23976 | 0.23976 | 0.23976 | 0.98606 | -0.26612 | 0.98574 | -0.27231 | 32.9335
56 | 0.006705 | 0.0016802 | -0.0067046 | -0.0016801 | 3.6412e-07 | 1.1209e-07 | 0.010119 | 0.010119 | 0.010119 | 0.98599 | -0.26779 | 0.98593 | -0.26893 | 2.7799
57 | -0.19767 | -0.050299 | 0.19789 | 0.05044 | 0.00022109 | 0.00014116 | 0.2971 | 0.2971 | 0.2971 | 0.99093 | -0.17237 | 0.99214 | -0.1492 | 40.8108
58 | 0.15697 | 0.039745 | -0.15683 | -0.039656 | 0.00013897 | 8.8608e-05 | 0.2371 | 0.2371 | 0.2371 | 0.98574 | -0.27231 | 0.98479 | -0.29077 | 32.5691
59 | 0.004512 | 0.0011306 | -0.0045119 | -0.0011306 | 1.2788e-07 | -1.1934e-08 | 0.0068097 | 0.0068098 | 0.0068098 | 0.98593 | -0.26893 | 0.9859 | -0.26953 | 1.8708
60 | -0.19929 | -0.050789 | 0.19954 | 0.05095 | 0.00025227 | 0.00016106 | 0.29919 | 0.29919 | 0.29919 | 0.99214 | -0.1492 | 0.99351 | -0.123 | 41.0978
61 | 0.097208 | 0.024619 | -0.097123 | -0.024564 | 8.5526e-05 | 5.4602e-05 | 0.14697 | 0.14697 | 0.14697 | 0.98479 | -0.29077 | 0.98384 | -0.30911 | 40.3775
62 | 0.049518 | 0.012504 | -0.049442 | -0.012456 | 7.5987e-05 | 4.8173e-05 | 0.074856 | 0.074856 | 0.074856 | 0.98479 | -0.29077 | 0.98314 | -0.32285 | 20.5648
63 | 0.010108 | 0.0025337 | -0.010105 | -0.0025323 | 2.8668e-06 | 1.4179e-06 | 0.015273 | 0.015273 | 0.015273 | 0.98479 | -0.29077 | 0.98448 | -0.29672 | 4.196
64 | 0.0021909 | 0.00054891 | -0.0021908 | -0.00054903 | 4.7573e-08 | -1.175e-07 | 0.0033066 | 0.0033067 | 0.0033067 | 0.9859 | -0.26953 | 0.98588 | -0.26998 | 0.90843
65 | 0.0046618 | 0.0011681 | -0.0046616 | -0.0011681 | 2.2018e-07 | -1.5043e-08 | 0.0069821 | 0.0069821 | 0.0069821 | 0.99351 | -0.123 | 0.99346 | -0.124 | 1.9182
66 | -0.2042 | -0.052118 | 0.20437 | 0.05223 | 0.00017429 | 0.00011129 | 0.30617 | 0.30617 | 0.30617 | 0.99351 | -0.123 | 0.99444 | -0.10535 | 42.0568
67 | 0.096031 | 0.024291 | -0.095911 | -0.024214 | 0.00012024 | 7.676e-05 | 0.14532 | 0.14532 | 0.14532 | 0.98384 | -0.30911 | 0.9825 | -0.33524 | 39.9239
68 | 0.047935 | 0.012078 | -0.047896 | -0.012053 | 3.915e-05 | 2.4805e-05 | 0.072574 | 0.072575 | 0.072575 | 0.98314 | -0.32285 | 0.98226 | -0.33994 | 19.9381
69 | 0.0087431 | 0.002191 | -0.0087426 | -0.0021908 | 4.3587e-07 | 1.9433e-07 | 0.013215 | 0.013215 | 0.013215 | 0.98448 | -0.29672 | 0.98443 | -0.29777 | 3.6305
70 | 0.015781 | 0.0039566 | -0.015777 | -0.0039541 | 4.3398e-06 | 2.5114e-06 | 0.023682 | 0.023682 | 0.023682 | 0.99157 | -0.16185 | 0.99127 | -0.16762 | 6.5062
71 | -0.021737 | -0.0054494 | 0.021744 | 0.0054537 | 7.044e-06 | 4.2804e-06 | 0.032621 | 0.032621 | 0.032621 | 0.99157 | -0.16185 | 0.99192 | -0.15505 | 8.9617
72 | 0.012549 | 0.0031452 | -0.012549 | -0.0031451 | 3.3796e-07 | 1.8356e-07 | 0.018838 | 0.018838 | 0.018838 | 0.99127 | -0.16762 | 0.99125 | -0.16819 | 5.1752
73 | -0.028294 | -0.0070953 | 0.028306 | 0.0071026 | 1.1826e-05 | 7.3423e-06 | 0.042447 | 0.042447 | 0.042447 | 0.99192 | -0.15505 | 0.99238 | -0.14629 | 11.6612
74 | 0.008153 | 0.0020434 | -0.0081517 | -0.0020428 | 1.3084e-06 | 5.3717e-07 | 0.012239 | 0.012239 | 0.012239 | 0.99125 | -0.16819 | 0.99107 | -0.17156 | 3.3624
75 | -0.030004 | -0.0075282 | 0.030015 | 0.0075349 | 1.0712e-05 | 6.6735e-06 | 0.044993 | 0.044992 | 0.044993 | 0.99238 | -0.14629 | 0.99276 | -0.1388 | 12.3606
76 | 0.0048511 | 0.0012156 | -0.0048505 | -0.0012156 | 5.7028e-07 | -4.3673e-09 | 0.0072835 | 0.0072836 | 0.0072836 | 0.99107 | -0.17156 | 0.99094 | -0.17402 | 2.001
77 | -0.032044 | -0.0080435 | 0.032072 | 0.0080609 | 2.7914e-05 | 1.7447e-05 | 0.048034 | 0.048034 | 0.048034 | 0.99276 | -0.1388 | 0.99371 | -0.12055 | 13.1962
78 | 0.0025508 | 0.00063927 | -0.0025508 | -0.00063929 | 1.0414e-08 | -1.772e-08 | 0.0038303 | 0.0038303 | 0.0038303 | 0.99094 | -0.17402 | 0.99094 | -0.17411 | 1.0523
79 | -0.035809 | -0.0089974 | 0.035839 | 0.0090164 | 3.0282e-05 | 1.9016e-05 | 0.053629 | 0.053629 | 0.053629 | 0.99371 | -0.12055 | 0.99462 | -0.10285 | 14.7333
80 | 0.21047 | 0.053984 | -0.21013 | -0.053769 | 0.0003359 | 0.0002145 | 0.31441 | 0.31441 | 0.31441 | 0.99749 | -0.047434 | 0.99575 | -0.080396 | 43.1881
81 | -0.21349 | -0.054741 | 0.21398 | 0.055055 | 0.00049229 | 0.00031439 | 0.31892 | 0.31892 | 0.31892 | 0.99749 | -0.047434 | 1 | 0 | 43.8071
82 | 0.20737 | 0.053076 | -0.20712 | -0.052916 | 0.00025029 | 0.00015982 | 0.31027 | 0.31027 | 0.31027 | 0.99575 | -0.080396 | 0.99444 | -0.10535 | 42.6202
83 | 0.0038281 | 0.00095925 | -0.0038279 | -0.00095931 | 1.613e-07 | -6.6172e-08 | 0.0057337 | 0.0057338 | 0.0057338 | 0.99346 | -0.124 | 0.99341 | -0.12488 | 1.5752
84 | 0.0025671 | 0.00064333 | -0.0025671 | -0.00064334 | 4.5253e-09 | -7.6705e-09 | 0.0038452 | 0.0038452 | 0.0038452 | 0.99341 | -0.12488 | 0.99341 | -0.12492 | 1.0564
85 | 0.0017289 | 0.00043327 | -0.0017289 | -0.00043331 | 9.1259e-09 | -4.1138e-08 | 0.0025897 | 0.0025897 | 0.0025897 | 0.99341 | -0.12492 | 0.99341 | -0.12503 | 0.71147
86 | -0.086775 | -0.021858 | 0.086788 | 0.021866 | 1.3585e-05 | 8.6682e-06 | 0.13173 | 0.13173 | 0.13173 | 0.98051 | -0.37403 | 0.98067 | -0.37076 | 36.1893
87 | 0.082921 | 0.020892 | -0.082801 | -0.020815 | 0.00012031 | 7.6743e-05 | 0.12588 | 0.12588 | 0.12588 | 0.98051 | -0.37403 | 0.97895 | -0.40441 | 34.5825
88 | -0.090041 | -0.022682 | 0.090067 | 0.022698 | 2.6141e-05 | 1.6683e-05 | 0.13666 | 0.13666 | 0.13666 | 0.98067 | -0.37076 | 0.98098 | -0.36469 | 37.5452
89 | 0.073871 | 0.018577 | -0.073845 | -0.01856 | 2.5929e-05 | 1.6526e-05 | 0.11231 | 0.11231 | 0.11231 | 0.97895 | -0.40441 | 0.97858 | -0.41176 | 30.8536
90 | 0.0089297 | 0.0022385 | -0.0089274 | -0.0022374 | 2.3013e-06 | 1.0542e-06 | 0.013573 | 0.013574 | 0.013574 | 0.97895 | -0.40441 | 0.97868 | -0.40982 | 3.729
91 | -0.093206 | -0.023485 | 0.093337 | 0.023569 | 0.00013149 | 8.393e-05 | 0.14143 | 0.14143 | 0.14143 | 0.98098 | -0.36469 | 0.9825 | -0.33524 | 38.8531
92 | 0.029861 | 0.0075016 | -0.029831 | -0.0074829 | 3.0029e-05 | 1.8731e-05 | 0.045413 | 0.045413 | 0.045413 | 0.97858 | -0.41176 | 0.9775 | -0.43285 | 12.4761
93 | 0.043984 | 0.011059 | -0.043954 | -0.01104 | 2.97e-05 | 1.8786e-05 | 0.066894 | 0.066894 | 0.066894 | 0.97858 | -0.41176 | 0.97786 | -0.42591 | 18.3775
94 | 0.0064852 | 0.0016253 | -0.006485 | -0.0016253 | 2.0315e-07 | 6.0002e-08 | 0.0098603 | 0.0098603 | 0.0098603 | 0.97868 | -0.40982 | 0.97864 | -0.41048 | 2.7089
95 | 0.041002 | 0.0103 | -0.040987 | -0.01029 | 1.5004e-05 | 9.4736e-06 | 0.062402 | 0.062402 | 0.062402 | 0.97786 | -0.42591 | 0.97746 | -0.43358 | 17.1434
96 | 0.037905 | 0.009518 | -0.037879 | -0.0095019 | 2.5549e-05 | 1.6095e-05 | 0.05771 | 0.05771 | 0.05771 | 0.97746 | -0.43358 | 0.97675 | -0.44772 | 15.8544
97 | 0.034655 | 0.0086937 | -0.034654 | -0.0086933 | 7.3349e-07 | 4.6065e-07 | 0.052798 | 0.052798 | 0.052798 | 0.97675 | -0.44772 | 0.97672 | -0.44816 | 14.5048
98 | 0.0039015 | 0.00097746 | -0.0039015 | -0.00097746 | 6.5799e-09 | -2.2012e-09 | 0.0058978 | 0.0058978 | 0.0058978 | 0.98434 | -0.29946 | 0.98434 | -0.29949 | 1.6203
99 | -0.0067023 | -0.0016794 | 0.0067028 | 0.0016796 | 5.3878e-07 | 1.6688e-07 | 0.010132 | 0.010132 | 0.010132 | 0.98434 | -0.29946 | 0.98443 | -0.29777 | 2.7834
100 | 0.0027083 | 0.00067841 | -0.0027083 | -0.00067844 | 2.3121e-08 | -3.1961e-08 | 0.004094 | 0.004094 | 0.004094 | 0.98434 | -0.29949 | 0.98433 | -0.29967 | 1.1247
101 | 0.00076831 | 0.00019223 | -0.0007683 | -0.00019255 | 1.3063e-08 | -3.199e-07 | 0.0011613 | 0.0011615 | 0.0011615 | 0.98433 | -0.29967 | 0.98431 | -0.30003 | 0.31908
102 | 0.046241 | 0.011638 | -0.046229 | -0.011631 | 1.2119e-05 | 7.6726e-06 | 0.070068 | 0.070068 | 0.070068 | 0.98226 | -0.33994 | 0.98198 | -0.34543 | 19.2495
103 | 0.044964 | 0.011313 | -0.044953 | -0.011306 | 1.1209e-05 | 7.0926e-06 | 0.068151 | 0.068151 | 0.068151 | 0.98198 | -0.34543 | 0.98171 | -0.35064 | 18.7228
104 | 0.043549 | 0.010955 | -0.043539 | -0.010948 | 1.0844e-05 | 6.8565e-06 | 0.066024 | 0.066024 | 0.066024 | 0.98171 | -0.35064 | 0.98144 | -0.35586 | 18.1385
105 | -0.0088746 | -0.0022241 | 0.0088765 | 0.0022249 | 1.8894e-06 | 8.6189e-07 | 0.013498 | 0.013498 | 0.013498 | 0.97833 | -0.41688 | 0.97856 | -0.41241 | 3.7082
106 | 0.0012944 | 0.00032429 | -0.0012944 | -0.00032441 | 1.4535e-08 | -1.1627e-07 | 0.0019687 | 0.0019688 | 0.0019688 | 0.97833 | -0.41688 | 0.97832 | -0.41712 | 0.54087
107 | -0.012663 | -0.003174 | 0.012664 | 0.0031745 | 8.7654e-07 | 4.8179e-07 | 0.019256 | 0.019256 | 0.019256 | 0.97856 | -0.41241 | 0.97863 | -0.41096 | 5.2902
108 | 0.013822 | 0.0034654 | -0.013819 | -0.0034639 | 2.538e-06 | 1.4318e-06 | 0.021017 | 0.021017 | 0.021017 | 0.97863 | -0.41096 | 0.97844 | -0.41481 | 5.7738
109 | -0.026486 | -0.0066399 | 0.026508 | 0.0066533 | 2.1709e-05 | 1.3445e-05 | 0.040273 | 0.040273 | 0.040273 | 0.97863 | -0.41096 | 0.97951 | -0.39377 | 11.064
110 | 0.010192 | 0.0025548 | -0.01019 | -0.0025539 | 1.7539e-06 | 8.7804e-07 | 0.0155 | 0.0155 | 0.0155 | 0.97844 | -0.41481 | 0.97825 | -0.41843 | 4.2582
111 | -0.031152 | -0.0078173 | 0.031162 | 0.0078232 | 9.3295e-06 | 5.8311e-06 | 0.047328 | 0.047328 | 0.047328 | 0.97951 | -0.39377 | 0.97983 | -0.38749 | 13.0023
112 | 0.0073653 | 0.001846 | -0.0073646 | -0.0018458 | 7.062e-07 | 2.6362e-07 | 0.011203 | 0.011204 | 0.011204 | 0.97825 | -0.41843 | 0.97815 | -0.42044 | 3.0779
113 | -0.035368 | -0.0088774 | 0.03537 | 0.0088785 | 1.7063e-06 | 1.0721e-06 | 0.053717 | 0.053717 | 0.053717 | 0.97983 | -0.38749 | 0.97988 | -0.38648 | 14.7573
114 | -0.038124 | -0.0095688 | 0.038153 | 0.0095869 | 2.8863e-05 | 1.8183e-05 | 0.057899 | 0.057899 | 0.057899 | 0.97988 | -0.38648 | 0.98069 | -0.37062 | 15.9063
115 | -0.040208 | -0.010102 | 0.040217 | 0.010108 | 9.3344e-06 | 5.8897e-06 | 0.061017 | 0.061017 | 0.061017 | 0.98069 | -0.37062 | 0.98094 | -0.36576 | 16.7629
116 | 0.02822 | 0.0070809 | -0.028214 | -0.0070767 | 6.6466e-06 | 4.1339e-06 | 0.042996 | 0.042996 | 0.042996 | 0.97672 | -0.44816 | 0.97647 | -0.4531 | 11.8121
117 | 0.024993 | 0.0062695 | -0.02499 | -0.0062677 | 2.9815e-06 | 1.8396e-06 | 0.038088 | 0.038088 | 0.038088 | 0.97647 | -0.4531 | 0.97634 | -0.45561 | 10.4638
118 | 0.022086 | 0.0055399 | -0.02208 | -0.0055359 | 6.6461e-06 | 4.058e-06 | 0.033663 | 0.033663 | 0.033663 | 0.97634 | -0.45561 | 0.97602 | -0.46192 | 9.248
119 | 0.019864 | 0.0049806 | -0.019863 | -0.0049803 | 5.2293e-07 | 3.1567e-07 | 0.030285 | 0.030285 | 0.030285 | 0.97602 | -0.46192 | 0.976 | -0.46247 | 8.32
120 | 0.016153 | 0.0040504 | -0.016147 | -0.0040465 | 6.6467e-06 | 3.8888e-06 | 0.024628 | 0.024628 | 0.024628 | 0.976 | -0.46247 | 0.97556 | -0.47111 | 6.766
121 | 0.0054747 | 0.0013717 | -0.0054743 | -0.0013717 | 3.4707e-07 | 5.6413e-08 | 0.0083504 | 0.0083505 | 0.0083505 | 0.97556 | -0.47111 | 0.97549 | -0.47244 | 2.2941
122 | 0.010672 | 0.0026748 | -0.010671 | -0.0026742 | 1.1027e-06 | 5.6718e-07 | 0.016278 | 0.016278 | 0.016278 | 0.97556 | -0.47111 | 0.97545 | -0.47328 | 4.472
123 | 0.0023227 | 0.0005818 | -0.0023226 | -0.00058189 | 4.3531e-08 | -8.7588e-08 | 0.0035429 | 0.003543 | 0.003543 | 0.97549 | -0.47244 | 0.97547 | -0.47284 | 0.97334
124 | 0.0094641 | 0.0023718 | -0.0094636 | -0.0023716 | 4.6993e-07 | 2.2571e-07 | 0.014437 | 0.014437 | 0.014437 | 0.97545 | -0.47328 | 0.97539 | -0.47432 | 3.9662
125 | 0.0014671 | 0.00036747 | -0.0014671 | -0.00036757 | 1.7058e-08 | -1.0247e-07 | 0.0022379 | 0.0022379 | 0.0022379 | 0.97547 | -0.47284 | 0.97546 | -0.47308 | 0.61482
126 | 0.0087433 | 0.002191 | -0.0087428 | -0.0021908 | 4.6923e-07 | 2.1253e-07 | 0.013338 | 0.013338 | 0.013338 | 0.97539 | -0.47432 | 0.97534 | -0.47545 | 3.6644
127 | 0.0014671 | 0.00036757 | -0.0014671 | -0.00036761 | 6.6092e-09 | -3.9698e-08 | 0.0022379 | 0.002238 | 0.002238 | 0.97546 | -0.47308 | 0.97545 | -0.47318 | 0.61483
128 | 0.0061615 | 0.0015439 | -0.0061613 | -0.0015438 | 1.4181e-07 | 3.7348e-08 | 0.0094001 | 0.0094001 | 0.0094001 | 0.97534 | -0.47545 | 0.97531 | -0.47593 | 2.5824
129 | 0.00074416 | 0.00018643 | -0.00074416 | -0.0001865 | 2.933e-09 | -7.3888e-08 | 0.0011352 | 0.0011352 | 0.0011352 | 0.97545 | -0.47318 | 0.97545 | -0.47326 | 0.31187
130 | 0.0015138 | 0.00037906 | -0.0015138 | -0.00037929 | 4.1478e-08 | -2.3223e-07 | 0.0023095 | 0.0023096 | 0.0023096 | 0.97531 | -0.47593 | 0.97528 | -0.47651 | 0.63449
131 | 0.00077596 | 0.00019438 | -0.00077596 | -0.00019447 | 4.0199e-09 | -9.2867e-08 | 0.0011839 | 0.0011839 | 0.0011839 | 0.97528 | -0.47651 | 0.97528 | -0.47662 | 0.32525
132 | -0.041345 | -0.010391 | 0.041355 | 0.010397 | 9.7567e-06 | 6.1608e-06 | 0.062728 | 0.062728 | 0.062728 | 0.98094 | -0.36576 | 0.98119 | -0.36082 | 17.2329
133 | -0.042438 | -0.010668 | 0.042448 | 0.010675 | 1.0053e-05 | 6.352e-06 | 0.06437 | 0.06437 | 0.06437 | 0.98119 | -0.36082 | 0.98144 | -0.35586 | 17.6842
134 | 0.0021908 | 0.00054903 | -0.0021908 | -0.00054907 | 1.926e-08 | -4.7567e-08 | 0.0033067 | 0.0033067 | 0.0033067 | 0.98588 | -0.26998 | 0.98587 | -0.27017 | 0.90844

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.38059 | 0.096993

## res_load
| p_mw | q_mvar
0 | 0.0042639 | 0.0010686
1 | 0.00037966 | 9.5152e-05
2 | 0.00092294 | 0.00023131
3 | 0.0022934 | 0.00057479
4 | 0.00050076 | 0.0001255
5 | 0.0025339 | 0.00063506
6 | 0.00050718 | 0.00012711
7 | 0.0004596 | 0.00011519
8 | 0.002054 | 0.00051477
9 | 0.0016112 | 0.00040381
10 | 0.003557 | 0.00089147
11 | 0.0031742 | 0.00079552
12 | 0.0021529 | 0.00053957
13 | 0.0017096 | 0.00042847
14 | 0.002738 | 0.0006862
15 | 0.0018688 | 0.00046837
16 | 0.0084255 | 0.0021116
17 | 0.0076963 | 0.0019289
18 | 0.0027345 | 0.00068532
19 | 0.0027723 | 0.00069481
20 | 0.0035394 | 0.00088705
21 | 0.0031128 | 0.00078014
22 | 0.002527 | 0.00063333
23 | 0.021935 | 0.0054973
24 | 0.0029215 | 0.0007322
25 | 0.0021728 | 0.00054456
26 | 0.0054575 | 0.0013678
27 | 0.0023408 | 0.00058666
28 | 0.01083 | 0.0027144
29 | 0.002117 | 0.00053056
30 | 0.0023437 | 0.00058739
31 | 0.016685 | 0.0041818
32 | 0.0087755 | 0.0021994
33 | 0.0016275 | 0.0004079
34 | 0.0018158 | 0.00045508
35 | 0.0034804 | 0.00087226
36 | 0.0014145 | 0.0003545
37 | 0.0013262 | 0.00033237
38 | 0.0028888 | 0.00072401
39 | 0.00224 | 0.0005614
40 | 0.017922 | 0.0044917
41 | 0.0043546 | 0.0010914
42 | 0.0021944 | 0.00054997
43 | 0.0033807 | 0.00084728
44 | 0.0011489 | 0.00028794
45 | 0.0023192 | 0.00058123
46 | 0.0017575 | 0.00044048
47 | 0.0021926 | 0.0005495
48 | 0.001393 | 0.00034911
49 | 0.002321 | 0.0005817
50 | 0.0010918 | 0.00027362
51 | 0.0015073 | 0.00037777
52 | 0.001362 | 0.00034134
53 | 0.0059563 | 0.0014928
54 | 0.0032274 | 0.00080887
55 | 0.0065501 | 0.0016416
56 | 0.0043958 | 0.0011017
57 | 0.0016979 | 0.00042554
58 | 0.0033006 | 0.0008272
59 | 0.0020294 | 0.00050862
60 | 0.0022997 | 0.00057637
61 | 0.0037365 | 0.00093646
62 | 0.0025508 | 0.00063929
63 | 0.0030213 | 0.00075721
64 | 0.0027667 | 0.0006934
65 | 0.0027772 | 0.00069603
66 | 0.0008335 | 0.00020889
67 | 0.0012608 | 0.00031598
68 | 0.0018369 | 0.00046038
69 | 0.00083819 | 0.00021007
70 | 0.0017289 | 0.00043331
71 | 0.0038538 | 0.00096585
72 | 0.0032529 | 0.00081526
73 | 0.0031384 | 0.00078655
74 | 0.0024422 | 0.00061207
75 | 0.0025737 | 0.00064502
76 | 0.0016219 | 0.00040649
77 | 0.0029522 | 0.0007399
78 | 0.006485 | 0.0016253
79 | 0.0030821 | 0.00077244
80 | 0.0032246 | 0.00080816
81 | 0.0028008 | 0.00070194
82 | 0.0011932 | 0.00029905
83 | 0.0020398 | 0.00051122
84 | 0.00194 | 0.00048621
85 | 0.0007683 | 0.00019255
86 | 0.0016544 | 0.00041464
87 | 0.0020626 | 0.00051694
88 | 0.0012653 | 0.00031712
89 | 0.0014033 | 0.00035169
90 | 0.0075802 | 0.0018998
91 | 0.003787 | 0.0009491
92 | 0.0012944 | 0.00032441
93 | 0.0036277 | 0.00090918
94 | 0.0046444 | 0.001164
95 | 0.0028245 | 0.00070788
96 | 0.0042066 | 0.0010543
97 | 0.0073646 | 0.0018458
98 | 0.0027542 | 0.00069026
99 | 0.002055 | 0.00051504
100 | 0.0064336 | 0.0016124
101 | 0.0032207 | 0.00080718
102 | 0.0029038 | 0.00072775
103 | 0.0022157 | 0.00055532
104 | 0.0037101 | 0.00092985
105 | 0.0031516 | 0.00078988
106 | 0.0012067 | 0.00030243
107 | 0.00085553 | 0.00021442
108 | 0.00072033 | 0.00018053
109 | 0.0025813 | 0.00064694
110 | 0.00072293 | 0.00018118
111 | 0.0046475 | 0.0011648
112 | 0.00074416 | 0.0001865
113 | 0.0007378 | 0.00018491
114 | 0.00077596 | 0.00019447
115 | 0.0011279 | 0.00028268
116 | 0.0010831 | 0.00027145
117 | 0.0010907 | 0.00027335
118 | 0.0021908 | 0.00054907

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1