## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_131-17_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_131-17_0_5_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_131-17_0_5_node_7 | 0.4 | n |  | TRUE
3 | bus_LV_131-17_0_5_node_8 | 0.4 | n |  | TRUE
4 | bus_LV_131-17_0_5_node_132 | 0.4 | n |  | TRUE
5 | bus_LV_131-17_0_5_node_143 | 0.4 | n |  | TRUE
6 | bus_LV_131-17_0_5_node_55 | 0.4 | n |  | TRUE
7 | bus_LV_131-17_0_5_node_54 | 0.4 | n |  | TRUE
8 | bus_LV_131-17_0_5_node_112 | 0.4 | n |  | TRUE
9 | bus_LV_131-17_0_5_node_111 | 0.4 | n |  | TRUE
10 | bus_LV_131-17_0_5_node_42 | 0.4 | n |  | TRUE
11 | bus_LV_131-17_0_5_node_43 | 0.4 | n |  | TRUE
12 | bus_LV_131-17_0_5_node_133 | 0.4 | n |  | TRUE
13 | bus_LV_131-17_0_5_node_134 | 0.4 | n |  | TRUE
14 | bus_LV_131-17_0_5_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_131-17_0_5_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_131-17_0_5_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_131-17_0_5_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_131-17_0_5_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_131-17_0_5_node_75 | 0.4 | n |  | TRUE
20 | bus_LV_131-17_0_5_node_89 | 0.4 | n |  | TRUE
21 | bus_LV_131-17_0_5_node_137 | 0.4 | n |  | TRUE
22 | bus_LV_131-17_0_5_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_131-17_0_5_node_129 | 0.4 | n |  | TRUE
24 | bus_LV_131-17_0_5_node_127 | 0.4 | n |  | TRUE
25 | bus_LV_131-17_0_5_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_131-17_0_5_node_21 | 0.4 | n |  | TRUE
27 | bus_LV_131-17_0_5_node_83 | 0.4 | n |  | TRUE
28 | bus_LV_131-17_0_5_node_19 | 0.4 | n |  | TRUE
29 | bus_LV_131-17_0_5_node_35 | 0.4 | n |  | TRUE
30 | bus_LV_131-17_0_5_node_117 | 0.4 | n |  | TRUE
31 | bus_LV_131-17_0_5_node_20 | 0.4 | n |  | TRUE
32 | bus_LV_131-17_0_5_node_22 | 0.4 | n |  | TRUE
33 | bus_LV_131-17_0_5_node_116 | 0.4 | n |  | TRUE
34 | bus_LV_131-17_0_5_node_130 | 0.4 | n |  | TRUE
35 | bus_LV_131-17_0_5_node_141 | 0.4 | n |  | TRUE
36 | bus_LV_131-17_0_5_node_147 | 0.4 | n |  | TRUE
37 | bus_LV_131-17_0_5_node_23 | 0.4 | n |  | TRUE
38 | bus_LV_131-17_0_5_node_79 | 0.4 | n |  | TRUE
39 | bus_LV_131-17_0_5_node_73 | 0.4 | n |  | TRUE
40 | bus_LV_131-17_0_5_node_90 | 0.4 | n |  | TRUE
41 | bus_LV_131-17_0_5_node_138 | 0.4 | n |  | TRUE
42 | bus_LV_131-17_0_5_node_128 | 0.4 | n |  | TRUE
43 | bus_LV_131-17_0_5_node_69 | 0.4 | n |  | TRUE
44 | bus_LV_131-17_0_5_node_70 | 0.4 | n |  | TRUE
45 | bus_LV_131-17_0_5_node_36 | 0.4 | n |  | TRUE
46 | bus_LV_131-17_0_5_node_140 | 0.4 | n |  | TRUE
47 | bus_LV_131-17_0_5_node_64 | 0.4 | n |  | TRUE
48 | bus_LV_131-17_0_5_node_67 | 0.4 | n |  | TRUE
49 | bus_LV_131-17_0_5_node_62 | 0.4 | n |  | TRUE
50 | bus_LV_131-17_0_5_node_106 | 0.4 | n |  | TRUE
51 | bus_LV_131-17_0_5_node_105 | 0.4 | n |  | TRUE
52 | bus_LV_131-17_0_5_node_80 | 0.4 | n |  | TRUE
53 | bus_LV_131-17_0_5_node_81 | 0.4 | n |  | TRUE
54 | bus_LV_131-17_0_5_node_78 | 0.4 | n |  | TRUE
55 | bus_LV_131-17_0_5_node_24 | 0.4 | n |  | TRUE
56 | bus_LV_131-17_0_5_node_25 | 0.4 | n |  | TRUE
57 | bus_LV_131-17_0_5_node_26 | 0.4 | n |  | TRUE
58 | bus_LV_131-17_0_5_node_27 | 0.4 | n |  | TRUE
59 | bus_LV_131-17_0_5_node_28 | 0.4 | n |  | TRUE
60 | bus_LV_131-17_0_5_node_32 | 0.4 | n |  | TRUE
61 | bus_LV_131-17_0_5_node_34 | 0.4 | n |  | TRUE
62 | bus_LV_131-17_0_5_node_30 | 0.4 | n |  | TRUE
63 | bus_LV_131-17_0_5_node_71 | 0.4 | n |  | TRUE
64 | bus_LV_131-17_0_5_node_142 | 0.4 | n |  | TRUE
65 | bus_LV_131-17_0_5_node_94 | 0.4 | n |  | TRUE
66 | bus_LV_131-17_0_5_node_93 | 0.4 | n |  | TRUE
67 | bus_LV_131-17_0_5_node_29 | 0.4 | n |  | TRUE
68 | bus_LV_131-17_0_5_node_123 | 0.4 | n |  | TRUE
69 | bus_LV_131-17_0_5_node_37 | 0.4 | n |  | TRUE
70 | bus_LV_131-17_0_5_node_38 | 0.4 | n |  | TRUE
71 | bus_LV_131-17_0_5_node_39 | 0.4 | n |  | TRUE
72 | bus_LV_131-17_0_5_node_40 | 0.4 | n |  | TRUE
73 | bus_LV_131-17_0_5_node_41 | 0.4 | n |  | TRUE
74 | bus_LV_131-17_0_5_node_45 | 0.4 | n |  | TRUE
75 | bus_LV_131-17_0_5_node_68 | 0.4 | n |  | TRUE
76 | bus_LV_131-17_0_5_node_113 | 0.4 | n |  | TRUE
77 | bus_LV_131-17_0_5_node_44 | 0.4 | n |  | TRUE
78 | bus_LV_131-17_0_5_node_61 | 0.4 | n |  | TRUE
79 | bus_LV_131-17_0_5_node_58 | 0.4 | n |  | TRUE
80 | bus_LV_131-17_0_5_node_46 | 0.4 | n |  | TRUE
81 | bus_LV_131-17_0_5_node_47 | 0.4 | n |  | TRUE
82 | bus_LV_131-17_0_5_node_49 | 0.4 | n |  | TRUE
83 | bus_LV_131-17_0_5_node_50 | 0.4 | n |  | TRUE
84 | bus_LV_131-17_0_5_node_48 | 0.4 | n |  | TRUE
85 | bus_LV_131-17_0_5_node_51 | 0.4 | n |  | TRUE
86 | bus_LV_131-17_0_5_node_53 | 0.4 | n |  | TRUE
87 | bus_LV_131-17_0_5_node_118 | 0.4 | n |  | TRUE
88 | bus_LV_131-17_0_5_node_98 | 0.4 | n |  | TRUE
89 | bus_LV_131-17_0_5_node_77 | 0.4 | n |  | TRUE
90 | bus_LV_131-17_0_5_node_88 | 0.4 | n |  | TRUE
91 | bus_LV_131-17_0_5_node_119 | 0.4 | n |  | TRUE
92 | bus_LV_131-17_0_5_node_86 | 0.4 | n |  | TRUE
93 | bus_LV_131-17_0_5_node_109 | 0.4 | n |  | TRUE
94 | bus_LV_131-17_0_5_node_120 | 0.4 | n |  | TRUE
95 | bus_LV_131-17_0_5_node_76 | 0.4 | n |  | TRUE
96 | bus_LV_131-17_0_5_node_99 | 0.4 | n |  | TRUE
97 | bus_LV_131-17_0_5_node_65 | 0.4 | n |  | TRUE
98 | bus_LV_131-17_0_5_node_56 | 0.4 | n |  | TRUE
99 | bus_LV_131-17_0_5_node_57 | 0.4 | n |  | TRUE
100 | bus_LV_131-17_0_5_node_59 | 0.4 | n |  | TRUE
101 | bus_LV_131-17_0_5_node_60 | 0.4 | n |  | TRUE
102 | bus_LV_131-17_0_5_node_97 | 0.4 | n |  | TRUE
103 | bus_LV_131-17_0_5_node_145 | 0.4 | n |  | TRUE
104 | bus_LV_131-17_0_5_node_146 | 0.4 | n |  | TRUE
105 | bus_LV_131-17_0_5_node_96 | 0.4 | n |  | TRUE
106 | bus_LV_131-17_0_5_node_63 | 0.4 | n |  | TRUE
107 | bus_LV_131-17_0_5_node_66 | 0.4 | n |  | TRUE
108 | bus_LV_131-17_0_5_node_95 | 0.4 | n |  | TRUE
109 | bus_LV_131-17_0_5_node_72 | 0.4 | n |  | TRUE
110 | bus_LV_131-17_0_5_node_114 | 0.4 | n |  | TRUE
111 | bus_LV_131-17_0_5_node_74 | 0.4 | n |  | TRUE
112 | bus_LV_131-17_0_5_node_100 | 0.4 | n |  | TRUE
113 | bus_LV_131-17_0_5_node_101 | 0.4 | n |  | TRUE
114 | bus_LV_131-17_0_5_node_122 | 0.4 | n |  | TRUE
115 | bus_LV_131-17_0_5_node_121 | 0.4 | n |  | TRUE
116 | bus_LV_131-17_0_5_node_85 | 0.4 | n |  | TRUE
117 | bus_LV_131-17_0_5_node_87 | 0.4 | n |  | TRUE
118 | bus_LV_131-17_0_5_node_91 | 0.4 | n |  | TRUE
119 | bus_LV_131-17_0_5_node_92 | 0.4 | n |  | TRUE
120 | bus_LV_131-17_0_5_node_107 | 0.4 | n |  | TRUE
121 | bus_LV_131-17_0_5_node_108 | 0.4 | n |  | TRUE
122 | bus_LV_131-17_0_5_node_115 | 0.4 | n |  | TRUE
123 | bus_LV_131-17_0_5_node_102 | 0.4 | n |  | TRUE
124 | bus_LV_131-17_0_5_node_103 | 0.4 | n |  | TRUE
125 | bus_LV_131-17_0_5_node_126 | 0.4 | n |  | TRUE
126 | bus_LV_131-17_0_5_node_125 | 0.4 | n |  | TRUE
127 | bus_LV_131-17_0_5_node_104 | 0.4 | n |  | TRUE
128 | bus_LV_131-17_0_5_node_124 | 0.4 | n |  | TRUE
129 | bus_LV_131-17_0_5_node_131 | 0.4 | n |  | TRUE
130 | bus_LV_131-17_0_5_node_135 | 0.4 | n |  | TRUE
131 | bus_LV_131-17_0_5_node_136 | 0.4 | n |  | TRUE
132 | bus_LV_131-17_0_5_node_139 | 0.4 | n |  | TRUE
133 | bus_LV_131-17_0_5_node_144 | 0.4 | n |  | TRUE
134 | bus_MV_360_0_node_8 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_131-17_0_5_load_0 | 0 | 0.0067055 | 0.0016806 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_131-17_0_5_load_7 | 2 | 0.0059618 | 0.0014942 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_131-17_0_5_load_8 | 3 | 0.010261 | 0.0025717 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_131-17_0_5_load_132 | 4 | 0.0047034 | 0.0011788 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_131-17_0_5_load_143 | 5 | 0.0090411 | 0.0022659 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_131-17_0_5_load_55 | 6 | 0.0017238 | 0.00043201 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_131-17_0_5_load_54 | 7 | 0.0023976 | 0.00060089 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_131-17_0_5_load_112 | 8 | 0.0048499 | 0.0012155 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_131-17_0_5_load_42 | 10 | 0.0037131 | 0.0009306 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_131-17_0_5_load_43 | 11 | 0.0019608 | 0.00049141 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_131-17_0_5_load_133 | 12 | 0.0016353 | 0.00040985 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_131-17_0_5_load_134 | 13 | 0.0021702 | 0.00054391 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_131-17_0_5_load_9 | 14 | 0.031598 | 0.0079193 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_131-17_0_5_load_10 | 15 | 0.024532 | 0.0061483 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_131-17_0_5_load_14 | 18 | 0.0065565 | 0.0016432 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_131-17_0_5_load_75 | 19 | 0.0022355 | 0.00056028 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_131-17_0_5_load_89 | 20 | 0.0022316 | 0.0005593 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_131-17_0_5_load_137 | 21 | 0.0031278 | 0.00078391 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_131-17_0_5_load_129 | 23 | 0.003127 | 0.0007837 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_131-17_0_5_load_127 | 24 | 0.010488 | 0.0026286 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_131-17_0_5_load_83 | 27 | 0.02069 | 0.0051854 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_131-17_0_5_load_117 | 30 | 0.0027682 | 0.00069378 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_131-17_0_5_load_116 | 33 | 0.0024286 | 0.00060867 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_131-17_0_5_load_141 | 35 | 0.0016349 | 0.00040973 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_131-17_0_5_load_147 | 36 | 0.0048649 | 0.0012192 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_131-17_0_5_load_79 | 38 | 0.015072 | 0.0037773 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_131-17_0_5_load_138 | 41 | 0.0031053 | 0.00077825 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_131-17_0_5_load_69 | 43 | 0.0049377 | 0.0012375 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_131-17_0_5_load_140 | 46 | 0.0016245 | 0.00040713 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_131-17_0_5_load_62 | 49 | 0.0047237 | 0.0011839 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_131-17_0_5_load_106 | 50 | 0.002877 | 0.00072105 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_131-17_0_5_load_105 | 51 | 0.0034079 | 0.0008541 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_131-17_0_5_load_81 | 53 | 0.010604 | 0.0026575 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_131-17_0_5_load_78 | 54 | 0.010473 | 0.0026247 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_131-17_0_5_load_24 | 55 | 0.0028539 | 0.00071527 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_131-17_0_5_load_25 | 56 | 0.0019405 | 0.00048633 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_131-17_0_5_load_26 | 57 | 0.0020968 | 0.00052551 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_131-17_0_5_load_30 | 62 | 0.0021089 | 0.00052854 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_131-17_0_5_load_71 | 63 | 0.0053229 | 0.001334 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_131-17_0_5_load_142 | 64 | 0.0086887 | 0.0021776 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_131-17_0_5_load_94 | 65 | 0.0019691 | 0.00049351 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_131-17_0_5_load_93 | 66 | 0.0023031 | 0.00057722 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_131-17_0_5_load_29 | 67 | 0.0035236 | 0.0008831 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_131-17_0_5_load_123 | 68 | 0.0039852 | 0.00099879 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_131-17_0_5_load_37 | 69 | 0.0024643 | 0.00061761 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_131-17_0_5_load_38 | 70 | 0.0017425 | 0.00043671 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_131-17_0_5_load_39 | 71 | 0.0023429 | 0.00058719 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_131-17_0_5_load_40 | 72 | 0.0038218 | 0.00095784 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_131-17_0_5_load_41 | 73 | 0.0015309 | 0.00038367 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_131-17_0_5_load_45 | 74 | 0.0012606 | 0.00031593 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_131-17_0_5_load_68 | 75 | 0.0053289 | 0.0013356 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_131-17_0_5_load_113 | 76 | 0.0022336 | 0.00055978 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_131-17_0_5_load_44 | 77 | 0.0018036 | 0.00045203 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_131-17_0_5_load_61 | 78 | 0.001637 | 0.00041028 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_131-17_0_5_load_46 | 80 | 0.010878 | 0.0027264 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_131-17_0_5_load_50 | 83 | 0.010988 | 0.0027539 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_131-17_0_5_load_51 | 85 | 0.015812 | 0.0039629 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_131-17_0_5_load_118 | 87 | 0.0084777 | 0.0021247 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_131-17_0_5_load_86 | 92 | 0.0078024 | 0.0019555 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_131-17_0_5_load_109 | 93 | 0.0019414 | 0.00048657 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_131-17_0_5_load_120 | 94 | 0.0080509 | 0.0020177 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_131-17_0_5_load_76 | 95 | 0.015598 | 0.0039091 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_131-17_0_5_load_99 | 96 | 0.013421 | 0.0033636 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_131-17_0_5_load_56 | 98 | 0.0023273 | 0.00058327 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_131-17_0_5_load_57 | 99 | 0.0094912 | 0.0023787 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_131-17_0_5_load_59 | 100 | 0.0021313 | 0.00053414 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_131-17_0_5_load_145 | 103 | 0.0024762 | 0.0006206 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_131-17_0_5_load_146 | 104 | 0.0042424 | 0.0010632 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_131-17_0_5_load_66 | 107 | 0.0023752 | 0.00059529 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_131-17_0_5_load_95 | 108 | 0.0023758 | 0.00059544 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_131-17_0_5_load_72 | 109 | 0.01134 | 0.0028421 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_131-17_0_5_load_74 | 111 | 0.0046491 | 0.0011652 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_131-17_0_5_load_100 | 112 | 0.0023752 | 0.00059529 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_131-17_0_5_load_101 | 113 | 0.0022339 | 0.00055986 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_131-17_0_5_load_122 | 114 | 0.0043409 | 0.0010879 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_131-17_0_5_load_121 | 115 | 0.0040937 | 0.001026 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_131-17_0_5_load_85 | 116 | 0.001966 | 0.00049273 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_131-17_0_5_load_87 | 117 | 0.0020069 | 0.00050299 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_131-17_0_5_load_91 | 118 | 0.0034522 | 0.00086519 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_131-17_0_5_load_92 | 119 | 0.0022326 | 0.00055953 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_131-17_0_5_load_107 | 120 | 0.0016775 | 0.00042042 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_131-17_0_5_load_108 | 121 | 0.0016246 | 0.00040717 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_131-17_0_5_load_115 | 122 | 0.0034453 | 0.00086347 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_131-17_0_5_load_102 | 123 | 0.0067947 | 0.0017029 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_131-17_0_5_load_103 | 124 | 0.0022339 | 0.00055986 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_131-17_0_5_load_126 | 125 | 0.0022321 | 0.00055943 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_131-17_0_5_load_125 | 126 | 0.002375 | 0.00059522 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_131-17_0_5_load_104 | 127 | 0.0022321 | 0.00055943 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_131-17_0_5_load_124 | 128 | 0.0023745 | 0.00059511 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_131-17_0_5_load_131 | 129 | 0.001635 | 0.00040977 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_131-17_0_5_load_135 | 130 | 0.0016343 | 0.0004096 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_131-17_0_5_load_136 | 131 | 0.0016251 | 0.00040729 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_131-17_0_5_load_139 | 132 | 0.0016338 | 0.00040946 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_131-17_0_5_load_144 | 133 | 0.0026319 | 0.00065962 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 108 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_131-17_0_5_line_0 |  | 0 | 1 | 0.0050166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_131-17_0_5_line_1 |  | 1 | 2 | 0.025785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_131-17_0_5_line_2 |  | 1 | 3 | 0.047492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_131-17_0_5_line_3 |  | 2 | 4 | 0.033831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_131-17_0_5_line_4 |  | 3 | 5 | 0.011746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_131-17_0_5_line_5 |  | 4 | 12 | 0.024871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_131-17_0_5_line_6 |  | 4 | 13 | 0.01728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_131-17_0_5_line_7 |  | 6 | 7 | 0.0065732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_131-17_0_5_line_8 |  | 7 | 74 | 0.021311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_131-17_0_5_line_9 |  | 8 | 9 | 0.0095477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_131-17_0_5_line_10 |  | 9 | 93 | 0.022606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_131-17_0_5_line_11 |  | 9 | 90 | 0.049598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_131-17_0_5_line_12 |  | 10 | 11 | 0.0041386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_131-17_0_5_line_13 |  | 11 | 77 | 0.029268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_131-17_0_5_line_14 |  | 12 | 46 | 0.0013135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_131-17_0_5_line_15 |  | 13 | 133 | 0.0057832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_131-17_0_5_line_16 |  | 14 | 15 | 0.05215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_131-17_0_5_line_17 |  | 14 | 16 | 0.029327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_131-17_0_5_line_18 |  | 16 | 17 | 0.005746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_131-17_0_5_line_19 |  | 16 | 18 | 0.0088486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_131-17_0_5_line_20 |  | 17 | 19 | 0.022868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_131-17_0_5_line_21 |  | 17 | 20 | 0.020021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_131-17_0_5_line_22 |  | 18 | 21 | 0.022931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_131-17_0_5_line_23 |  | 19 | 39 | 0.01779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_131-17_0_5_line_24 |  | 20 | 40 | 0.011209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_131-17_0_5_line_25 |  | 21 | 41 | 0.0064794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_131-17_0_5_line_26 |  | 22 | 23 | 0.015366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_131-17_0_5_line_27 |  | 22 | 24 | 0.017785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_131-17_0_5_line_28 |  | 23 | 41 | 0.0064483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_131-17_0_5_line_29 |  | 24 | 42 | 0.012605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_131-17_0_5_line_30 |  | 25 | 26 | 0.044092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_131-17_0_5_line_31 |  | 25 | 27 | 0.065845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_131-17_0_5_line_32 |  | 26 | 34 | 0.040099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_131-17_0_5_line_33 |  | 26 | 35 | 0.051138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_131-17_0_5_line_34 |  | 28 | 29 | 0.03666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_131-17_0_5_line_35 |  | 28 | 30 | 0.043165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_131-17_0_5_line_36 |  | 29 | 45 | 0.015141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_131-17_0_5_line_37 |  | 30 | 31 | 0.015206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_131-17_0_5_line_38 |  | 31 | 32 | 0.021267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_131-17_0_5_line_39 |  | 31 | 33 | 0.016812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_131-17_0_5_line_40 |  | 32 | 36 | 0.034704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_131-17_0_5_line_41 |  | 32 | 37 | 0.009326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_131-17_0_5_line_42 |  | 34 | 42 | 0.009233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_131-17_0_5_line_43 |  | 35 | 46 | 0.0013693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_131-17_0_5_line_44 |  | 37 | 38 | 0.033497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_131-17_0_5_line_45 |  | 38 | 48 | 0.025313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_131-17_0_5_line_46 |  | 39 | 111 | 0.0087072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_131-17_0_5_line_47 |  | 39 | 109 | 0.014402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
48 | LV_131-17_0_5_line_48 |  | 40 | 118 | 0.014705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_131-17_0_5_line_49 |  | 40 | 119 | 0.014465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_131-17_0_5_line_50 |  | 42 | 129 | 0.015287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_131-17_0_5_line_51 |  | 43 | 44 | 0.015683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_131-17_0_5_line_52 |  | 44 | 63 | 0.035121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_131-17_0_5_line_53 |  | 45 | 50 | 0.024144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_131-17_0_5_line_54 |  | 45 | 51 | 0.033181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_131-17_0_5_line_55 |  | 47 | 48 | 0.004244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
56 | LV_131-17_0_5_line_56 |  | 47 | 49 | 0.0070814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
57 | LV_131-17_0_5_line_57 |  | 48 | 95 | 0.038214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_131-17_0_5_line_58 |  | 49 | 106 | 0.046402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
59 | LV_131-17_0_5_line_59 |  | 50 | 68 | 0.029198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_131-17_0_5_line_60 |  | 51 | 65 | 0.021414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_131-17_0_5_line_61 |  | 52 | 53 | 0.0062043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_131-17_0_5_line_62 |  | 52 | 54 | 0.023949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_131-17_0_5_line_63 |  | 54 | 89 | 0.041293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_131-17_0_5_line_64 |  | 55 | 56 | 0.022486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_131-17_0_5_line_65 |  | 55 | 57 | 0.024249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_131-17_0_5_line_66 |  | 56 | 58 | 0.023543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_131-17_0_5_line_67 |  | 57 | 59 | 0.03219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_131-17_0_5_line_68 |  | 58 | 60 | 0.014934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_131-17_0_5_line_69 |  | 59 | 61 | 0.020294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_131-17_0_5_line_70 |  | 59 | 62 | 0.015134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_131-17_0_5_line_71 |  | 60 | 65 | 0.015715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_131-17_0_5_line_72 |  | 60 | 66 | 0.0042153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_131-17_0_5_line_73 |  | 61 | 63 | 0.013688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_131-17_0_5_line_74 |  | 61 | 64 | 0.026549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_131-17_0_5_line_75 |  | 62 | 67 | 0.032894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_131-17_0_5_line_76 |  | 68 | 115 | 0.02553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_131-17_0_5_line_77 |  | 69 | 70 | 0.018616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_131-17_0_5_line_78 |  | 69 | 71 | 0.014477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_131-17_0_5_line_79 |  | 70 | 72 | 0.017577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_131-17_0_5_line_80 |  | 71 | 73 | 0.018074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_131-17_0_5_line_81 |  | 72 | 74 | 0.0081143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_131-17_0_5_line_82 |  | 73 | 75 | 0.028942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_131-17_0_5_line_83 |  | 75 | 76 | 0.026186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_131-17_0_5_line_84 |  | 76 | 110 | 0.013002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_131-17_0_5_line_85 |  | 77 | 78 | 0.029896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_131-17_0_5_line_86 |  | 78 | 79 | 0.0058834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_131-17_0_5_line_87 |  | 79 | 101 | 0.024713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_131-17_0_5_line_88 |  | 79 | 98 | 0.026035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_131-17_0_5_line_89 |  | 80 | 81 | 0.026575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_131-17_0_5_line_90 |  | 81 | 82 | 0.012077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_131-17_0_5_line_91 |  | 81 | 83 | 0.027693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_131-17_0_5_line_92 |  | 82 | 87 | 0.024386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_131-17_0_5_line_93 |  | 84 | 85 | 0.025988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_131-17_0_5_line_94 |  | 84 | 86 | 0.044022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_131-17_0_5_line_95 |  | 85 | 88 | 0.01818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_131-17_0_5_line_96 |  | 86 | 89 | 0.042329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_131-17_0_5_line_97 |  | 87 | 91 | 0.019739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_131-17_0_5_line_98 |  | 88 | 94 | 0.019435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_131-17_0_5_line_99 |  | 89 | 95 | 0.0062998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_131-17_0_5_line_100 |  | 90 | 91 | 0.019469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_131-17_0_5_line_101 |  | 90 | 92 | 0.019829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_131-17_0_5_line_102 |  | 91 | 94 | 0.016935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_131-17_0_5_line_103 |  | 92 | 116 | 0.0079888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_131-17_0_5_line_104 |  | 96 | 97 | 0.028219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_131-17_0_5_line_105 |  | 97 | 108 | 0.028993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
106 | LV_131-17_0_5_line_106 |  | 97 | 106 | 0.004046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
107 | LV_131-17_0_5_line_107 |  | 98 | 99 | 0.036582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_131-17_0_5_line_108 |  | 99 | 100 | 0.0079318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_131-17_0_5_line_109 |  | 100 | 102 | 0.016905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_131-17_0_5_line_110 |  | 101 | 103 | 0.040152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_131-17_0_5_line_111 |  | 101 | 104 | 0.020818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_131-17_0_5_line_112 |  | 102 | 105 | 0.015095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_131-17_0_5_line_113 |  | 105 | 108 | 0.0098425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_131-17_0_5_line_114 |  | 106 | 107 | 0.022005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
115 | LV_131-17_0_5_line_115 |  | 107 | 109 | 0.0093197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
116 | LV_131-17_0_5_line_116 |  | 110 | 122 | 0.014282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_131-17_0_5_line_117 |  | 110 | 119 | 0.01336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_131-17_0_5_line_118 |  | 111 | 112 | 0.013479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_131-17_0_5_line_119 |  | 112 | 113 | 0.019412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_131-17_0_5_line_120 |  | 113 | 125 | 0.00010396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_131-17_0_5_line_121 |  | 114 | 115 | 0.036244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_131-17_0_5_line_122 |  | 116 | 117 | 0.023792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_131-17_0_5_line_123 |  | 120 | 121 | 0.0056876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_131-17_0_5_line_124 |  | 121 | 129 | 0.0094689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_131-17_0_5_line_125 |  | 122 | 130 | 0.024228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_131-17_0_5_line_126 |  | 123 | 124 | 0.014924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_131-17_0_5_line_127 |  | 124 | 127 | 0.00010393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_131-17_0_5_line_128 |  | 125 | 126 | 0.013482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_131-17_0_5_line_129 |  | 126 | 128 | 0.00011036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_131-17_0_5_line_130 |  | 127 | 128 | 0.012666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_131-17_0_5_line_131 |  | 130 | 131 | 0.0064023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_131-17_0_5_line_132 |  | 131 | 132 | 0.0063211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_131-17_0_5_trafo_95 | 0.63 MVA 20/0.4 kV | 134 | 108 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2682554.2641 | 1240121.2281 | 2682549.8156 | 1240118.9093
1 | 2682554.2641 | 1240121.2281 | 2682563.0644 | 1240124.6974 | 2682578.7225 | 1240129.3162
2 | 2682554.2641 | 1240121.2281 | 2682559.6386 | 1240108.3826 | 2682574.4425 | 1240078.2558
3 | 2682611.171 | 1240138.8878 | 2682578.7225 | 1240129.3162
4 | 2682574.7371 | 1240066.5139 | 2682574.4425 | 1240078.2558
5 | 2682611.171 | 1240138.8878 | 2682635.0538 | 1240145.8307
6 | 2682611.171 | 1240138.8878 | 2682614.9603 | 1240122.0284
7 | 2682487.9156 | 1240185.7741 | 2682493.9692 | 1240188.3356
8 | 2682513.5952 | 1240196.64 | 2682493.9692 | 1240188.3356
9 | 2682469.7112 | 1240367.1624 | 2682460.4777 | 1240364.7334
10 | 2682469.7112 | 1240367.1624 | 2682471.5467 | 1240389.6943
11 | 2682469.7112 | 1240367.1624 | 2682486.4102 | 1240368.7288 | 2682492.7804 | 1240368.5505 | 2682519.2221 | 1240367.7952
12 | 2682461.818 | 1240238.9127 | 2682465.5029 | 1240240.7966
13 | 2682465.5029 | 1240240.7966 | 2682491.5625 | 1240254.1193
14 | 2682635.0538 | 1240145.8307 | 2682636.315 | 1240146.1973
15 | 2682618.5253 | 1240117.4748 | 2682614.9603 | 1240122.0284
16 | 2682735.1793 | 1240263.427 | 2682776.6927 | 1240294.9914
17 | 2682711.8342 | 1240245.6766 | 2682735.1793 | 1240263.427
18 | 2682709.9284 | 1240251.0984 | 2682711.8342 | 1240245.6766
19 | 2682711.8342 | 1240245.6766 | 2682714.1122 | 1240237.1263
20 | 2682709.9284 | 1240251.0984 | 2682703.6265 | 1240265.899 | 2682699.6782 | 1240271.4128
21 | 2682709.9284 | 1240251.0984 | 2682690.6698 | 1240245.6265
22 | 2682714.1122 | 1240237.1263 | 2682720.0159 | 1240214.9679
23 | 2682688.6764 | 1240285.338 | 2682692.5741 | 1240281.3339 | 2682699.6782 | 1240271.4128
24 | 2682679.8872 | 1240242.5628 | 2682690.6698 | 1240245.6265
25 | 2682720.0159 | 1240214.9679 | 2682721.684 | 1240208.707
26 | 2682727.3001 | 1240187.6283 | 2682723.3441 | 1240202.4761
27 | 2682727.3001 | 1240187.6283 | 2682710.1956 | 1240182.7569
28 | 2682723.3441 | 1240202.4761 | 2682721.684 | 1240208.707
29 | 2682698.0724 | 1240179.3041 | 2682710.1956 | 1240182.7569
30 | 2682714.9621 | 1240133.0507 | 2682720.0695 | 1240138.8371 | 2682716.3141 | 1240137.5172 | 2682710.8358 | 1240137.174 | 2682705.4957 | 1240139.3901 | 2682694.0612 | 1240147.4922 | 2682691.2995 | 1240149.2105 | 2682687.6592 | 1240150.4829
31 | 2682714.9621 | 1240133.0507 | 2682683.7443 | 1240100.3592 | 2682669.4866 | 1240085.432
32 | 2682689.1685 | 1240176.7672 | 2682691.2999 | 1240168.1796 | 2682697.2981 | 1240169.742 | 2682699.7579 | 1240169.6095 | 2682687.6592 | 1240150.4829
33 | 2682687.6592 | 1240150.4829 | 2682680.252 | 1240152.3367 | 2682671.8883 | 1240153.3654 | 2682655.5216 | 1240151.7809 | 2682637.6299 | 1240146.5796
34 | 2682682.5091 | 1240457.0973 | 2682675.2851 | 1240463.2011 | 2682655.4679 | 1240481.9164
35 | 2682682.5091 | 1240457.0973 | 2682718.2904 | 1240432.9533
36 | 2682655.4679 | 1240481.9164 | 2682648.704 | 1240488.1045 | 2682644.0678 | 1240484.3372
37 | 2682730.8953 | 1240424.448 | 2682718.2904 | 1240432.9533
38 | 2682720.7574 | 1240405.76 | 2682722.4484 | 1240409.2305 | 2682726.9819 | 1240417.1104 | 2682730.8953 | 1240424.448
39 | 2682730.8953 | 1240424.448 | 2682746.1434 | 1240417.3666
40 | 2682720.7574 | 1240405.76 | 2682751.8011 | 1240390.0702
41 | 2682717.8396 | 1240412.1684 | 2682722.4484 | 1240409.2305 | 2682720.7574 | 1240405.76
42 | 2682698.0724 | 1240179.3041 | 2682689.1685 | 1240176.7672
43 | 2682637.6299 | 1240146.5796 | 2682636.315 | 1240146.1973
44 | 2682717.8396 | 1240412.1684 | 2682715.9425 | 1240406.1265 | 2682705.6367 | 1240386.4578 | 2682703.2266 | 1240382.1233
45 | 2682690.9256 | 1240360.0006 | 2682703.2266 | 1240382.1233
46 | 2682688.6764 | 1240285.338 | 2682680.2993 | 1240282.9633
47 | 2682688.6764 | 1240285.338 | 2682678.9437 | 1240295.9536
48 | 2682679.8872 | 1240242.5628 | 2682681.1676 | 1240238.0552 | 2682683.6761 | 1240228.3556
49 | 2682679.8872 | 1240242.5628 | 2682665.9736 | 1240238.606
50 | 2682698.0724 | 1240179.3041 | 2682695.781 | 1240187.4336 | 2682694.0169 | 1240194.0428
51 | 2682764.9477 | 1240488.5351 | 2682774.6408 | 1240476.2058
52 | 2682764.9477 | 1240488.5351 | 2682730.1085 | 1240492.9777
53 | 2682644.0678 | 1240484.3372 | 2682639.798 | 1240480.8642 | 2682626.7124 | 1240485.3964 | 2682621.9229 | 1240485.5579
54 | 2682644.0678 | 1240484.3372 | 2682633.8073 | 1240493.4454 | 2682619.4926 | 1240505.8662 | 2682619.0781 | 1240506.1605
55 | 2682694.5045 | 1240357.7043 | 2682690.9256 | 1240360.0006
56 | 2682694.5045 | 1240357.7043 | 2682690.3781 | 1240351.9493
57 | 2682690.9256 | 1240360.0006 | 2682683.7681 | 1240364.582 | 2682674.4711 | 1240370.7347 | 2682658.2246 | 1240379.7238
58 | 2682657.7746 | 1240319.043 | 2682687.1603 | 1240347.4614 | 2682690.3781 | 1240351.9493
59 | 2682593.0948 | 1240489.3871 | 2682608.7356 | 1240486.0023 | 2682621.9229 | 1240485.5579
60 | 2682619.0781 | 1240506.1605 | 2682601.6175 | 1240518.5572
61 | 2682639.9483 | 1240435.3226 | 2682634.436 | 1240438.17
62 | 2682639.9483 | 1240435.3226 | 2682650.366 | 1240429.052 | 2682659.4624 | 1240421.551
63 | 2682652.7123 | 1240382.7737 | 2682662.1783 | 1240404.6545 | 2682662.5604 | 1240413.0547 | 2682659.4624 | 1240421.551
64 | 2682642.8841 | 1240511.0632 | 2682636.8294 | 1240512.6568 | 2682622.2835 | 1240519.8442
65 | 2682642.8841 | 1240511.0632 | 2682661.5052 | 1240506.1623 | 2682666.4579 | 1240505.525
66 | 2682601.177 | 1240530.2733 | 2682622.2835 | 1240519.8442
67 | 2682698.3851 | 1240501.4169 | 2682666.4579 | 1240505.525
68 | 2682588.8036 | 1240527.6548 | 2682591.2797 | 1240531.2252 | 2682593.665 | 1240529.3681 | 2682601.177 | 1240530.2733
69 | 2682698.3851 | 1240501.4169 | 2682711.9025 | 1240499.5483 | 2682716.5301 | 1240494.7093
70 | 2682698.3851 | 1240501.4169 | 2682698.143 | 1240516.5488
71 | 2682588.8036 | 1240527.6548 | 2682601.6175 | 1240518.5572
72 | 2682588.8036 | 1240527.6548 | 2682585.3664 | 1240530.095
73 | 2682716.5301 | 1240494.7093 | 2682730.1085 | 1240492.9777
74 | 2682716.5301 | 1240494.7093 | 2682712.8293 | 1240489.4873 | 2682692.7654 | 1240491.3373
75 | 2682697.6169 | 1240549.4388 | 2682698.143 | 1240516.5488
76 | 2682568.721 | 1240496.9848 | 2682593.0948 | 1240489.3871 | 2682593.0948 | 1240489.3871
77 | 2682537.6959 | 1240205.4426 | 2682555.486 | 1240210.9268
78 | 2682569.3209 | 1240215.1918 | 2682555.486 | 1240210.9268
79 | 2682537.6959 | 1240205.4426 | 2682525.548 | 1240201.6976 | 2682521.068 | 1240199.802
80 | 2682569.3209 | 1240215.1918 | 2682577.4104 | 1240217.6856 | 2682586.8576 | 1240219.4417
81 | 2682513.5952 | 1240196.64 | 2682521.068 | 1240199.802
82 | 2682615.3124 | 1240224.731 | 2682586.8576 | 1240219.4417
83 | 2682640.6159 | 1240231.3989 | 2682620.603 | 1240225.7144 | 2682615.3124 | 1240224.731
84 | 2682653.1228 | 1240234.9514 | 2682640.6159 | 1240231.3989
85 | 2682518.1816 | 1240267.728 | 2682491.5625 | 1240254.1193
86 | 2682523.4201 | 1240270.4061 | 2682518.1816 | 1240267.728
87 | 2682523.4201 | 1240270.4061 | 2682519.8885 | 1240294.8634
88 | 2682523.4201 | 1240270.4061 | 2682548.5713 | 1240277.1312
89 | 2682536.0827 | 1240422.9913 | 2682551.4307 | 1240422.1818 | 2682562.5714 | 1240420.9803
90 | 2682538.3878 | 1240411.137 | 2682536.0827 | 1240422.9913
91 | 2682536.0827 | 1240422.9913 | 2682535.4146 | 1240426.44 | 2682523.0669 | 1240432.8285 | 2682512.7896 | 1240432.819
92 | 2682538.3878 | 1240411.137 | 2682540.3831 | 1240400.8908 | 2682539.7033 | 1240386.9598
93 | 2682579.4119 | 1240403.7133 | 2682583.5955 | 1240378.0642
94 | 2682579.4119 | 1240403.7133 | 2682607.6992 | 1240404.0069 | 2682612.694 | 1240389.088
95 | 2682574.345 | 1240362.4132 | 2682583.5955 | 1240378.0642
96 | 2682612.694 | 1240389.088 | 2682628.221 | 1240392.8178 | 2682652.7123 | 1240382.7737
97 | 2682538.7412 | 1240367.2439 | 2682539.7033 | 1240386.9598
98 | 2682574.345 | 1240362.4132 | 2682572.4348 | 1240363.821 | 2682558.7597 | 1240366.6773 | 2682555.669 | 1240366.7648
99 | 2682652.7123 | 1240382.7737 | 2682658.2246 | 1240379.7238
100 | 2682538.7412 | 1240367.2439 | 2682519.2221 | 1240367.7952
101 | 2682519.2221 | 1240367.7952 | 2682518.9556 | 1240347.9681
102 | 2682538.7412 | 1240367.2439 | 2682555.669 | 1240366.7648
103 | 2682516.7116 | 1240340.477 | 2682518.9173 | 1240345.1192 | 2682518.9556 | 1240347.9681
104 | 2682654.5339 | 1240316.6073 | 2682638.9629 | 1240340.1411
105 | 2682654.5339 | 1240316.6073 | 2682635.8904 | 1240302.6044 | 2682630.9444 | 1240299.8187
106 | 2682657.7746 | 1240319.043 | 2682654.5339 | 1240316.6073
107 | 2682548.5713 | 1240277.1312 | 2682553.4684 | 1240278.4406 | 2682582.1266 | 1240282.0195 | 2682584.6949 | 1240282.5965
108 | 2682592.4338 | 1240284.3352 | 2682584.6949 | 1240282.5965
109 | 2682608.9281 | 1240288.041 | 2682592.4338 | 1240284.3352
110 | 2682545.1989 | 1240302.6096 | 2682545.0581 | 1240305.1206 | 2682518.3158 | 1240305.716 | 2682519.8885 | 1240294.8634
111 | 2682502.4746 | 1240289.7622 | 2682502.0269 | 1240292.5913 | 2682519.8885 | 1240294.8634
112 | 2682622.3685 | 1240294.9886 | 2682608.9281 | 1240288.041
113 | 2682622.3685 | 1240294.9886 | 2682630.9444 | 1240299.8187
114 | 2682657.7746 | 1240319.043 | 2682672.6455 | 1240302.8231
115 | 2682678.9437 | 1240295.9536 | 2682672.6455 | 1240302.8231
116 | 2682653.1228 | 1240234.9514 | 2682655.3326 | 1240227.2433 | 2682657.0238 | 1240221.2126
117 | 2682653.1228 | 1240234.9514 | 2682665.9736 | 1240238.606
118 | 2682680.2993 | 1240282.9633 | 2682667.3311 | 1240279.2872
119 | 2682667.3311 | 1240279.2872 | 2682664.4204 | 1240278.462 | 2682666.2045 | 1240271.4485 | 2682657.386 | 1240269.0109
120 | 2682657.386 | 1240269.0109 | 2682657.2858 | 1240268.9832
121 | 2682568.721 | 1240496.9848 | 2682541.4312 | 1240505.4913 | 2682533.8413 | 1240504.4613
122 | 2682507.3519 | 1240318.6284 | 2682510.9452 | 1240328.3408 | 2682516.7116 | 1240340.477
123 | 2682688.4608 | 1240205.9959 | 2682688.8092 | 1240204.7155 | 2682689.3236 | 1240203.0771 | 2682690.0699 | 1240200.5412
124 | 2682694.0169 | 1240194.0428 | 2682692.1264 | 1240201.1258 | 2682690.0699 | 1240200.5412 | 2682690.0699 | 1240200.5412
125 | 2682657.0238 | 1240221.2126 | 2682660.8396 | 1240207.6059 | 2682659.049 | 1240206.3912 | 2682659.6338 | 1240204.0422 | 2682661.2583 | 1240198.7747
126 | 2682617.4916 | 1240257.9831 | 2682617.4916 | 1240257.9831 | 2682631.8765 | 1240261.9594
127 | 2682631.9766 | 1240261.9871 | 2682631.8765 | 1240261.9594
128 | 2682657.2858 | 1240268.9832 | 2682644.2913 | 1240265.3912
129 | 2682644.2913 | 1240265.3912 | 2682644.1849 | 1240265.3618
130 | 2682644.1849 | 1240265.3618 | 2682631.9766 | 1240261.9871
131 | 2682661.2583 | 1240198.7747 | 2682661.7644 | 1240197.1335 | 2682662.2319 | 1240195.6056 | 2682663.1842 | 1240192.6691
132 | 2682665.3172 | 1240187.4872 | 2682664.6844 | 1240190.0247 | 2682664.2152 | 1240191.6749 | 2682663.9808 | 1240192.7613 | 2682663.2118 | 1240192.5838 | 2682663.1842 | 1240192.6691

## bus_geodata
| x | y | coords
0 | 2682549.8156 | 1240118.9093
1 | 2682554.2641 | 1240121.2281
2 | 2682578.7225 | 1240129.3162
3 | 2682574.4425 | 1240078.2558
4 | 2682611.171 | 1240138.8878
5 | 2682574.7371 | 1240066.5139
6 | 2682487.9156 | 1240185.7741
7 | 2682493.9692 | 1240188.3356
8 | 2682460.4777 | 1240364.7334
9 | 2682469.7112 | 1240367.1624
10 | 2682461.818 | 1240238.9127
11 | 2682465.5029 | 1240240.7966
12 | 2682635.0538 | 1240145.8307
13 | 2682614.9603 | 1240122.0284
14 | 2682735.1793 | 1240263.427
15 | 2682776.6927 | 1240294.9914
16 | 2682711.8341 | 1240245.6766
17 | 2682709.9284 | 1240251.0984
18 | 2682714.1122 | 1240237.1263
19 | 2682699.6782 | 1240271.4128
20 | 2682690.6698 | 1240245.6265
21 | 2682720.0159 | 1240214.9679
22 | 2682727.3001 | 1240187.6283
23 | 2682723.3441 | 1240202.4761
24 | 2682710.1956 | 1240182.7569
25 | 2682714.9621 | 1240133.0507
26 | 2682687.6592 | 1240150.4829
27 | 2682669.4866 | 1240085.432
28 | 2682682.5091 | 1240457.0973
29 | 2682655.4679 | 1240481.9164
30 | 2682718.2904 | 1240432.9533
31 | 2682730.8953 | 1240424.448
32 | 2682720.7574 | 1240405.76
33 | 2682746.1434 | 1240417.3666
34 | 2682689.1685 | 1240176.7672
35 | 2682637.6299 | 1240146.5796
36 | 2682751.8011 | 1240390.0702
37 | 2682717.8396 | 1240412.1684
38 | 2682703.2266 | 1240382.1233
39 | 2682688.6764 | 1240285.338
40 | 2682679.8872 | 1240242.5628
41 | 2682721.684 | 1240208.707
42 | 2682698.0724 | 1240179.3041
43 | 2682774.6408 | 1240476.2058
44 | 2682764.9477 | 1240488.5351
45 | 2682644.0678 | 1240484.3372
46 | 2682636.315 | 1240146.1973
47 | 2682694.5045 | 1240357.7043
48 | 2682690.9256 | 1240360.0006
49 | 2682690.3781 | 1240351.9493
50 | 2682621.9229 | 1240485.5579
51 | 2682619.0781 | 1240506.1605
52 | 2682639.9483 | 1240435.3226
53 | 2682634.436 | 1240438.17
54 | 2682659.4624 | 1240421.551
55 | 2682642.8841 | 1240511.0632
56 | 2682622.2835 | 1240519.8442
57 | 2682666.4579 | 1240505.525
58 | 2682601.177 | 1240530.2733
59 | 2682698.3851 | 1240501.4169
60 | 2682588.8036 | 1240527.6548
61 | 2682716.5301 | 1240494.7093
62 | 2682698.143 | 1240516.5488
63 | 2682730.1085 | 1240492.9777
64 | 2682692.7654 | 1240491.3373
65 | 2682601.6175 | 1240518.5572
66 | 2682585.3664 | 1240530.095
67 | 2682697.6169 | 1240549.4388
68 | 2682593.0948 | 1240489.3871
69 | 2682555.486 | 1240210.9268
70 | 2682537.6959 | 1240205.4425
71 | 2682569.3209 | 1240215.1918
72 | 2682521.068 | 1240199.802
73 | 2682586.8576 | 1240219.4417
74 | 2682513.5952 | 1240196.64
75 | 2682615.3124 | 1240224.731
76 | 2682640.6159 | 1240231.3989
77 | 2682491.5625 | 1240254.1193
78 | 2682518.1816 | 1240267.728
79 | 2682523.4201 | 1240270.4061
80 | 2682562.5714 | 1240420.9803
81 | 2682536.0827 | 1240422.9913
82 | 2682538.3878 | 1240411.137
83 | 2682512.7896 | 1240432.819
84 | 2682579.4119 | 1240403.7133
85 | 2682583.5955 | 1240378.0642
86 | 2682612.694 | 1240389.088
87 | 2682539.7033 | 1240386.9598
88 | 2682574.345 | 1240362.4132
89 | 2682652.7123 | 1240382.7737
90 | 2682519.2221 | 1240367.7952
91 | 2682538.7412 | 1240367.2439
92 | 2682518.9556 | 1240347.9681
93 | 2682471.5467 | 1240389.6943
94 | 2682555.669 | 1240366.7648
95 | 2682658.2246 | 1240379.7238
96 | 2682638.9629 | 1240340.1411
97 | 2682654.5339 | 1240316.6073
98 | 2682548.5713 | 1240277.1312
99 | 2682584.6949 | 1240282.5965
100 | 2682592.4338 | 1240284.3352
101 | 2682519.8885 | 1240294.8634
102 | 2682608.9281 | 1240288.041
103 | 2682545.1989 | 1240302.6096
104 | 2682502.4746 | 1240289.7622
105 | 2682622.3685 | 1240294.9886
106 | 2682657.7746 | 1240319.043
107 | 2682672.6455 | 1240302.8231
108 | 2682630.9444 | 1240299.8187
109 | 2682678.9437 | 1240295.9536
110 | 2682653.1228 | 1240234.9514
111 | 2682680.2993 | 1240282.9633
112 | 2682667.3311 | 1240279.2872
113 | 2682657.386 | 1240269.0109
114 | 2682533.8413 | 1240504.4613
115 | 2682568.721 | 1240496.9848
116 | 2682516.7116 | 1240340.477
117 | 2682507.3519 | 1240318.6284
118 | 2682683.6761 | 1240228.3556
119 | 2682665.9736 | 1240238.606
120 | 2682688.4608 | 1240205.9959
121 | 2682690.0699 | 1240200.5412
122 | 2682657.0238 | 1240221.2126
123 | 2682617.4916 | 1240257.9831
124 | 2682631.8765 | 1240261.9594
125 | 2682657.2858 | 1240268.9832
126 | 2682644.2913 | 1240265.3912
127 | 2682631.9766 | 1240261.9871
128 | 2682644.1849 | 1240265.3618
129 | 2682694.0169 | 1240194.0428
130 | 2682661.2583 | 1240198.7747
131 | 2682663.1841 | 1240192.6691
132 | 2682665.3172 | 1240187.4872
133 | 2682618.5253 | 1240117.4748
134 | 2682622.3685 | 1240294.9886

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97673 | -0.44891 | 0.0067055 | 0.0016806
1 | 0.97676 | -0.44829 | 0 | 0
2 | 0.97739 | -0.43605 | 0.0059618 | 0.0014942
3 | 0.97591 | -0.46506 | 0.010261 | 0.0025717
4 | 0.97839 | -0.41633 | 0.0047034 | 0.0011788
5 | 0.97581 | -0.467 | 0.0090411 | 0.0022659
6 | 0.98808 | -0.22877 | 0.0017238 | 0.00043201
7 | 0.98809 | -0.22856 | 0.0023976 | 0.00060089
8 | 0.97843 | -0.41549 | 0.0048499 | 0.0012155
9 | 0.97847 | -0.41465 | 0 | 0
10 | 0.99727 | -0.052459 | 0.0037131 | 0.0009306
11 | 0.99729 | -0.052189 | 0.0019608 | 0.00049141
12 | 0.97935 | -0.39757 | 0.0016353 | 0.00040985
13 | 0.97831 | -0.41785 | 0.0021702 | 0.00054391
14 | 0.9904 | -0.18375 | 0.031598 | 0.0079193
15 | 0.98922 | -0.20651 | 0.024532 | 0.0061483
16 | 0.9919 | -0.15454 | 0 | 0
17 | 0.99231 | -0.14668 | 0 | 0
18 | 0.9911 | -0.16998 | 0.0065565 | 0.0016432
19 | 0.99334 | -0.1269 | 0.0022355 | 0.00056028
20 | 0.99156 | -0.16126 | 0.0022316 | 0.0005593
21 | 0.98915 | -0.20743 | 0.0031278 | 0.00078391
22 | 0.98693 | -0.25018 | 0 | 0
23 | 0.9881 | -0.22753 | 0.003127 | 0.0007837
24 | 0.98557 | -0.27648 | 0.010488 | 0.0026286
25 | 0.98082 | -0.36895 | 0 | 0
26 | 0.98166 | -0.35244 | 0 | 0
27 | 0.97955 | -0.39367 | 0.02069 | 0.0051854
28 | 0.98528 | -0.28173 | 0 | 0
29 | 0.98343 | -0.31764 | 0 | 0
30 | 0.98746 | -0.23961 | 0.0027682 | 0.00069378
31 | 0.98827 | -0.22406 | 0 | 0
32 | 0.98944 | -0.20145 | 0 | 0
33 | 0.98823 | -0.22479 | 0.0024286 | 0.00060867
34 | 0.98415 | -0.30391 | 0 | 0
35 | 0.97946 | -0.39543 | 0.0016349 | 0.00040973
36 | 0.98929 | -0.20445 | 0.0048649 | 0.0012192
37 | 0.99 | -0.19074 | 0 | 0
38 | 0.992 | -0.15237 | 0.015072 | 0.0037773
39 | 0.99415 | -0.11136 | 0 | 0
40 | 0.99116 | -0.16898 | 0 | 0
41 | 0.98862 | -0.21768 | 0.0031053 | 0.00077825
42 | 0.98473 | -0.29278 | 0 | 0
43 | 0.97647 | -0.45397 | 0.0049377 | 0.0012375
44 | 0.97654 | -0.45255 | 0 | 0
45 | 0.98267 | -0.33252 | 0 | 0
46 | 0.9794 | -0.39654 | 0.0016245 | 0.00040713
47 | 0.99423 | -0.10967 | 0 | 0
48 | 0.99386 | -0.11675 | 0 | 0
49 | 0.99454 | -0.10377 | 0.0047237 | 0.0011839
50 | 0.98233 | -0.33919 | 0.002877 | 0.00072105
51 | 0.98147 | -0.356 | 0.0034079 | 0.0008541
52 | 0.98842 | -0.22141 | 0 | 0
53 | 0.98836 | -0.22258 | 0.010604 | 0.0026575
54 | 0.98865 | -0.21688 | 0.010473 | 0.0026247
55 | 0.97852 | -0.41357 | 0.0028539 | 0.00071527
56 | 0.97914 | -0.40149 | 0.0019405 | 0.00048633
57 | 0.97792 | -0.42536 | 0.0020968 | 0.00052551
58 | 0.97983 | -0.38802 | 0 | 0
59 | 0.97719 | -0.43979 | 0 | 0
60 | 0.98026 | -0.37949 | 0 | 0
61 | 0.97683 | -0.44681 | 0 | 0
62 | 0.97711 | -0.44135 | 0.0021089 | 0.00052854
63 | 0.9767 | -0.44938 | 0.0053229 | 0.001334
64 | 0.97662 | -0.45103 | 0.0086887 | 0.0021776
65 | 0.98076 | -0.36986 | 0.0019691 | 0.00049351
66 | 0.98025 | -0.37967 | 0.0023031 | 0.00057722
67 | 0.977 | -0.44346 | 0.0035236 | 0.0008831
68 | 0.98199 | -0.34574 | 0.0039852 | 0.00099879
69 | 0.98855 | -0.21969 | 0.0024643 | 0.00061761
70 | 0.98836 | -0.22333 | 0.0017425 | 0.00043671
71 | 0.98872 | -0.21623 | 0.0023429 | 0.00058719
72 | 0.98821 | -0.22622 | 0.0038218 | 0.00095784
73 | 0.98899 | -0.21115 | 0.0015309 | 0.00038367
74 | 0.98817 | -0.227 | 0.0012606 | 0.00031593
75 | 0.98944 | -0.20224 | 0.0053289 | 0.0013356
76 | 0.98999 | -0.1917 | 0.0022336 | 0.00055978
77 | 0.99744 | -0.049279 | 0.0018036 | 0.00045203
78 | 0.99764 | -0.045363 | 0.001637 | 0.00041028
79 | 0.99769 | -0.044424 | 0 | 0
80 | 0.97756 | -0.43263 | 0.010878 | 0.0027264
81 | 0.97783 | -0.42736 | 0 | 0
82 | 0.97807 | -0.42255 | 0 | 0
83 | 0.97754 | -0.43291 | 0.010988 | 0.0027539
84 | 0.98363 | -0.31393 | 0 | 0
85 | 0.98188 | -0.34807 | 0.015812 | 0.0039629
86 | 0.9866 | -0.25638 | 0 | 0
87 | 0.97857 | -0.41283 | 0.0084777 | 0.0021247
88 | 0.98092 | -0.36681 | 0 | 0
89 | 0.98945 | -0.20137 | 0 | 0
90 | 0.97879 | -0.40851 | 0 | 0
91 | 0.97912 | -0.40194 | 0 | 0
92 | 0.97857 | -0.41276 | 0.0078024 | 0.0019555
93 | 0.97843 | -0.41544 | 0.0019414 | 0.00048657
94 | 0.97989 | -0.38689 | 0.0080509 | 0.0020177
95 | 0.99 | -0.19085 | 0.015598 | 0.0039091
96 | 0.99668 | -0.063201 | 0.013421 | 0.0033636
97 | 0.99702 | -0.056558 | 0 | 0
98 | 0.99806 | -0.037206 | 0.0023273 | 0.00058327
99 | 0.99867 | -0.025585 | 0.0094912 | 0.0023787
100 | 0.99887 | -0.021751 | 0.0021313 | 0.00053414
101 | 0.99754 | -0.047333 | 0 | 0
102 | 0.99933 | -0.012958 | 0 | 0
103 | 0.99745 | -0.049075 | 0.0024762 | 0.0006206
104 | 0.99746 | -0.04888 | 0.0042424 | 0.0010632
105 | 0.99973 | -0.0051121 | 0 | 0
106 | 0.99662 | -0.064239 | 0 | 0
107 | 0.99541 | -0.087352 | 0.0023752 | 0.00059529
108 | 1 | 0 | -0.48382 | -0.12319
109 | 0.9949 | -0.09706 | 0.01134 | 0.0028421
110 | 0.99028 | -0.18596 | 0 | 0
111 | 0.99393 | -0.11559 | 0.0046491 | 0.0011652
112 | 0.99365 | -0.12102 | 0.0023752 | 0.00059529
113 | 0.99329 | -0.12804 | 0.0022339 | 0.00055986
114 | 0.98165 | -0.35248 | 0.0043409 | 0.0010879
115 | 0.9818 | -0.34963 | 0.0040937 | 0.001026
116 | 0.97854 | -0.41334 | 0.001966 | 0.00049273
117 | 0.9785 | -0.41421 | 0.0020069 | 0.00050299
118 | 0.99111 | -0.16989 | 0.0034522 | 0.00086519
119 | 0.99069 | -0.17808 | 0.0022326 | 0.00055953
120 | 0.98462 | -0.29487 | 0.0016775 | 0.00042042
121 | 0.98463 | -0.2947 | 0.0016246 | 0.00040717
122 | 0.99017 | -0.18808 | 0.0034453 | 0.00086347
123 | 0.99287 | -0.13625 | 0.0067947 | 0.0017029
124 | 0.99296 | -0.13445 | 0.0022339 | 0.00055986
125 | 0.99329 | -0.12808 | 0.0022321 | 0.00055943
126 | 0.99309 | -0.13189 | 0.002375 | 0.00059522
127 | 0.99296 | -0.13444 | 0.0022321 | 0.00055943
128 | 0.99309 | -0.13192 | 0.0023745 | 0.00059511
129 | 0.98466 | -0.29413 | 0.001635 | 0.00040977
130 | 0.99007 | -0.19018 | 0.0016343 | 0.0004096
131 | 0.99005 | -0.19056 | 0.0016251 | 0.00040729
132 | 0.99004 | -0.19074 | 0.0016338 | 0.00040946
133 | 0.9783 | -0.41812 | 0.0026319 | 0.00065962
134 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0067055 | -0.0016806 | 0.0067057 | 0.0016806 | 1.9632e-07 | 6.2856e-08 | 0.010216 | 0.010216 | 0.010216 | 0.97673 | -0.44891 | 0.97676 | -0.44829 | 2.8065
1 | -0.026024 | -0.0065279 | 0.026039 | 0.0065373 | 1.5199e-05 | 9.4046e-06 | 0.039648 | 0.039647 | 0.039648 | 0.97676 | -0.44829 | 0.97739 | -0.43605 | 10.8922
2 | 0.019318 | 0.0048472 | -0.019303 | -0.004838 | 1.5427e-05 | 9.2797e-06 | 0.029432 | 0.029432 | 0.029432 | 0.97676 | -0.44829 | 0.97591 | -0.46506 | 8.0858
3 | -0.032001 | -0.0080314 | 0.032031 | 0.0080503 | 3.0118e-05 | 1.8851e-05 | 0.048724 | 0.048724 | 0.048724 | 0.97739 | -0.43605 | 0.97839 | -0.41633 | 13.3857
4 | 0.009042 | 0.0022663 | -0.0090411 | -0.0022659 | 8.372e-07 | 3.8906e-07 | 0.013787 | 0.013787 | 0.013787 | 0.97591 | -0.46506 | 0.97581 | -0.467 | 3.7876
5 | -0.041537 | -0.010433 | 0.041574 | 0.010456 | 3.7231e-05 | 2.3515e-05 | 0.063181 | 0.063181 | 0.063181 | 0.97839 | -0.41633 | 0.97935 | -0.39757 | 17.3574
6 | 0.0048025 | 0.0012035 | -0.0048022 | -0.0012035 | 3.457e-07 | 4.2583e-09 | 0.007304 | 0.0073041 | 0.0073041 | 0.97839 | -0.41633 | 0.97831 | -0.41785 | 2.0066
7 | -0.0017238 | -0.00043201 | 0.0017238 | 0.00043194 | 1.6611e-08 | -7.3562e-08 | 0.0025959 | 0.0025959 | 0.0025959 | 0.98808 | -0.22877 | 0.98809 | -0.22856 | 0.71316
8 | -0.0041214 | -0.0010328 | 0.0041217 | 0.0010328 | 3.0784e-07 | -7.5967e-08 | 0.0062065 | 0.0062064 | 0.0062065 | 0.98809 | -0.22856 | 0.98817 | -0.227 | 1.7051
9 | -0.0048499 | -0.0012155 | 0.0048501 | 0.0012155 | 1.9478e-07 | 4.7392e-09 | 0.0073758 | 0.0073757 | 0.0073758 | 0.97843 | -0.41549 | 0.97847 | -0.41465 | 2.0263
10 | 0.0019415 | 0.00048634 | -0.0019414 | -0.00048657 | 7.3901e-08 | -2.3664e-07 | 0.0029525 | 0.0029526 | 0.0029526 | 0.97847 | -0.41465 | 0.97843 | -0.41544 | 0.81115
11 | -0.0067916 | -0.0017018 | 0.0067936 | 0.0017025 | 1.984e-06 | 6.4656e-07 | 0.010328 | 0.010328 | 0.010328 | 0.97847 | -0.41465 | 0.97879 | -0.40851 | 2.8374
12 | -0.0037131 | -0.0009306 | 0.0037132 | 0.00093058 | 4.7638e-08 | -2.3512e-08 | 0.0055403 | 0.0055403 | 0.0055403 | 0.99727 | -0.052459 | 0.99729 | -0.052189 | 1.5221
13 | -0.0056739 | -0.001422 | 0.0056747 | 0.0014221 | 7.866e-07 | 1.2148e-07 | 0.0084659 | 0.0084657 | 0.0084659 | 0.99729 | -0.052189 | 0.99744 | -0.049279 | 2.3258
14 | -0.04321 | -0.010866 | 0.043212 | 0.010867 | 2.1239e-06 | 1.3428e-06 | 0.065666 | 0.065666 | 0.065666 | 0.97935 | -0.39757 | 0.9794 | -0.39654 | 18.04
15 | 0.002632 | 0.00065957 | -0.0026319 | -0.00065962 | 3.4755e-08 | -5.0372e-08 | 0.0040032 | 0.0040032 | 0.0040032 | 0.97831 | -0.41785 | 0.9783 | -0.41812 | 1.0998
16 | 0.024559 | 0.0061646 | -0.024532 | -0.0061483 | 2.663e-05 | 1.6373e-05 | 0.036901 | 0.036902 | 0.036902 | 0.9904 | -0.18375 | 0.98922 | -0.20651 | 10.1378
17 | -0.056157 | -0.014084 | 0.056235 | 0.014134 | 7.8295e-05 | 4.9731e-05 | 0.084376 | 0.084376 | 0.084376 | 0.9904 | -0.18375 | 0.9919 | -0.15454 | 23.1802
18 | -0.15565 | -0.039436 | 0.15571 | 0.039474 | 5.8816e-05 | 3.7494e-05 | 0.23365 | 0.23365 | 0.23365 | 0.9919 | -0.15454 | 0.99231 | -0.14668 | 32.0946
19 | 0.099413 | 0.025303 | -0.099339 | -0.025255 | 7.3938e-05 | 4.7206e-05 | 0.14927 | 0.14927 | 0.14927 | 0.9919 | -0.15454 | 0.9911 | -0.16998 | 41.0092
20 | -0.19692 | -0.04984 | 0.1971 | 0.049959 | 0.00018715 | 0.00011859 | 0.29546 | 0.29546 | 0.29546 | 0.99231 | -0.14668 | 0.99334 | -0.1269 | 20.2924
21 | 0.041209 | 0.010366 | -0.041181 | -0.010348 | 2.8682e-05 | 1.8098e-05 | 0.061809 | 0.061809 | 0.061809 | 0.99231 | -0.14668 | 0.99156 | -0.16126 | 16.9805
22 | 0.092782 | 0.023612 | -0.092615 | -0.023506 | 0.00016718 | 0.0001067 | 0.13943 | 0.13943 | 0.13943 | 0.9911 | -0.16998 | 0.98915 | -0.20743 | 38.3049
23 | -0.19934 | -0.050519 | 0.19949 | 0.050613 | 0.00014891 | 9.4382e-05 | 0.29881 | 0.29881 | 0.29881 | 0.99334 | -0.1269 | 0.99415 | -0.11136 | 20.5224
24 | 0.038949 | 0.0097888 | -0.038935 | -0.0097797 | 1.4366e-05 | 9.0497e-06 | 0.05846 | 0.05846 | 0.05846 | 0.99156 | -0.16126 | 0.99116 | -0.16898 | 16.0604
25 | 0.089487 | 0.022722 | -0.089443 | -0.022693 | 4.4102e-05 | 2.8142e-05 | 0.13472 | 0.13472 | 0.13472 | 0.98915 | -0.20743 | 0.98862 | -0.21768 | 37.0123
26 | -0.08308 | -0.021048 | 0.08317 | 0.021105 | 9.0526e-05 | 5.774e-05 | 0.12534 | 0.12534 | 0.12534 | 0.98693 | -0.25018 | 0.9881 | -0.22753 | 34.4346
27 | 0.08308 | 0.021048 | -0.082975 | -0.020981 | 0.00010478 | 6.6831e-05 | 0.12534 | 0.12534 | 0.12534 | 0.98693 | -0.25018 | 0.98557 | -0.27648 | 34.4346
28 | -0.086297 | -0.021889 | 0.086338 | 0.021915 | 4.0898e-05 | 2.6092e-05 | 0.13005 | 0.13005 | 0.13005 | 0.9881 | -0.22753 | 0.98862 | -0.21768 | 35.7282
29 | 0.072487 | 0.018352 | -0.07243 | -0.018316 | 5.6685e-05 | 3.6118e-05 | 0.10951 | 0.10951 | 0.10951 | 0.98557 | -0.27648 | 0.98473 | -0.29278 | 30.0843
30 | -0.020714 | -0.0052001 | 0.020731 | 0.00521 | 1.6333e-05 | 9.8959e-06 | 0.031429 | 0.031429 | 0.031429 | 0.98082 | -0.36895 | 0.98166 | -0.35244 | 8.6344
31 | 0.020714 | 0.0052001 | -0.02069 | -0.0051854 | 2.4391e-05 | 1.478e-05 | 0.031429 | 0.031429 | 0.031429 | 0.98082 | -0.36895 | 0.97955 | -0.39367 | 8.6344
32 | -0.0673 | -0.016956 | 0.067456 | 0.017056 | 0.00015659 | 9.9708e-05 | 0.10205 | 0.10205 | 0.10205 | 0.98166 | -0.35244 | 0.98415 | -0.30391 | 28.0346
33 | 0.046569 | 0.011746 | -0.046474 | -0.011686 | 9.5631e-05 | 6.0559e-05 | 0.070617 | 0.070617 | 0.070617 | 0.98166 | -0.35244 | 0.97946 | -0.39543 | 19.4004
34 | 0.054771 | 0.013845 | -0.054677 | -0.013785 | 9.4159e-05 | 5.9796e-05 | 0.08276 | 0.08276 | 0.08276 | 0.98528 | -0.28173 | 0.98343 | -0.31764 | 22.7362
35 | -0.054771 | -0.013845 | 0.054882 | 0.013916 | 0.00011087 | 7.0404e-05 | 0.08276 | 0.082759 | 0.08276 | 0.98528 | -0.28173 | 0.98746 | -0.23961 | 22.7361
36 | 0.054677 | 0.013785 | -0.054638 | -0.013761 | 3.8889e-05 | 2.4697e-05 | 0.08276 | 0.08276 | 0.08276 | 0.98343 | -0.31764 | 0.98267 | -0.33252 | 22.7362
37 | -0.05765 | -0.014609 | 0.057693 | 0.014637 | 4.3092e-05 | 2.7384e-05 | 0.086931 | 0.086931 | 0.086931 | 0.98746 | -0.23961 | 0.98827 | -0.22406 | 23.8821
38 | -0.060122 | -0.015245 | 0.060187 | 0.015287 | 6.5446e-05 | 4.1613e-05 | 0.090588 | 0.090587 | 0.090588 | 0.98827 | -0.22406 | 0.98944 | -0.20145 | 24.8867
39 | 0.0024287 | 0.00060851 | -0.0024286 | -0.00060867 | 8.4308e-08 | -1.6145e-07 | 0.0036568 | 0.0036569 | 0.0036569 | 0.98827 | -0.22406 | 0.98823 | -0.22479 | 1.0046
40 | 0.0048656 | 0.0012192 | -0.0048649 | -0.0012192 | 6.9681e-07 | 2.9569e-10 | 0.0073172 | 0.0073174 | 0.0073174 | 0.98944 | -0.20145 | 0.98929 | -0.20445 | 2.0103
41 | -0.065053 | -0.016506 | 0.065086 | 0.016528 | 3.3522e-05 | 2.1334e-05 | 0.097905 | 0.097905 | 0.097905 | 0.98944 | -0.20145 | 0.99 | -0.19074 | 26.8969
42 | -0.067456 | -0.017056 | 0.067492 | 0.017079 | 3.6055e-05 | 2.2958e-05 | 0.10205 | 0.10205 | 0.10205 | 0.98415 | -0.30391 | 0.98473 | -0.29278 | 28.0346
43 | 0.044839 | 0.011276 | -0.044836 | -0.011274 | 2.3837e-06 | 1.5083e-06 | 0.068134 | 0.068134 | 0.068134 | 0.97946 | -0.39543 | 0.9794 | -0.39654 | 18.7181
44 | -0.065086 | -0.016528 | 0.065207 | 0.016604 | 0.00012041 | 7.6628e-05 | 0.097905 | 0.097904 | 0.097905 | 0.99 | -0.19074 | 0.992 | -0.15237 | 26.8969
45 | -0.080278 | -0.020381 | 0.080416 | 0.020469 | 0.00013786 | 8.7901e-05 | 0.12051 | 0.12051 | 0.12051 | 0.992 | -0.15237 | 0.99386 | -0.11675 | 33.1077
46 | 0.027524 | 0.0069061 | -0.027518 | -0.0069026 | 5.5423e-06 | 3.4342e-06 | 0.0412 | 0.0412 | 0.0412 | 0.99415 | -0.11136 | 0.99393 | -0.11559 | 11.3186
47 | -0.22701 | -0.057519 | 0.22717 | 0.057618 | 0.00015609 | 9.9147e-05 | 0.34001 | 0.34 | 0.34001 | 0.99415 | -0.11136 | 0.9949 | -0.09706 | 23.352
48 | 0.0034523 | 0.0008651 | -0.0034522 | -0.00086519 | 1.4813e-07 | -9.471e-08 | 0.0051829 | 0.0051829 | 0.0051829 | 0.99116 | -0.16898 | 0.99111 | -0.16989 | 1.4239
49 | 0.035482 | 0.0089146 | -0.035467 | -0.008905 | 1.5397e-05 | 9.6678e-06 | 0.053277 | 0.053277 | 0.053277 | 0.99116 | -0.16898 | 0.99069 | -0.17808 | 14.6366
50 | 0.0049375 | 0.0012372 | -0.0049372 | -0.0012372 | 3.1912e-07 | 9.7737e-09 | 0.007461 | 0.0074611 | 0.0074611 | 0.98473 | -0.29278 | 0.98466 | -0.29413 | 2.0497
51 | -0.0049377 | -0.0012375 | 0.004938 | 0.0012375 | 3.3297e-07 | 1.6904e-08 | 0.0075244 | 0.0075243 | 0.0075244 | 0.97647 | -0.45397 | 0.97654 | -0.45255 | 2.0671
52 | -0.004938 | -0.0012375 | 0.0049387 | 0.0012376 | 7.4564e-07 | 3.7736e-08 | 0.0075243 | 0.0075242 | 0.0075243 | 0.97654 | -0.45255 | 0.9767 | -0.44938 | 2.0671
53 | 0.015308 | 0.0038393 | -0.015303 | -0.0038365 | 4.8653e-06 | 2.808e-06 | 0.023181 | 0.023181 | 0.023181 | 0.98267 | -0.33252 | 0.98233 | -0.33919 | 6.3684
54 | 0.03933 | 0.0099215 | -0.039286 | -0.0098937 | 4.4167e-05 | 2.7847e-05 | 0.059579 | 0.059579 | 0.059579 | 0.98267 | -0.33252 | 0.98147 | -0.356 | 16.3679
55 | 0.19109 | 0.048679 | -0.19103 | -0.048638 | 6.5217e-05 | 4.1629e-05 | 0.28628 | 0.28628 | 0.28628 | 0.99423 | -0.10967 | 0.99386 | -0.11675 | 39.3241
56 | -0.19109 | -0.048679 | 0.19115 | 0.048714 | 5.4409e-05 | 3.4455e-05 | 0.28628 | 0.28628 | 0.28628 | 0.99423 | -0.10967 | 0.99454 | -0.10377 | 19.6621
57 | 0.11061 | 0.028168 | -0.11022 | -0.027917 | 0.00039378 | 0.00025153 | 0.16577 | 0.16577 | 0.16577 | 0.99386 | -0.11675 | 0.99 | -0.19085 | 45.5406
58 | -0.19587 | -0.049897 | 0.19625 | 0.050135 | 0.00037434 | 0.00023716 | 0.29335 | 0.29335 | 0.29335 | 0.99454 | -0.10377 | 0.99662 | -0.064239 | 20.1475
59 | 0.012426 | 0.0031154 | -0.012422 | -0.0031133 | 3.8793e-06 | 2.1133e-06 | 0.018823 | 0.018823 | 0.018823 | 0.98233 | -0.33919 | 0.98199 | -0.34574 | 5.1712
60 | 0.035878 | 0.0090396 | -0.035854 | -0.0090246 | 2.3775e-05 | 1.4946e-05 | 0.054412 | 0.054412 | 0.054412 | 0.98147 | -0.356 | 0.98076 | -0.36986 | 14.9485
61 | 0.010604 | 0.0026578 | -0.010604 | -0.0026575 | 5.9296e-07 | 2.9998e-07 | 0.015964 | 0.015964 | 0.015964 | 0.98842 | -0.22141 | 0.98836 | -0.22258 | 4.3858
62 | -0.010604 | -0.0026578 | 0.010607 | 0.002659 | 2.2889e-06 | 1.1579e-06 | 0.015964 | 0.015964 | 0.015964 | 0.98842 | -0.22141 | 0.98865 | -0.21688 | 4.3858
63 | -0.021079 | -0.0052837 | 0.021095 | 0.0052932 | 1.5587e-05 | 9.4455e-06 | 0.031727 | 0.031726 | 0.031727 | 0.98865 | -0.21688 | 0.98945 | -0.20137 | 8.7161
64 | -0.029576 | -0.0074265 | 0.029593 | 0.0074371 | 1.706e-05 | 1.0636e-05 | 0.04498 | 0.04498 | 0.04498 | 0.97852 | -0.41357 | 0.97914 | -0.40149 | 12.3572
65 | 0.026722 | 0.0067112 | -0.026707 | -0.0067019 | 1.5019e-05 | 9.3075e-06 | 0.04064 | 0.04064 | 0.04064 | 0.97852 | -0.41357 | 0.97792 | -0.42536 | 11.1649
66 | -0.031533 | -0.0079234 | 0.031553 | 0.0079361 | 2.0281e-05 | 1.2683e-05 | 0.047929 | 0.047929 | 0.047929 | 0.97914 | -0.40149 | 0.97983 | -0.38802 | 13.1673
67 | 0.02461 | 0.0061764 | -0.024593 | -0.0061659 | 1.693e-05 | 1.0432e-05 | 0.03745 | 0.03745 | 0.03745 | 0.97792 | -0.42536 | 0.97719 | -0.43979 | 10.2884
68 | -0.031553 | -0.0079361 | 0.031566 | 0.0079442 | 1.2865e-05 | 8.0454e-06 | 0.047929 | 0.047929 | 0.047929 | 0.97983 | -0.38802 | 0.98026 | -0.37949 | 13.1673
69 | 0.01896 | 0.0047544 | -0.018953 | -0.0047506 | 6.3438e-06 | 3.8059e-06 | 0.028872 | 0.028872 | 0.028872 | 0.97719 | -0.43979 | 0.97683 | -0.44681 | 7.9319
70 | 0.0056333 | 0.0014115 | -0.0056329 | -0.0014115 | 4.1759e-07 | 7.7686e-08 | 0.008578 | 0.0085781 | 0.0085781 | 0.97719 | -0.43979 | 0.97711 | -0.44135 | 2.3566
71 | -0.033869 | -0.0085213 | 0.033885 | 0.0085311 | 1.5585e-05 | 9.7759e-06 | 0.051425 | 0.051425 | 0.051425 | 0.98026 | -0.37949 | 0.98076 | -0.36986 | 14.1277
72 | 0.0023031 | 0.00057718 | -0.0023031 | -0.00057722 | 1.9321e-08 | -4.0774e-08 | 0.0034961 | 0.0034961 | 0.0034961 | 0.98026 | -0.37949 | 0.98025 | -0.37967 | 0.96047
73 | 0.010263 | 0.0025722 | -0.010262 | -0.0025716 | 1.2546e-06 | 6.3161e-07 | 0.015634 | 0.015634 | 0.015634 | 0.97683 | -0.44681 | 0.9767 | -0.44938 | 4.295
74 | 0.0086904 | 0.0021784 | -0.0086887 | -0.0021776 | 1.7448e-06 | 7.8442e-07 | 0.013238 | 0.013238 | 0.013238 | 0.97683 | -0.44681 | 0.97662 | -0.45103 | 3.6369
75 | 0.003524 | 0.00088292 | -0.0035236 | -0.0008831 | 3.5526e-07 | -1.8461e-07 | 0.0053665 | 0.0053666 | 0.0053666 | 0.97711 | -0.44135 | 0.977 | -0.44346 | 1.4743
76 | 0.0084367 | 0.0021145 | -0.0084352 | -0.0021138 | 1.5647e-06 | 6.7851e-07 | 0.012784 | 0.012784 | 0.012784 | 0.98199 | -0.34574 | 0.9818 | -0.34963 | 3.5122
77 | 0.01095 | 0.0027448 | -0.010948 | -0.0027438 | 1.8966e-06 | 9.7521e-07 | 0.016483 | 0.016483 | 0.016483 | 0.98855 | -0.21969 | 0.98836 | -0.22333 | 4.5282
78 | -0.013414 | -0.0033624 | 0.013416 | 0.0033637 | 2.2135e-06 | 1.231e-06 | 0.020192 | 0.020192 | 0.020192 | 0.98855 | -0.21969 | 0.98872 | -0.21623 | 5.5473
79 | 0.0092055 | 0.0023071 | -0.0092043 | -0.0023065 | 1.2661e-06 | 5.8505e-07 | 0.013859 | 0.013859 | 0.013859 | 0.98836 | -0.22333 | 0.98821 | -0.22622 | 3.8075
80 | -0.015759 | -0.0039509 | 0.015763 | 0.0039531 | 3.8128e-06 | 2.2083e-06 | 0.023718 | 0.023718 | 0.023718 | 0.98872 | -0.21623 | 0.98899 | -0.21115 | 6.5159
81 | 0.0053825 | 0.0013487 | -0.0053823 | -0.0013487 | 1.9987e-07 | 2.3964e-08 | 0.0081046 | 0.0081047 | 0.0081047 | 0.98821 | -0.22622 | 0.98817 | -0.227 | 2.2266
82 | -0.017294 | -0.0043367 | 0.017301 | 0.0043411 | 7.3488e-06 | 4.3317e-06 | 0.026021 | 0.026021 | 0.026021 | 0.98899 | -0.21115 | 0.98944 | -0.20224 | 7.1487
83 | -0.02263 | -0.0056766 | 0.022642 | 0.0056836 | 1.1375e-05 | 6.9435e-06 | 0.034035 | 0.034035 | 0.034035 | 0.98944 | -0.20224 | 0.98999 | -0.1917 | 9.3504
84 | -0.024875 | -0.0062433 | 0.024882 | 0.0062475 | 6.817e-06 | 4.1957e-06 | 0.037392 | 0.037392 | 0.037392 | 0.98999 | -0.1917 | 0.99028 | -0.18596 | 10.2726
85 | -0.0074784 | -0.0018741 | 0.0074798 | 0.0018746 | 1.3954e-06 | 5.0276e-07 | 0.011156 | 0.011156 | 0.011156 | 0.99744 | -0.049279 | 0.99764 | -0.045363 | 3.065
86 | -0.0091168 | -0.0022849 | 0.0091172 | 0.0022851 | 4.0795e-07 | 1.8426e-07 | 0.013598 | 0.013598 | 0.013598 | 0.99764 | -0.045363 | 0.99769 | -0.044424 | 3.7357
87 | 0.0067201 | 0.0016837 | -0.0067192 | -0.0016834 | 9.3093e-07 | 2.7312e-07 | 0.010023 | 0.010023 | 0.010023 | 0.99769 | -0.044424 | 0.99754 | -0.047333 | 2.7535
88 | -0.015837 | -0.0039688 | 0.015843 | 0.0039719 | 5.4471e-06 | 3.146e-06 | 0.023621 | 0.02362 | 0.023621 | 0.99769 | -0.044424 | 0.99806 | -0.037206 | 6.4892
89 | -0.010878 | -0.0027264 | 0.010881 | 0.0027278 | 2.7325e-06 | 1.4155e-06 | 0.016559 | 0.016559 | 0.016559 | 0.97756 | -0.43263 | 0.97783 | -0.42736 | 4.5492
90 | -0.021872 | -0.0054833 | 0.021877 | 0.0054863 | 5.0175e-06 | 3.0597e-06 | 0.033285 | 0.033285 | 0.033285 | 0.97783 | -0.42736 | 0.97807 | -0.42255 | 9.1443
91 | 0.010991 | 0.0027554 | -0.010988 | -0.0027539 | 2.9053e-06 | 1.5121e-06 | 0.016726 | 0.016726 | 0.016726 | 0.97783 | -0.42736 | 0.97754 | -0.43291 | 4.5952
92 | -0.021877 | -0.0054863 | 0.021888 | 0.0054925 | 1.0131e-05 | 6.1779e-06 | 0.033285 | 0.033285 | 0.033285 | 0.97807 | -0.42255 | 0.97857 | -0.41283 | 9.1442
93 | 0.073082 | 0.018431 | -0.072962 | -0.018355 | 0.00011921 | 7.5963e-05 | 0.1106 | 0.1106 | 0.1106 | 0.98363 | -0.31393 | 0.98188 | -0.34807 | 30.3841
94 | -0.073082 | -0.018431 | 0.073283 | 0.01856 | 0.00020193 | 0.00012867 | 0.1106 | 0.1106 | 0.1106 | 0.98363 | -0.31393 | 0.9866 | -0.25638 | 30.3841
95 | 0.05715 | 0.014393 | -0.057099 | -0.01436 | 5.1171e-05 | 3.252e-05 | 0.086635 | 0.086635 | 0.086635 | 0.98188 | -0.34807 | 0.98092 | -0.36681 | 23.8009
96 | -0.073283 | -0.01856 | 0.073478 | 0.018684 | 0.00019416 | 0.00012372 | 0.1106 | 0.1106 | 0.1106 | 0.9866 | -0.25638 | 0.98945 | -0.20137 | 30.384
97 | -0.030365 | -0.0076172 | 0.030381 | 0.0076271 | 1.5783e-05 | 9.8533e-06 | 0.046176 | 0.046176 | 0.046176 | 0.97857 | -0.41283 | 0.97912 | -0.40194 | 12.6858
98 | 0.057099 | 0.01436 | -0.057044 | -0.014325 | 5.4703e-05 | 3.4765e-05 | 0.086635 | 0.086635 | 0.086635 | 0.98092 | -0.36681 | 0.97989 | -0.38689 | 23.8009
99 | -0.094573 | -0.023977 | 0.09462 | 0.024007 | 4.7854e-05 | 3.0545e-05 | 0.14232 | 0.14232 | 0.14232 | 0.98945 | -0.20137 | 0.99 | -0.19085 | 39.1
100 | -0.018571 | -0.0046547 | 0.018577 | 0.0046581 | 5.8198e-06 | 3.4799e-06 | 0.028234 | 0.028234 | 0.028234 | 0.97879 | -0.40851 | 0.97912 | -0.40194 | 7.7565
101 | 0.011778 | 0.0029522 | -0.011776 | -0.0029509 | 2.384e-06 | 1.2766e-06 | 0.017906 | 0.017906 | 0.017906 | 0.97879 | -0.40851 | 0.97857 | -0.41276 | 4.9192
102 | -0.048958 | -0.012285 | 0.048994 | 0.012307 | 3.5161e-05 | 2.229e-05 | 0.07441 | 0.07441 | 0.07441 | 0.97912 | -0.40194 | 0.97989 | -0.38689 | 20.4422
103 | 0.0039732 | 0.00099545 | -0.0039731 | -0.00099548 | 1.0935e-07 | -3.0379e-08 | 0.0060415 | 0.0060415 | 0.0060415 | 0.97857 | -0.41276 | 0.97854 | -0.41334 | 1.6598
104 | -0.013421 | -0.0033636 | 0.013425 | 0.003366 | 4.2486e-06 | 2.3512e-06 | 0.020037 | 0.020037 | 0.020037 | 0.99668 | -0.063201 | 0.99702 | -0.056558 | 5.5048
105 | -0.4511 | -0.1149 | 0.45233 | 0.11569 | 0.0012344 | 0.0007885 | 0.6739 | 0.6739 | 0.6739 | 0.99702 | -0.056558 | 1 | 0 | 46.2842
106 | 0.43767 | 0.11154 | -0.43751 | -0.11143 | 0.00016217 | 0.00010358 | 0.65386 | 0.65386 | 0.65386 | 0.99702 | -0.056558 | 0.99662 | -0.064239 | 44.9081
107 | -0.01817 | -0.0045552 | 0.01818 | 0.0045612 | 1.0068e-05 | 5.9649e-06 | 0.02709 | 0.02709 | 0.02709 | 0.99806 | -0.037206 | 0.99867 | -0.025585 | 7.4424
108 | -0.027671 | -0.0069399 | 0.027676 | 0.006943 | 5.0567e-06 | 3.1325e-06 | 0.041232 | 0.041232 | 0.041232 | 0.99867 | -0.025585 | 0.99887 | -0.021751 | 11.3275
109 | -0.029808 | -0.0074772 | 0.02982 | 0.0074849 | 1.2501e-05 | 7.7795e-06 | 0.044407 | 0.044407 | 0.044407 | 0.99887 | -0.021751 | 0.99933 | -0.012958 | 12.1997
110 | 0.0024764 | 0.00062021 | -0.0024762 | -0.0006206 | 2.0546e-07 | -3.9263e-07 | 0.0036939 | 0.0036941 | 0.0036941 | 0.99754 | -0.047333 | 0.99745 | -0.049075 | 1.0149
111 | 0.0042427 | 0.0010632 | -0.0042424 | -0.0010632 | 3.1269e-07 | -7.1633e-08 | 0.0063287 | 0.0063288 | 0.0063288 | 0.99754 | -0.047333 | 0.99746 | -0.04888 | 1.7387
112 | -0.02982 | -0.0074849 | 0.029831 | 0.0074919 | 1.1163e-05 | 6.9462e-06 | 0.044407 | 0.044407 | 0.044407 | 0.99933 | -0.012958 | 0.99973 | -0.0051121 | 12.1997
113 | -0.029831 | -0.0074919 | 0.029839 | 0.0074964 | 7.2784e-06 | 4.5291e-06 | 0.044407 | 0.044407 | 0.044407 | 0.99973 | -0.0051121 | 1 | 0 | 12.1996
114 | 0.24126 | 0.061297 | -0.24099 | -0.061127 | 0.00026813 | 0.00017046 | 0.36052 | 0.36052 | 0.36052 | 0.99662 | -0.064239 | 0.99541 | -0.087352 | 24.7607
115 | 0.23862 | 0.060531 | -0.23851 | -0.060461 | 0.00011133 | 7.0769e-05 | 0.35697 | 0.35697 | 0.35697 | 0.99541 | -0.087352 | 0.9949 | -0.09706 | 24.5169
116 | 0.0083399 | 0.0020901 | -0.0083391 | -0.0020897 | 8.4108e-07 | 3.5457e-07 | 0.012532 | 0.012532 | 0.012532 | 0.99028 | -0.18596 | 0.99017 | -0.18808 | 3.4428
117 | -0.033222 | -0.0083376 | 0.033234 | 0.0083454 | 1.2487e-05 | 7.8199e-06 | 0.049924 | 0.049924 | 0.049924 | 0.99028 | -0.18596 | 0.99069 | -0.17808 | 13.7154
118 | 0.022869 | 0.0057375 | -0.022863 | -0.0057338 | 5.9258e-06 | 3.6179e-06 | 0.034239 | 0.034239 | 0.034239 | 0.99393 | -0.11559 | 0.99365 | -0.12102 | 9.4064
119 | 0.020488 | 0.0051386 | -0.020481 | -0.0051344 | 6.8529e-06 | 4.1345e-06 | 0.030682 | 0.030683 | 0.030683 | 0.99365 | -0.12102 | 0.99329 | -0.12804 | 8.4293
120 | 0.018247 | 0.0045746 | -0.018247 | -0.0045745 | 2.9132e-08 | 1.7299e-08 | 0.027336 | 0.027336 | 0.027336 | 0.99329 | -0.12804 | 0.99329 | -0.12808 | 7.5099
121 | -0.0043409 | -0.0010879 | 0.0043415 | 0.0010879 | 5.8847e-07 | -8.1658e-08 | 0.0065801 | 0.0065799 | 0.0065801 | 0.98165 | -0.35248 | 0.9818 | -0.34963 | 1.8077
122 | 0.002007 | 0.00050274 | -0.0020069 | -0.00050299 | 8.3103e-08 | -2.4569e-07 | 0.0030519 | 0.003052 | 0.003052 | 0.97854 | -0.41334 | 0.9785 | -0.41421 | 0.83846
123 | -0.0016775 | -0.00042042 | 0.0016775 | 0.00042035 | 1.3707e-08 | -6.3568e-08 | 0.0025351 | 0.0025351 | 0.0025351 | 0.98462 | -0.29487 | 0.98463 | -0.2947 | 0.69646
124 | -0.0033021 | -0.00082752 | 0.0033022 | 0.00082746 | 8.8426e-08 | -6.3847e-08 | 0.0049903 | 0.0049902 | 0.0049903 | 0.98463 | -0.2947 | 0.98466 | -0.29413 | 1.371
125 | 0.0048938 | 0.0012262 | -0.0048933 | -0.0012262 | 4.9139e-07 | 2.8833e-09 | 0.0073542 | 0.0073543 | 0.0073543 | 0.99017 | -0.18808 | 0.99007 | -0.19018 | 2.0204
126 | -0.0067947 | -0.0017029 | 0.0067953 | 0.0017031 | 5.8037e-07 | 1.784e-07 | 0.010183 | 0.010183 | 0.010183 | 0.99287 | -0.13625 | 0.99296 | -0.13445 | 2.7976
127 | -0.0090292 | -0.002263 | 0.0090292 | 0.002263 | 7.1342e-09 | 3.2229e-09 | 0.013531 | 0.013531 | 0.013531 | 0.99296 | -0.13445 | 0.99296 | -0.13444 | 3.7173
128 | 0.016015 | 0.0040151 | -0.016012 | -0.0040134 | 2.9102e-06 | 1.688e-06 | 0.023992 | 0.023992 | 0.023992 | 0.99329 | -0.12808 | 0.99309 | -0.13189 | 6.5913
129 | 0.013637 | 0.0034182 | -0.013637 | -0.0034182 | 1.728e-08 | 9.6316e-09 | 0.020434 | 0.020434 | 0.020434 | 0.99309 | -0.13189 | 0.99309 | -0.13192 | 5.6137
130 | -0.011261 | -0.0028224 | 0.011263 | 0.0028231 | 1.3527e-06 | 7.0187e-07 | 0.016876 | 0.016876 | 0.016876 | 0.99296 | -0.13444 | 0.99309 | -0.13192 | 4.6362
131 | 0.0032589 | 0.00081663 | -0.0032589 | -0.00081668 | 5.7597e-08 | -4.5469e-08 | 0.004898 | 0.004898 | 0.004898 | 0.99007 | -0.19018 | 0.99005 | -0.19056 | 1.3456
132 | 0.0016338 | 0.00040939 | -0.0016338 | -0.00040946 | 1.4293e-08 | -7.2137e-08 | 0.0024555 | 0.0024555 | 0.0024555 | 0.99005 | -0.19056 | 0.99004 | -0.19074 | 0.6746

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.48619 | 0.12378

## res_load
| p_mw | q_mvar
0 | 0.0067055 | 0.0016806
1 | 0.0059618 | 0.0014942
2 | 0.010261 | 0.0025717
3 | 0.0047034 | 0.0011788
4 | 0.0090411 | 0.0022659
5 | 0.0017238 | 0.00043201
6 | 0.0023976 | 0.00060089
7 | 0.0048499 | 0.0012155
8 | 0.0037131 | 0.0009306
9 | 0.0019608 | 0.00049141
10 | 0.0016353 | 0.00040985
11 | 0.0021702 | 0.00054391
12 | 0.031598 | 0.0079193
13 | 0.024532 | 0.0061483
14 | 0.0065565 | 0.0016432
15 | 0.0022355 | 0.00056028
16 | 0.0022316 | 0.0005593
17 | 0.0031278 | 0.00078391
18 | 0.003127 | 0.0007837
19 | 0.010488 | 0.0026286
20 | 0.02069 | 0.0051854
21 | 0.0027682 | 0.00069378
22 | 0.0024286 | 0.00060867
23 | 0.0016349 | 0.00040973
24 | 0.0048649 | 0.0012192
25 | 0.015072 | 0.0037773
26 | 0.0031053 | 0.00077825
27 | 0.0049377 | 0.0012375
28 | 0.0016245 | 0.00040713
29 | 0.0047237 | 0.0011839
30 | 0.002877 | 0.00072105
31 | 0.0034079 | 0.0008541
32 | 0.010604 | 0.0026575
33 | 0.010473 | 0.0026247
34 | 0.0028539 | 0.00071527
35 | 0.0019405 | 0.00048633
36 | 0.0020968 | 0.00052551
37 | 0.0021089 | 0.00052854
38 | 0.0053229 | 0.001334
39 | 0.0086887 | 0.0021776
40 | 0.0019691 | 0.00049351
41 | 0.0023031 | 0.00057722
42 | 0.0035236 | 0.0008831
43 | 0.0039852 | 0.00099879
44 | 0.0024643 | 0.00061761
45 | 0.0017425 | 0.00043671
46 | 0.0023429 | 0.00058719
47 | 0.0038218 | 0.00095784
48 | 0.0015309 | 0.00038367
49 | 0.0012606 | 0.00031593
50 | 0.0053289 | 0.0013356
51 | 0.0022336 | 0.00055978
52 | 0.0018036 | 0.00045203
53 | 0.001637 | 0.00041028
54 | 0.010878 | 0.0027264
55 | 0.010988 | 0.0027539
56 | 0.015812 | 0.0039629
57 | 0.0084777 | 0.0021247
58 | 0.0078024 | 0.0019555
59 | 0.0019414 | 0.00048657
60 | 0.0080509 | 0.0020177
61 | 0.015598 | 0.0039091
62 | 0.013421 | 0.0033636
63 | 0.0023273 | 0.00058327
64 | 0.0094912 | 0.0023787
65 | 0.0021313 | 0.00053414
66 | 0.0024762 | 0.0006206
67 | 0.0042424 | 0.0010632
68 | 0.0023752 | 0.00059529
69 | 0.0023758 | 0.00059544
70 | 0.01134 | 0.0028421
71 | 0.0046491 | 0.0011652
72 | 0.0023752 | 0.00059529
73 | 0.0022339 | 0.00055986
74 | 0.0043409 | 0.0010879
75 | 0.0040937 | 0.001026
76 | 0.001966 | 0.00049273
77 | 0.0020069 | 0.00050299
78 | 0.0034522 | 0.00086519
79 | 0.0022326 | 0.00055953
80 | 0.0016775 | 0.00042042
81 | 0.0016246 | 0.00040717
82 | 0.0034453 | 0.00086347
83 | 0.0067947 | 0.0017029
84 | 0.0022339 | 0.00055986
85 | 0.0022321 | 0.00055943
86 | 0.002375 | 0.00059522
87 | 0.0022321 | 0.00055943
88 | 0.0023745 | 0.00059511
89 | 0.001635 | 0.00040977
90 | 0.0016343 | 0.0004096
91 | 0.0016251 | 0.00040729
92 | 0.0016338 | 0.00040946
93 | 0.0026319 | 0.00065962

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1