## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_131-22_0_9_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_131-22_0_9_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_131-22_0_9_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_131-22_0_9_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_131-22_0_9_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_131-22_0_9_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_131-22_0_9_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_131-22_0_9_node_33 | 0.4 | n |  | TRUE
8 | bus_LV_131-22_0_9_node_110 | 0.4 | n |  | TRUE
9 | bus_LV_131-22_0_9_node_109 | 0.4 | n |  | TRUE
10 | bus_LV_131-22_0_9_node_50 | 0.4 | n |  | TRUE
11 | bus_LV_131-22_0_9_node_51 | 0.4 | n |  | TRUE
12 | bus_LV_131-22_0_9_node_59 | 0.4 | n |  | TRUE
13 | bus_LV_131-22_0_9_node_31 | 0.4 | n |  | TRUE
14 | bus_LV_131-22_0_9_node_111 | 0.4 | n |  | TRUE
15 | bus_LV_131-22_0_9_node_7 | 0.4 | n |  | TRUE
16 | bus_LV_131-22_0_9_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_131-22_0_9_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_131-22_0_9_node_13 | 0.4 | n |  | TRUE
19 | bus_LV_131-22_0_9_node_34 | 0.4 | n |  | TRUE
20 | bus_LV_131-22_0_9_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_131-22_0_9_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_131-22_0_9_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_131-22_0_9_node_163 | 0.4 | n |  | TRUE
24 | bus_LV_131-22_0_9_node_85 | 0.4 | n |  | TRUE
25 | bus_LV_131-22_0_9_node_86 | 0.4 | n |  | TRUE
26 | bus_LV_131-22_0_9_node_47 | 0.4 | n |  | TRUE
27 | bus_LV_131-22_0_9_node_14 | 0.4 | n |  | TRUE
28 | bus_LV_131-22_0_9_node_26 | 0.4 | n |  | TRUE
29 | bus_LV_131-22_0_9_node_151 | 0.4 | n |  | TRUE
30 | bus_LV_131-22_0_9_node_38 | 0.4 | n |  | TRUE
31 | bus_LV_131-22_0_9_node_17 | 0.4 | n |  | TRUE
32 | bus_LV_131-22_0_9_node_145 | 0.4 | n |  | TRUE
33 | bus_LV_131-22_0_9_node_150 | 0.4 | n |  | TRUE
34 | bus_LV_131-22_0_9_node_105 | 0.4 | n |  | TRUE
35 | bus_LV_131-22_0_9_node_142 | 0.4 | n |  | TRUE
36 | bus_LV_131-22_0_9_node_18 | 0.4 | n |  | TRUE
37 | bus_LV_131-22_0_9_node_114 | 0.4 | n |  | TRUE
38 | bus_LV_131-22_0_9_node_115 | 0.4 | n |  | TRUE
39 | bus_LV_131-22_0_9_node_25 | 0.4 | n |  | TRUE
40 | bus_LV_131-22_0_9_node_113 | 0.4 | n |  | TRUE
41 | bus_LV_131-22_0_9_node_20 | 0.4 | n |  | TRUE
42 | bus_LV_131-22_0_9_node_28 | 0.4 | n |  | TRUE
43 | bus_LV_131-22_0_9_node_67 | 0.4 | n |  | TRUE
44 | bus_LV_131-22_0_9_node_22 | 0.4 | n |  | TRUE
45 | bus_LV_131-22_0_9_node_45 | 0.4 | n |  | TRUE
46 | bus_LV_131-22_0_9_node_87 | 0.4 | n |  | TRUE
47 | bus_LV_131-22_0_9_node_66 | 0.4 | n |  | TRUE
48 | bus_LV_131-22_0_9_node_143 | 0.4 | n |  | TRUE
49 | bus_LV_131-22_0_9_node_27 | 0.4 | n |  | TRUE
50 | bus_LV_131-22_0_9_node_29 | 0.4 | n |  | TRUE
51 | bus_LV_131-22_0_9_node_101 | 0.4 | n |  | TRUE
52 | bus_LV_131-22_0_9_node_48 | 0.4 | n |  | TRUE
53 | bus_LV_131-22_0_9_node_49 | 0.4 | n |  | TRUE
54 | bus_LV_131-22_0_9_node_46 | 0.4 | n |  | TRUE
55 | bus_LV_131-22_0_9_node_61 | 0.4 | n |  | TRUE
56 | bus_LV_131-22_0_9_node_30 | 0.4 | n |  | TRUE
57 | bus_LV_131-22_0_9_node_76 | 0.4 | n |  | TRUE
58 | bus_LV_131-22_0_9_node_73 | 0.4 | n |  | TRUE
59 | bus_LV_131-22_0_9_node_55 | 0.4 | n |  | TRUE
60 | bus_LV_131-22_0_9_node_122 | 0.4 | n |  | TRUE
61 | bus_LV_131-22_0_9_node_32 | 0.4 | n |  | TRUE
62 | bus_LV_131-22_0_9_node_72 | 0.4 | n |  | TRUE
63 | bus_LV_131-22_0_9_node_136 | 0.4 | n |  | TRUE
64 | bus_LV_131-22_0_9_node_165 | 0.4 | n |  | TRUE
65 | bus_LV_131-22_0_9_node_39 | 0.4 | n |  | TRUE
66 | bus_LV_131-22_0_9_node_77 | 0.4 | n |  | TRUE
67 | bus_LV_131-22_0_9_node_78 | 0.4 | n |  | TRUE
68 | bus_LV_131-22_0_9_node_42 | 0.4 | n |  | TRUE
69 | bus_LV_131-22_0_9_node_147 | 0.4 | n |  | TRUE
70 | bus_LV_131-22_0_9_node_164 | 0.4 | n |  | TRUE
71 | bus_LV_131-22_0_9_node_144 | 0.4 | n |  | TRUE
72 | bus_LV_131-22_0_9_node_127 | 0.4 | n |  | TRUE
73 | bus_LV_131-22_0_9_node_146 | 0.4 | n |  | TRUE
74 | bus_LV_131-22_0_9_node_103 | 0.4 | n |  | TRUE
75 | bus_LV_131-22_0_9_node_112 | 0.4 | n |  | TRUE
76 | bus_LV_131-22_0_9_node_132 | 0.4 | n |  | TRUE
77 | bus_LV_131-22_0_9_node_148 | 0.4 | n |  | TRUE
78 | bus_LV_131-22_0_9_node_157 | 0.4 | n |  | TRUE
79 | bus_LV_131-22_0_9_node_64 | 0.4 | n |  | TRUE
80 | bus_LV_131-22_0_9_node_44 | 0.4 | n |  | TRUE
81 | bus_LV_131-22_0_9_node_125 | 0.4 | n |  | TRUE
82 | bus_LV_131-22_0_9_node_134 | 0.4 | n |  | TRUE
83 | bus_LV_131-22_0_9_node_133 | 0.4 | n |  | TRUE
84 | bus_LV_131-22_0_9_node_60 | 0.4 | n |  | TRUE
85 | bus_LV_131-22_0_9_node_135 | 0.4 | n |  | TRUE
86 | bus_LV_131-22_0_9_node_74 | 0.4 | n |  | TRUE
87 | bus_LV_131-22_0_9_node_53 | 0.4 | n |  | TRUE
88 | bus_LV_131-22_0_9_node_75 | 0.4 | n |  | TRUE
89 | bus_LV_131-22_0_9_node_70 | 0.4 | n |  | TRUE
90 | bus_LV_131-22_0_9_node_58 | 0.4 | n |  | TRUE
91 | bus_LV_131-22_0_9_node_137 | 0.4 | n |  | TRUE
92 | bus_LV_131-22_0_9_node_56 | 0.4 | n |  | TRUE
93 | bus_LV_131-22_0_9_node_54 | 0.4 | n |  | TRUE
94 | bus_LV_131-22_0_9_node_166 | 0.4 | n |  | TRUE
95 | bus_LV_131-22_0_9_node_140 | 0.4 | n |  | TRUE
96 | bus_LV_131-22_0_9_node_94 | 0.4 | n |  | TRUE
97 | bus_LV_131-22_0_9_node_83 | 0.4 | n |  | TRUE
98 | bus_LV_131-22_0_9_node_167 | 0.4 | n |  | TRUE
99 | bus_LV_131-22_0_9_node_52 | 0.4 | n |  | TRUE
100 | bus_LV_131-22_0_9_node_62 | 0.4 | n |  | TRUE
101 | bus_LV_131-22_0_9_node_63 | 0.4 | n |  | TRUE
102 | bus_LV_131-22_0_9_node_65 | 0.4 | n |  | TRUE
103 | bus_LV_131-22_0_9_node_68 | 0.4 | n |  | TRUE
104 | bus_LV_131-22_0_9_node_69 | 0.4 | n |  | TRUE
105 | bus_LV_131-22_0_9_node_71 | 0.4 | n |  | TRUE
106 | bus_LV_131-22_0_9_node_141 | 0.4 | n |  | TRUE
107 | bus_LV_131-22_0_9_node_128 | 0.4 | n |  | TRUE
108 | bus_LV_131-22_0_9_node_129 | 0.4 | n |  | TRUE
109 | bus_LV_131-22_0_9_node_79 | 0.4 | n |  | TRUE
110 | bus_LV_131-22_0_9_node_80 | 0.4 | n |  | TRUE
111 | bus_LV_131-22_0_9_node_81 | 0.4 | n |  | TRUE
112 | bus_LV_131-22_0_9_node_82 | 0.4 | n |  | TRUE
113 | bus_LV_131-22_0_9_node_84 | 0.4 | n |  | TRUE
114 | bus_LV_131-22_0_9_node_88 | 0.4 | n |  | TRUE
115 | bus_LV_131-22_0_9_node_118 | 0.4 | n |  | TRUE
116 | bus_LV_131-22_0_9_node_99 | 0.4 | n |  | TRUE
117 | bus_LV_131-22_0_9_node_117 | 0.4 | n |  | TRUE
118 | bus_LV_131-22_0_9_node_89 | 0.4 | n |  | TRUE
119 | bus_LV_131-22_0_9_node_90 | 0.4 | n |  | TRUE
120 | bus_LV_131-22_0_9_node_91 | 0.4 | n |  | TRUE
121 | bus_LV_131-22_0_9_node_92 | 0.4 | n |  | TRUE
122 | bus_LV_131-22_0_9_node_93 | 0.4 | n |  | TRUE
123 | bus_LV_131-22_0_9_node_95 | 0.4 | n |  | TRUE
124 | bus_LV_131-22_0_9_node_106 | 0.4 | n |  | TRUE
125 | bus_LV_131-22_0_9_node_119 | 0.4 | n |  | TRUE
126 | bus_LV_131-22_0_9_node_116 | 0.4 | n |  | TRUE
127 | bus_LV_131-22_0_9_node_107 | 0.4 | n |  | TRUE
128 | bus_LV_131-22_0_9_node_154 | 0.4 | n |  | TRUE
129 | bus_LV_131-22_0_9_node_96 | 0.4 | n |  | TRUE
130 | bus_LV_131-22_0_9_node_97 | 0.4 | n |  | TRUE
131 | bus_LV_131-22_0_9_node_98 | 0.4 | n |  | TRUE
132 | bus_LV_131-22_0_9_node_100 | 0.4 | n |  | TRUE
133 | bus_LV_131-22_0_9_node_126 | 0.4 | n |  | TRUE
134 | bus_LV_131-22_0_9_node_123 | 0.4 | n |  | TRUE
135 | bus_LV_131-22_0_9_node_102 | 0.4 | n |  | TRUE
136 | bus_LV_131-22_0_9_node_104 | 0.4 | n |  | TRUE
137 | bus_LV_131-22_0_9_node_108 | 0.4 | n |  | TRUE
138 | bus_LV_131-22_0_9_node_120 | 0.4 | n |  | TRUE
139 | bus_LV_131-22_0_9_node_121 | 0.4 | n |  | TRUE
140 | bus_LV_131-22_0_9_node_149 | 0.4 | n |  | TRUE
141 | bus_LV_131-22_0_9_node_152 | 0.4 | n |  | TRUE
142 | bus_LV_131-22_0_9_node_124 | 0.4 | n |  | TRUE
143 | bus_LV_131-22_0_9_node_162 | 0.4 | n |  | TRUE
144 | bus_LV_131-22_0_9_node_160 | 0.4 | n |  | TRUE
145 | bus_LV_131-22_0_9_node_130 | 0.4 | n |  | TRUE
146 | bus_LV_131-22_0_9_node_131 | 0.4 | n |  | TRUE
147 | bus_LV_131-22_0_9_node_156 | 0.4 | n |  | TRUE
148 | bus_LV_131-22_0_9_node_155 | 0.4 | n |  | TRUE
149 | bus_LV_131-22_0_9_node_153 | 0.4 | n |  | TRUE
150 | bus_LV_131-22_0_9_node_158 | 0.4 | n |  | TRUE
151 | bus_LV_131-22_0_9_node_159 | 0.4 | n |  | TRUE
152 | bus_MV_360_0_node_171 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_131-22_0_9_load_0 | 0 | 0.014488 | 0.003631 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_131-22_0_9_load_3 | 3 | 0.0080943 | 0.0020286 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_131-22_0_9_load_4 | 4 | 0.002921 | 0.00073206 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_131-22_0_9_load_6 | 6 | 0.0077571 | 0.0019441 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_131-22_0_9_load_110 | 8 | 0.0068855 | 0.0017257 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_131-22_0_9_load_109 | 9 | 0.0084661 | 0.0021218 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_131-22_0_9_load_50 | 10 | 0.0043237 | 0.0010836 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_131-22_0_9_load_51 | 11 | 0.0031754 | 0.00079583 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_131-22_0_9_load_59 | 12 | 0.0029671 | 0.00074362 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_131-22_0_9_load_7 | 15 | 0.0071529 | 0.0017927 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_131-22_0_9_load_8 | 16 | 0.001537 | 0.00038522 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_131-22_0_9_load_163 | 23 | 0.0026154 | 0.00065549 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_131-22_0_9_load_85 | 24 | 0.0043287 | 0.0010849 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_131-22_0_9_load_86 | 25 | 0.0041627 | 0.0010433 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_131-22_0_9_load_47 | 26 | 0.0015289 | 0.00038317 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_131-22_0_9_load_151 | 29 | 0.0030793 | 0.00077175 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_131-22_0_9_load_145 | 32 | 0.0021383 | 0.0005359 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_131-22_0_9_load_150 | 33 | 0.0031532 | 0.00079027 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_131-22_0_9_load_142 | 35 | 0.0029052 | 0.00072811 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_131-22_0_9_load_115 | 38 | 0.010192 | 0.0025545 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_131-22_0_9_load_113 | 40 | 0.014215 | 0.0035625 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_131-22_0_9_load_67 | 43 | 0.019176 | 0.0048059 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_131-22_0_9_load_66 | 47 | 0.02293 | 0.0057467 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_131-22_0_9_load_143 | 48 | 0.0019058 | 0.00047763 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_131-22_0_9_load_101 | 51 | 0.010239 | 0.002566 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_131-22_0_9_load_48 | 52 | 0.0024499 | 0.00061399 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_131-22_0_9_load_46 | 54 | 0.0032961 | 0.00082607 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_131-22_0_9_load_61 | 55 | 0.0036519 | 0.00091526 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_131-22_0_9_load_76 | 57 | 0.0099984 | 0.0025058 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_131-22_0_9_load_73 | 58 | 0.0023141 | 0.00057996 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_131-22_0_9_load_55 | 59 | 0.0092061 | 0.0023073 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_131-22_0_9_load_122 | 60 | 0.0034472 | 0.00086395 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_131-22_0_9_load_72 | 62 | 0.0041577 | 0.001042 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_131-22_0_9_load_136 | 63 | 0.020055 | 0.0050262 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_131-22_0_9_load_165 | 64 | 0.0031284 | 0.00078405 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_131-22_0_9_load_78 | 67 | 0.0088509 | 0.0022182 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_131-22_0_9_load_147 | 69 | 0.0035035 | 0.00087806 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_131-22_0_9_load_164 | 70 | 0.0055966 | 0.0014026 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_131-22_0_9_load_144 | 71 | 0.0028563 | 0.00071585 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_131-22_0_9_load_127 | 72 | 0.0021165 | 0.00053046 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_131-22_0_9_load_146 | 73 | 0.0055465 | 0.0013901 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_131-22_0_9_load_103 | 74 | 0.006299 | 0.0015787 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_131-22_0_9_load_112 | 75 | 0.001475 | 0.00036966 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_131-22_0_9_load_148 | 77 | 0.0073063 | 0.0018311 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_131-22_0_9_load_157 | 78 | 0.0078386 | 0.0019645 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_131-22_0_9_load_44 | 80 | 0.02944 | 0.0073783 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_131-22_0_9_load_125 | 81 | 0.0078373 | 0.0019642 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_131-22_0_9_load_134 | 82 | 0.0044964 | 0.0011269 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_131-22_0_9_load_133 | 83 | 0.0025825 | 0.00064723 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_131-22_0_9_load_60 | 84 | 0.0027612 | 0.00069203 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_131-22_0_9_load_135 | 85 | 0.0071562 | 0.0017935 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_131-22_0_9_load_74 | 86 | 0.0022576 | 0.00056581 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_131-22_0_9_load_53 | 87 | 0.0035438 | 0.00088816 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_131-22_0_9_load_75 | 88 | 0.0028555 | 0.00071565 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_131-22_0_9_load_70 | 89 | 0.016168 | 0.004052 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_131-22_0_9_load_58 | 90 | 0.0025911 | 0.00064939 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_131-22_0_9_load_137 | 91 | 0.0026622 | 0.00066721 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_131-22_0_9_load_56 | 92 | 0.0033316 | 0.00083498 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_131-22_0_9_load_166 | 94 | 0.0036852 | 0.0009236 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_131-22_0_9_load_140 | 95 | 0.0029614 | 0.00074221 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_131-22_0_9_load_94 | 96 | 0.005286 | 0.0013248 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_131-22_0_9_load_83 | 97 | 0.0060702 | 0.0015213 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_131-22_0_9_load_167 | 98 | 0.0022868 | 0.00057314 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_131-22_0_9_load_52 | 99 | 0.010855 | 0.0027206 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_131-22_0_9_load_62 | 100 | 0.0088111 | 0.0022083 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_131-22_0_9_load_63 | 101 | 0.0031273 | 0.00078377 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_131-22_0_9_load_65 | 102 | 0.0055277 | 0.0013854 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_131-22_0_9_load_68 | 103 | 0.0076229 | 0.0019105 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_131-22_0_9_load_69 | 104 | 0.017138 | 0.0042953 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_131-22_0_9_load_71 | 105 | 0.008446 | 0.0021168 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_131-22_0_9_load_141 | 106 | 0.0029393 | 0.00073665 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_131-22_0_9_load_129 | 108 | 0.0028986 | 0.00072647 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_131-22_0_9_load_79 | 109 | 0.0021655 | 0.00054273 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_131-22_0_9_load_80 | 110 | 0.0019598 | 0.00049117 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_131-22_0_9_load_82 | 112 | 0.0017603 | 0.00044117 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_131-22_0_9_load_84 | 113 | 0.0015696 | 0.00039339 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_131-22_0_9_load_88 | 114 | 0.0028073 | 0.00070357 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_131-22_0_9_load_118 | 115 | 0.0010314 | 0.0002585 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_131-22_0_9_load_99 | 116 | 0.0078391 | 0.0019647 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_131-22_0_9_load_117 | 117 | 0.0017371 | 0.00043535 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_131-22_0_9_load_89 | 118 | 0.0022078 | 0.00055333 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_131-22_0_9_load_90 | 119 | 0.0024861 | 0.00062308 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_131-22_0_9_load_91 | 120 | 0.0023627 | 0.00059214 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_131-22_0_9_load_92 | 121 | 0.0016023 | 0.00040157 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_131-22_0_9_load_93 | 122 | 0.0022893 | 0.00057374 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_131-22_0_9_load_106 | 124 | 0.002356 | 0.00059048 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_131-22_0_9_load_119 | 125 | 0.0010238 | 0.00025659 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_131-22_0_9_load_116 | 126 | 0.0025389 | 0.00063631 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_131-22_0_9_load_107 | 127 | 0.00201 | 0.00050377 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_131-22_0_9_load_154 | 128 | 0.0095152 | 0.0023847 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_131-22_0_9_load_96 | 129 | 0.0019755 | 0.0004951 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_131-22_0_9_load_97 | 130 | 0.0069978 | 0.0017538 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_131-22_0_9_load_98 | 131 | 0.0039326 | 0.00098561 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_131-22_0_9_load_100 | 132 | 0.0030868 | 0.00077363 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_131-22_0_9_load_123 | 134 | 0.002493 | 0.00062481 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_131-22_0_9_load_102 | 135 | 0.0060864 | 0.0015254 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_131-22_0_9_load_104 | 136 | 0.026362 | 0.006607 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_131-22_0_9_load_108 | 137 | 0.002084 | 0.00052231 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_131-22_0_9_load_120 | 138 | 0.0023122 | 0.00057949 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_131-22_0_9_load_149 | 140 | 0.0080497 | 0.0020174 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_131-22_0_9_load_152 | 141 | 0.0013269 | 0.00033255 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_131-22_0_9_load_124 | 142 | 0.0021997 | 0.00055129 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_131-22_0_9_load_162 | 143 | 0.0031782 | 0.00079652 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_131-22_0_9_load_160 | 144 | 0.0050518 | 0.0012661 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_131-22_0_9_load_130 | 145 | 0.0018151 | 0.00045492 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_131-22_0_9_load_131 | 146 | 0.013584 | 0.0034044 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_131-22_0_9_load_156 | 147 | 0.0020113 | 0.00050409 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_131-22_0_9_load_155 | 148 | 0.001562 | 0.00039147 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_131-22_0_9_load_153 | 149 | 0.002524 | 0.00063257 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_131-22_0_9_load_158 | 150 | 0.0020614 | 0.00051663 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_131-22_0_9_load_159 | 151 | 0.0022003 | 0.00055146 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 5 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_131-22_0_9_line_0 |  | 0 | 1 | 0.03133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
1 | LV_131-22_0_9_line_1 |  | 0 | 2 | 0.033056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
2 | LV_131-22_0_9_line_2 |  | 1 | 3 | 0.024669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_131-22_0_9_line_3 |  | 1 | 4 | 0.017098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_131-22_0_9_line_4 |  | 2 | 5 | 0.023477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
5 | LV_131-22_0_9_line_5 |  | 2 | 6 | 0.025333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_131-22_0_9_line_6 |  | 4 | 7 | 0.0097823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_131-22_0_9_line_7 |  | 5 | 8 | 0.021372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_131-22_0_9_line_8 |  | 5 | 9 | 0.022986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_131-22_0_9_line_9 |  | 7 | 12 | 0.015021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_131-22_0_9_line_10 |  | 7 | 13 | 0.022804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_131-22_0_9_line_11 |  | 8 | 14 | 0.012322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
12 | LV_131-22_0_9_line_12 |  | 10 | 11 | 0.009381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_131-22_0_9_line_13 |  | 11 | 65 | 0.0088119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_131-22_0_9_line_14 |  | 12 | 90 | 0.017867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_131-22_0_9_line_15 |  | 13 | 59 | 0.014587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_131-22_0_9_line_16 |  | 13 | 60 | 0.012884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_131-22_0_9_line_17 |  | 14 | 75 | 0.015297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_131-22_0_9_line_18 |  | 15 | 16 | 0.0038538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_131-22_0_9_line_19 |  | 15 | 17 | 0.0085995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_131-22_0_9_line_20 |  | 17 | 18 | 0.019828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_131-22_0_9_line_21 |  | 17 | 19 | 0.019926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_131-22_0_9_line_22 |  | 18 | 24 | 0.012943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_131-22_0_9_line_23 |  | 18 | 25 | 0.022556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_131-22_0_9_line_24 |  | 18 | 26 | 0.011493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_131-22_0_9_line_25 |  | 19 | 63 | 0.043958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_131-22_0_9_line_26 |  | 20 | 21 | 0.006626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_131-22_0_9_line_27 |  | 20 | 22 | 0.0091121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_131-22_0_9_line_28 |  | 20 | 23 | 0.0041535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_131-22_0_9_line_29 |  | 21 | 30 | 0.027514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_131-22_0_9_line_30 |  | 21 | 31 | 0.0087445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_131-22_0_9_line_31 |  | 21 | 32 | 0.015083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_131-22_0_9_line_32 |  | 22 | 33 | 0.01088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_131-22_0_9_line_33 |  | 23 | 70 | 0.017509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_131-22_0_9_line_34 |  | 26 | 54 | 0.020643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_131-22_0_9_line_35 |  | 27 | 28 | 0.005124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_131-22_0_9_line_36 |  | 27 | 29 | 0.036017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_131-22_0_9_line_37 |  | 28 | 48 | 0.064305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
38 | LV_131-22_0_9_line_38 |  | 29 | 33 | 0.02158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_131-22_0_9_line_39 |  | 30 | 64 | 0.013845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_131-22_0_9_line_40 |  | 31 | 34 | 0.004623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_131-22_0_9_line_41 |  | 31 | 35 | 0.017868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_131-22_0_9_line_42 |  | 32 | 73 | 0.024754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_131-22_0_9_line_43 |  | 34 | 74 | 0.012448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_131-22_0_9_line_44 |  | 35 | 76 | 0.014056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_131-22_0_9_line_45 |  | 36 | 37 | 0.038438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
46 | LV_131-22_0_9_line_46 |  | 36 | 38 | 0.017078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
47 | LV_131-22_0_9_line_47 |  | 36 | 39 | 0.0093251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
48 | LV_131-22_0_9_line_48 |  | 36 | 40 | 0.04309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_131-22_0_9_line_49 |  | 37 | 77 | 0.026049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_131-22_0_9_line_50 |  | 37 | 75 | 0.011494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
51 | LV_131-22_0_9_line_51 |  | 38 | 48 | 0.033211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
52 | LV_131-22_0_9_line_52 |  | 39 | 46 | 0.009053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
53 | LV_131-22_0_9_line_53 |  | 39 | 47 | 0.034333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_131-22_0_9_line_54 |  | 40 | 44 | 0.034082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_131-22_0_9_line_55 |  | 41 | 42 | 0.032202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_131-22_0_9_line_56 |  | 41 | 43 | 0.011323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_131-22_0_9_line_57 |  | 42 | 52 | 0.013704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_131-22_0_9_line_58 |  | 42 | 53 | 0.018138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_131-22_0_9_line_59 |  | 42 | 54 | 0.011686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_131-22_0_9_line_60 |  | 43 | 79 | 0.03145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_131-22_0_9_line_61 |  | 44 | 45 | 0.022146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_131-22_0_9_line_62 |  | 45 | 80 | 0.0013479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_131-22_0_9_line_63 |  | 46 | 81 | 0.015724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_131-22_0_9_line_64 |  | 46 | 78 | 0.03808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_131-22_0_9_line_65 |  | 47 | 79 | 0.044772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_131-22_0_9_line_66 |  | 49 | 50 | 0.049639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_131-22_0_9_line_67 |  | 49 | 51 | 0.012626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_131-22_0_9_line_68 |  | 50 | 55 | 0.03674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_131-22_0_9_line_69 |  | 51 | 61 | 0.019118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_131-22_0_9_line_70 |  | 53 | 82 | 0.012443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_131-22_0_9_line_71 |  | 53 | 83 | 0.014569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_131-22_0_9_line_72 |  | 55 | 84 | 0.023955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_131-22_0_9_line_73 |  | 56 | 57 | 0.021528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_131-22_0_9_line_74 |  | 56 | 58 | 0.030637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_131-22_0_9_line_75 |  | 57 | 85 | 0.021998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_131-22_0_9_line_76 |  | 58 | 86 | 0.0029903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_131-22_0_9_line_77 |  | 59 | 87 | 0.026124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_131-22_0_9_line_78 |  | 60 | 88 | 0.02125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_131-22_0_9_line_79 |  | 61 | 62 | 0.012179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_131-22_0_9_line_80 |  | 62 | 89 | 0.015704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_131-22_0_9_line_81 |  | 63 | 91 | 0.0088574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_131-22_0_9_line_82 |  | 64 | 94 | 0.014071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_131-22_0_9_line_83 |  | 65 | 66 | 0.004296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_131-22_0_9_line_84 |  | 65 | 67 | 0.024258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_131-22_0_9_line_85 |  | 66 | 95 | 0.021193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_131-22_0_9_line_86 |  | 66 | 68 | 0.001293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_131-22_0_9_line_87 |  | 68 | 69 | 0.0038844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_131-22_0_9_line_88 |  | 71 | 72 | 0.0145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_131-22_0_9_line_89 |  | 72 | 133 | 0.01637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_131-22_0_9_line_90 |  | 74 | 135 | 0.026193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_131-22_0_9_line_91 |  | 76 | 106 | 0.0076698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_131-22_0_9_line_92 |  | 76 | 107 | 0.004664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_131-22_0_9_line_93 |  | 77 | 140 | 0.01573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_131-22_0_9_line_94 |  | 79 | 100 | 0.02257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_131-22_0_9_line_95 |  | 81 | 116 | 0.030294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_131-22_0_9_line_96 |  | 82 | 98 | 0.012831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_131-22_0_9_line_97 |  | 84 | 90 | 0.013441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_131-22_0_9_line_98 |  | 86 | 88 | 0.0096935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_131-22_0_9_line_99 |  | 87 | 99 | 0.0033341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_131-22_0_9_line_100 |  | 89 | 103 | 0.0067547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_131-22_0_9_line_101 |  | 92 | 93 | 0.031346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_131-22_0_9_line_102 |  | 93 | 99 | 0.025576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_131-22_0_9_line_103 |  | 95 | 106 | 0.020149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_131-22_0_9_line_104 |  | 96 | 97 | 0.030335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_131-22_0_9_line_105 |  | 97 | 111 | 0.020845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_131-22_0_9_line_106 |  | 100 | 101 | 0.034452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_131-22_0_9_line_107 |  | 101 | 102 | 0.02042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_131-22_0_9_line_108 |  | 103 | 104 | 0.0070338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_131-22_0_9_line_109 |  | 104 | 105 | 0.0069272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_131-22_0_9_line_110 |  | 107 | 108 | 0.0083569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_131-22_0_9_line_111 |  | 108 | 145 | 0.011336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_131-22_0_9_line_112 |  | 109 | 110 | 0.023406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_131-22_0_9_line_113 |  | 109 | 111 | 0.0054549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_131-22_0_9_line_114 |  | 110 | 112 | 0.019547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_131-22_0_9_line_115 |  | 111 | 113 | 0.025697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_131-22_0_9_line_116 |  | 112 | 114 | 0.0033156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_131-22_0_9_line_117 |  | 114 | 115 | 0.025811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_131-22_0_9_line_118 |  | 115 | 117 | 0.0036088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_131-22_0_9_line_119 |  | 116 | 130 | 0.00531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_131-22_0_9_line_120 |  | 117 | 126 | 0.018407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_131-22_0_9_line_121 |  | 118 | 119 | 0.0010306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_131-22_0_9_line_122 |  | 118 | 120 | 0.020293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_131-22_0_9_line_123 |  | 119 | 121 | 0.0029378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_131-22_0_9_line_124 |  | 120 | 122 | 0.0044689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_131-22_0_9_line_125 |  | 121 | 123 | 0.017085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_131-22_0_9_line_126 |  | 122 | 124 | 0.00055144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_131-22_0_9_line_127 |  | 123 | 125 | 0.037651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_131-22_0_9_line_128 |  | 123 | 126 | 0.0036824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_131-22_0_9_line_129 |  | 124 | 127 | 0.01971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_131-22_0_9_line_130 |  | 125 | 128 | 0.014183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_131-22_0_9_line_131 |  | 127 | 137 | 0.0013191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_131-22_0_9_line_132 |  | 128 | 141 | 0.0078301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_131-22_0_9_line_133 |  | 129 | 130 | 0.02099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_131-22_0_9_line_134 |  | 129 | 131 | 0.00046928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_131-22_0_9_line_135 |  | 131 | 132 | 0.021623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_131-22_0_9_line_136 |  | 132 | 133 | 0.013133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_131-22_0_9_line_137 |  | 133 | 134 | 0.017877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_131-22_0_9_line_138 |  | 134 | 139 | 0.0049817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_131-22_0_9_line_139 |  | 135 | 136 | 0.051594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_131-22_0_9_line_140 |  | 137 | 138 | 0.0042307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_131-22_0_9_line_141 |  | 138 | 139 | 0.01492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_131-22_0_9_line_142 |  | 139 | 142 | 0.016309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_131-22_0_9_line_143 |  | 141 | 149 | 0.016158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_131-22_0_9_line_144 |  | 142 | 143 | 0.019116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_131-22_0_9_line_145 |  | 143 | 144 | 0.014432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_131-22_0_9_line_146 |  | 144 | 150 | 0.0062715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_131-22_0_9_line_147 |  | 145 | 146 | 0.010896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_131-22_0_9_line_148 |  | 147 | 148 | 0.034118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_131-22_0_9_line_149 |  | 148 | 149 | 0.0020232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_131-22_0_9_line_150 |  | 150 | 151 | 0.0038861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_131-22_0_9_trafo_5 | 0.63 MVA 20/0.4 kV | 152 | 5 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2682433.7581 | 1240919.6588 | 2682436.4712 | 1240920.864 | 2682462.7318 | 1240931.577
1 | 2682492.0425 | 1240946.4876 | 2682488.3355 | 1240943.3449 | 2682472.9845 | 1240935.7596 | 2682462.7318 | 1240931.577
2 | 2682433.7581 | 1240919.6588 | 2682442.6717 | 1240896.6566
3 | 2682433.7581 | 1240919.6588 | 2682427.8333 | 1240935.6976
4 | 2682492.0425 | 1240946.4876 | 2682513.1464 | 1240956.8994
5 | 2682492.0425 | 1240946.4876 | 2682482.4226 | 1240952.5583 | 2682472.489 | 1240955.0888 | 2682470.6439 | 1240958.3041
6 | 2682423.7712 | 1240944.5269 | 2682425.5157 | 1240941.9715 | 2682427.8333 | 1240935.6976
7 | 2682513.1464 | 1240956.8994 | 2682523.2935 | 1240938.0898
8 | 2682513.1464 | 1240956.8994 | 2682501.5764 | 1240976.7616
9 | 2682423.7712 | 1240944.5269 | 2682414.0439 | 1240933.0809
10 | 2682423.7712 | 1240944.5269 | 2682420.7378 | 1240948.9657 | 2682425.2622 | 1240954.2323 | 2682428.6553 | 1240958.1934 | 2682424.8018 | 1240961.7869
11 | 2682529.1439 | 1240927.245 | 2682523.2935 | 1240938.0898
12 | 2682478.728 | 1240804.9075 | 2682482.257 | 1240796.2155
13 | 2682485.5718 | 1240788.0508 | 2682482.257 | 1240796.2155
14 | 2682414.0439 | 1240933.0809 | 2682402.4734 | 1240919.4661
15 | 2682424.8018 | 1240961.7869 | 2682414.5232 | 1240972.1367
16 | 2682424.8018 | 1240961.7869 | 2682433.0815 | 1240971.6585
17 | 2682529.1439 | 1240927.245 | 2682542.6488 | 1240934.4292
18 | 2682534.3464 | 1241140.037 | 2682534.6784 | 1241136.1975
19 | 2682533.7188 | 1241127.8191 | 2682534.6921 | 1241130.1454 | 2682534.9639 | 1241132.8956 | 2682534.6784 | 1241136.1975
20 | 2682519.2284 | 1241119.2893 | 2682525.2837 | 1241117.7724 | 2682525.4288 | 1241119.8426 | 2682531.9309 | 1241125.8817 | 2682533.7188 | 1241127.8191
21 | 2682533.7188 | 1241127.8191 | 2682531.9309 | 1241125.8817 | 2682531.3507 | 1241119.2133 | 2682541.9187 | 1241119.983
22 | 2682519.2284 | 1241119.2893 | 2682506.4691 | 1241121.6693
23 | 2682519.2284 | 1241119.2893 | 2682517.9354 | 1241131.2466 | 2682517.5518 | 1241141.7685
24 | 2682519.2284 | 1241119.2893 | 2682517.8169 | 1241107.8836
25 | 2682541.9187 | 1241119.983 | 2682549.4422 | 1241114.0278 | 2682557.8299 | 1241104.6599 | 2682567.5792 | 1241085.1744
26 | 2682574.4436 | 1240815.5614 | 2682568.4879 | 1240812.6209
27 | 2682571.1494 | 1240824.055 | 2682572.6984 | 1240819.7957 | 2682574.4436 | 1240815.5614
28 | 2682574.4436 | 1240815.5614 | 2682578.1713 | 1240817.3934
29 | 2682568.4879 | 1240812.6209 | 2682570.6313 | 1240809.6597 | 2682580.4773 | 1240787.9144
30 | 2682562.0442 | 1240814.8551 | 2682565.7121 | 1240816.4628 | 2682568.4879 | 1240812.6209
31 | 2682568.4879 | 1240812.6209 | 2682562.3429 | 1240810.2337 | 2682564.5102 | 1240809.9081 | 2682567.6016 | 1240804.4193
32 | 2682571.1494 | 1240824.055 | 2682580.9529 | 1240828.7743
33 | 2682578.1713 | 1240817.3934 | 2682593.8856 | 1240825.1163
34 | 2682517.8169 | 1241107.8836 | 2682517.7397 | 1241107.26 | 2682514.0605 | 1241087.5865
35 | 2682632.8499 | 1240853.7569 | 2682637.0203 | 1240856.7505
36 | 2682632.8499 | 1240853.7569 | 2682600.3972 | 1240838.1346
37 | 2682637.0203 | 1240856.7505 | 2682638.632 | 1240860.4756 | 2682637.6244 | 1240865.4985 | 2682611.156 | 1240913.851
38 | 2682580.9529 | 1240828.7743 | 2682600.3972 | 1240838.1346
39 | 2682580.4773 | 1240787.9144 | 2682593.1218 | 1240793.5544
40 | 2682562.0442 | 1240814.8551 | 2682560.6068 | 1240819.2494
41 | 2682562.0442 | 1240814.8551 | 2682545.5574 | 1240807.9668
42 | 2682567.6016 | 1240804.4193 | 2682576.0864 | 1240789.3544 | 2682579.2464 | 1240782.5922
43 | 2682560.6068 | 1240819.2494 | 2682556.7368 | 1240831.0807
44 | 2682532.5875 | 1240802.5479 | 2682545.5574 | 1240807.9668
45 | 2682586.838 | 1240957.8692 | 2682552.7962 | 1240939.8272
46 | 2682586.838 | 1240957.8692 | 2682595.1129 | 1240942.9295
47 | 2682586.838 | 1240957.8692 | 2682590.6069 | 1240959.823 | 2682595.2124 | 1240961.9664
48 | 2682586.838 | 1240957.8692 | 2682577.0921 | 1240962.6704 | 2682561.7112 | 1240990.9889
49 | 2682552.7962 | 1240939.8272 | 2682565.6621 | 1240917.1771
50 | 2682552.7962 | 1240939.8272 | 2682542.6488 | 1240934.4292
51 | 2682611.156 | 1240913.851 | 2682605.8267 | 1240923.5865 | 2682595.1129 | 1240942.9295
52 | 2682599.6027 | 1240954.044 | 2682595.2124 | 1240961.9664
53 | 2682595.2124 | 1240961.9664 | 2682578.5913 | 1240992.0078
54 | 2682545.4443 | 1241020.9388 | 2682561.7112 | 1240990.9889
55 | 2682510.7283 | 1241076.396 | 2682515.7352 | 1241074.6866 | 2682516.9957 | 1241077.5728 | 2682526.7888 | 1241071.5379 | 2682532.5906 | 1241065.959 | 2682535.966 | 1241068.4744
56 | 2682535.966 | 1241068.4744 | 2682541.5123 | 1241058.6023
57 | 2682510.7283 | 1241076.396 | 2682504.9423 | 1241063.973
58 | 2682493.5267 | 1241082.2945 | 2682510.7283 | 1241076.396
59 | 2682510.7283 | 1241076.396 | 2682513.7702 | 1241086.034 | 2682514.0605 | 1241087.5865
60 | 2682556.9165 | 1241031.1834 | 2682541.5123 | 1241058.6023
61 | 2682545.4443 | 1241020.9388 | 2682525.628 | 1241010.9339
62 | 2682525.628 | 1241010.9339 | 2682524.6201 | 1241010.0389
63 | 2682599.6027 | 1240954.044 | 2682613.4642 | 1240961.4666
64 | 2682599.6027 | 1240954.044 | 2682617.6204 | 1240920.4958
65 | 2682556.9165 | 1241031.1834 | 2682578.5913 | 1240992.0078
66 | 2682370.5243 | 1240895.7974 | 2682367.0032 | 1240890.7005 | 2682360.0751 | 1240878.2732 | 2682353.8382 | 1240865.0773 | 2682352.5532 | 1240861.7682 | 2682357.5036 | 1240859.7799 | 2682362.7094 | 1240857.3726
67 | 2682370.5243 | 1240895.7974 | 2682375.5726 | 1240903.0949 | 2682377.9356 | 1240906.0104
68 | 2682362.7094 | 1240857.3726 | 2682373.7164 | 1240881.02 | 2682379.8654 | 1240889.7227
69 | 2682389.9733 | 1240920.863 | 2682377.9356 | 1240906.0104
70 | 2682481.7271 | 1241086.3446 | 2682493.5267 | 1241082.2945
71 | 2682493.5267 | 1241082.2945 | 2682488.7145 | 1241068.5432
72 | 2682379.8654 | 1240889.7227 | 2682393.0281 | 1240908.352 | 2682393.7696 | 1240909.2245
73 | 2682474.7948 | 1241020.9458 | 2682459.0769 | 1241035.6566
74 | 2682474.7948 | 1241020.9458 | 2682456.5416 | 1240999.1211 | 2682455.1206 | 1240997.4609
75 | 2682443.0161 | 1241050.6884 | 2682459.0769 | 1241035.6566
76 | 2682453.176 | 1240995.1892 | 2682455.1206 | 1240997.4609
77 | 2682396.1147 | 1240990.673 | 2682414.5232 | 1240972.1367
78 | 2682433.0815 | 1240971.6585 | 2682435.3795 | 1240974.3983 | 2682446.8725 | 1240987.8251
79 | 2682389.9733 | 1240920.863 | 2682380.6506 | 1240928.7004
80 | 2682380.6506 | 1240928.7004 | 2682368.6302 | 1240938.8056
81 | 2682571.5425 | 1241077.2532 | 2682567.5792 | 1241085.1744
82 | 2682593.1218 | 1240793.5544 | 2682605.9727 | 1240799.2863
83 | 2682487.1925 | 1240784.0704 | 2682485.5718 | 1240788.0508
84 | 2682485.5718 | 1240788.0508 | 2682507.9705 | 1240797.3644
85 | 2682487.1925 | 1240784.0704 | 2682506.8223 | 1240792.0576
86 | 2682487.1925 | 1240784.0704 | 2682485.9893 | 1240783.5867
87 | 2682485.9893 | 1240783.5867 | 2682487.6713 | 1240780.0853
88 | 2682707.5176 | 1240976.8629 | 2682701.36 | 1240989.991
89 | 2682694.4086 | 1241004.8113 | 2682701.36 | 1240989.991
90 | 2682548.5937 | 1240855.9755 | 2682556.7368 | 1240831.0807
91 | 2682532.5875 | 1240802.5479 | 2682525.485 | 1240799.6529
92 | 2682530.8334 | 1240806.871 | 2682532.5875 | 1240802.5479
93 | 2682573.4315 | 1240903.4993 | 2682565.6621 | 1240917.1771
94 | 2682556.9165 | 1241031.1834 | 2682576.6282 | 1241042.1765 | 2682576.6282 | 1241042.1765
95 | 2682640.1699 | 1240975.7672 | 2682613.4642 | 1240961.4666
96 | 2682473.3829 | 1241081.1694 | 2682475.2732 | 1241086.6218 | 2682476.0924 | 1241087.5227 | 2682477.2541 | 1241087.7279 | 2682481.7271 | 1241086.3446
97 | 2682393.7696 | 1240909.2245 | 2682402.4734 | 1240919.4661
98 | 2682453.176 | 1240995.1892 | 2682446.8725 | 1240987.8251
99 | 2682396.1147 | 1240990.673 | 2682393.7652 | 1240993.0387
100 | 2682363.4599 | 1240943.1521 | 2682368.6302 | 1240938.8056
101 | 2682375.743 | 1241011.1859 | 2682397.2504 | 1241033.9896
102 | 2682375.743 | 1241011.1859 | 2682393.7652 | 1240993.0387
103 | 2682506.8223 | 1240792.0576 | 2682523.2108 | 1240798.7259 | 2682525.485 | 1240799.6529
104 | 2682582.6595 | 1241209.1856 | 2682563.2884 | 1241232.5299
105 | 2682595.7022 | 1241192.9278 | 2682587.6349 | 1241203.1896 | 2682582.6595 | 1241209.1856
106 | 2682597.8895 | 1241015.5926 | 2682588.2833 | 1241023.5253 | 2682576.6282 | 1241042.1765
107 | 2682610.5694 | 1240999.8041 | 2682608.0253 | 1241001.9289 | 2682599.9491 | 1241013.8918 | 2682597.8895 | 1241015.5926
108 | 2682363.4599 | 1240943.1521 | 2682358.0758 | 1240947.6784
109 | 2682352.7734 | 1240952.136 | 2682358.0758 | 1240947.6784
110 | 2682530.8334 | 1240806.871 | 2682527.6038 | 1240814.5787
111 | 2682523.223 | 1240825.0338 | 2682527.6038 | 1240814.5787
112 | 2682598.5874 | 1241188.2984 | 2682610.9675 | 1241168.4348
113 | 2682595.7022 | 1241192.9278 | 2682598.5874 | 1241188.2984
114 | 2682610.9675 | 1241168.4348 | 2682617.3506 | 1241158.193 | 2682620.9333 | 1241151.6276
115 | 2682595.7022 | 1241192.9278 | 2682605.6564 | 1241198.1256 | 2682616.2453 | 1241201.7311 | 2682619.516 | 1241201.9955
116 | 2682620.9333 | 1241151.6276 | 2682622.5215 | 1241148.7171
117 | 2682634.8849 | 1241126.0603 | 2682622.5215 | 1241148.7171
118 | 2682634.8849 | 1241126.0603 | 2682636.6135 | 1241122.8925
119 | 2682644.8509 | 1240978.2738 | 2682640.1699 | 1240975.7672
120 | 2682645.4304 | 1241106.7349 | 2682636.6135 | 1241122.8925
121 | 2682656.334 | 1241084.5363 | 2682655.8866 | 1241085.4648
122 | 2682656.334 | 1241084.5363 | 2682665.1436 | 1241066.2552
123 | 2682655.8866 | 1241085.4648 | 2682654.6112 | 1241088.1113
124 | 2682667.0837 | 1241062.2293 | 2682665.1436 | 1241066.2552
125 | 2682647.1943 | 1241103.5025 | 2682654.6112 | 1241088.1113
126 | 2682667.0837 | 1241062.2293 | 2682667.323 | 1241061.7325
127 | 2682647.1943 | 1241103.5025 | 2682681.9139 | 1241118.0677
128 | 2682647.1943 | 1241103.5025 | 2682645.4304 | 1241106.7349
129 | 2682667.323 | 1241061.7325 | 2682675.8796 | 1241043.9766
130 | 2682694.9928 | 1241123.5544 | 2682681.9139 | 1241118.0677
131 | 2682676.4522 | 1241042.7883 | 2682675.8796 | 1241043.9766
132 | 2682694.9928 | 1241123.5544 | 2682702.2132 | 1241126.5834
133 | 2682663.3553 | 1240988.1826 | 2682644.8509 | 1240978.2738
134 | 2682663.769 | 1240988.4042 | 2682663.3553 | 1240988.1826
135 | 2682663.769 | 1240988.4042 | 2682682.8313 | 1240998.6118
136 | 2682694.4086 | 1241004.8113 | 2682682.8313 | 1240998.6118
137 | 2682694.4086 | 1241004.8113 | 2682686.8674 | 1241021.0196
138 | 2682684.7659 | 1241025.5363 | 2682686.8674 | 1241021.0196
139 | 2682521.2723 | 1240888.619 | 2682526.1901 | 1240875.3889 | 2682528.8641 | 1240874.5144 | 2682538.1944 | 1240877.8576 | 2682541.0348 | 1240870.9921 | 2682544.7161 | 1240867.8299 | 2682548.5937 | 1240855.9755
140 | 2682676.4522 | 1241042.7883 | 2682678.2888 | 1241038.9771
141 | 2682684.7659 | 1241025.5363 | 2682678.2888 | 1241038.9771
142 | 2682684.7659 | 1241025.5363 | 2682699.36 | 1241032.816
143 | 2682702.2132 | 1241126.5834 | 2682704.3287 | 1241127.4709 | 2682718.1435 | 1241128.6323
144 | 2682716.892 | 1241040.2478 | 2682710.7939 | 1241038.5193 | 2682699.36 | 1241032.816
145 | 2682730.8279 | 1241043.9022 | 2682729.3601 | 1241043.7818 | 2682716.892 | 1241040.2478
146 | 2682730.8279 | 1241043.9022 | 2682737.0784 | 1241044.415
147 | 2682513.2883 | 1240820.5592 | 2682523.223 | 1240825.0338
148 | 2682754.135 | 1241130.3895 | 2682747.9307 | 1241131.1366 | 2682720.1596 | 1241128.8018
149 | 2682720.1596 | 1241128.8018 | 2682718.1435 | 1241128.6323
150 | 2682737.0784 | 1241044.415 | 2682740.9514 | 1241044.7328

## bus_geodata
| x | y | coords
0 | 2682462.7318 | 1240931.577
1 | 2682433.7581 | 1240919.6588
2 | 2682492.0425 | 1240946.4876
3 | 2682442.6717 | 1240896.6566
4 | 2682427.8333 | 1240935.6976
5 | 2682513.1464 | 1240956.8994
6 | 2682470.6439 | 1240958.3041
7 | 2682423.7712 | 1240944.5269
8 | 2682523.2935 | 1240938.0898
9 | 2682501.5764 | 1240976.7616
10 | 2682478.728 | 1240804.9075
11 | 2682482.257 | 1240796.2155
12 | 2682414.0439 | 1240933.0809
13 | 2682424.8018 | 1240961.7869
14 | 2682529.1439 | 1240927.245
15 | 2682534.6784 | 1241136.1975
16 | 2682534.3464 | 1241140.037
17 | 2682533.7188 | 1241127.8191
18 | 2682519.2284 | 1241119.2893
19 | 2682541.9187 | 1241119.983
20 | 2682574.4436 | 1240815.5614
21 | 2682568.4879 | 1240812.6209
22 | 2682571.1494 | 1240824.055
23 | 2682578.1713 | 1240817.3934
24 | 2682506.4691 | 1241121.6693
25 | 2682517.5518 | 1241141.7685
26 | 2682517.8169 | 1241107.8836
27 | 2682632.8499 | 1240853.7569
28 | 2682637.0203 | 1240856.7505
29 | 2682600.3972 | 1240838.1346
30 | 2682580.4773 | 1240787.9144
31 | 2682562.0442 | 1240814.8551
32 | 2682567.6016 | 1240804.4193
33 | 2682580.9529 | 1240828.7743
34 | 2682560.6068 | 1240819.2494
35 | 2682545.5574 | 1240807.9668
36 | 2682586.838 | 1240957.8692
37 | 2682552.7962 | 1240939.8272
38 | 2682595.1129 | 1240942.9295
39 | 2682595.2124 | 1240961.9664
40 | 2682561.7112 | 1240990.9889
41 | 2682535.966 | 1241068.4744
42 | 2682510.7283 | 1241076.396
43 | 2682541.5123 | 1241058.6023
44 | 2682545.4443 | 1241020.9388
45 | 2682525.628 | 1241010.9339
46 | 2682599.6027 | 1240954.044
47 | 2682578.5913 | 1240992.0078
48 | 2682611.156 | 1240913.851
49 | 2682370.5243 | 1240895.7974
50 | 2682362.7094 | 1240857.3726
51 | 2682377.9356 | 1240906.0104
52 | 2682504.9423 | 1241063.973
53 | 2682493.5267 | 1241082.2945
54 | 2682514.0605 | 1241087.5865
55 | 2682379.8654 | 1240889.7227
56 | 2682474.7948 | 1241020.9458
57 | 2682459.0769 | 1241035.6566
58 | 2682455.1206 | 1240997.4609
59 | 2682414.5232 | 1240972.1367
60 | 2682433.0815 | 1240971.6585
61 | 2682389.9733 | 1240920.863
62 | 2682380.6506 | 1240928.7004
63 | 2682567.5792 | 1241085.1744
64 | 2682593.1218 | 1240793.5544
65 | 2682485.5718 | 1240788.0508
66 | 2682487.1925 | 1240784.0704
67 | 2682507.9705 | 1240797.3644
68 | 2682485.9893 | 1240783.5867
69 | 2682487.6713 | 1240780.0853
70 | 2682593.8856 | 1240825.1163
71 | 2682707.5176 | 1240976.8629
72 | 2682701.36 | 1240989.991
73 | 2682579.2464 | 1240782.5922
74 | 2682556.7368 | 1240831.0807
75 | 2682542.6488 | 1240934.4292
76 | 2682532.5875 | 1240802.5479
77 | 2682565.6621 | 1240917.1771
78 | 2682617.6204 | 1240920.4958
79 | 2682556.9165 | 1241031.1834
80 | 2682524.6201 | 1241010.0389
81 | 2682613.4642 | 1240961.4666
82 | 2682481.7271 | 1241086.3446
83 | 2682488.7145 | 1241068.5432
84 | 2682393.7696 | 1240909.2245
85 | 2682443.0161 | 1241050.6884
86 | 2682453.176 | 1240995.1892
87 | 2682396.1147 | 1240990.673
88 | 2682446.8725 | 1240987.8251
89 | 2682368.6302 | 1240938.8056
90 | 2682402.4734 | 1240919.4661
91 | 2682571.5425 | 1241077.2532
92 | 2682397.2504 | 1241033.9896
93 | 2682375.743 | 1241011.1859
94 | 2682605.9727 | 1240799.2863
95 | 2682506.8223 | 1240792.0576
96 | 2682563.2884 | 1241232.5299
97 | 2682582.6595 | 1241209.1856
98 | 2682473.3829 | 1241081.1694
99 | 2682393.7652 | 1240993.0387
100 | 2682576.6282 | 1241042.1765
101 | 2682597.8895 | 1241015.5926
102 | 2682610.5694 | 1240999.8041
103 | 2682363.4599 | 1240943.1521
104 | 2682358.0758 | 1240947.6784
105 | 2682352.7734 | 1240952.136
106 | 2682525.485 | 1240799.6529
107 | 2682530.8334 | 1240806.871
108 | 2682527.6038 | 1240814.5787
109 | 2682598.5875 | 1241188.2985
110 | 2682610.9675 | 1241168.4348
111 | 2682595.7022 | 1241192.9278
112 | 2682620.9333 | 1241151.6276
113 | 2682619.516 | 1241201.9955
114 | 2682622.5215 | 1241148.7171
115 | 2682634.8849 | 1241126.0603
116 | 2682640.1699 | 1240975.7672
117 | 2682636.6135 | 1241122.8925
118 | 2682656.334 | 1241084.5363
119 | 2682655.8866 | 1241085.4648
120 | 2682665.1436 | 1241066.2552
121 | 2682654.6112 | 1241088.1113
122 | 2682667.0837 | 1241062.2293
123 | 2682647.1943 | 1241103.5025
124 | 2682667.323 | 1241061.7325
125 | 2682681.9139 | 1241118.0677
126 | 2682645.4304 | 1241106.7349
127 | 2682675.8796 | 1241043.9766
128 | 2682694.9928 | 1241123.5544
129 | 2682663.3553 | 1240988.1826
130 | 2682644.8509 | 1240978.2738
131 | 2682663.769 | 1240988.4042
132 | 2682682.8313 | 1240998.6118
133 | 2682694.4086 | 1241004.8113
134 | 2682686.8674 | 1241021.0196
135 | 2682548.5937 | 1240855.9755
136 | 2682521.2723 | 1240888.619
137 | 2682676.4522 | 1241042.7883
138 | 2682678.2888 | 1241038.9771
139 | 2682684.7659 | 1241025.5363
140 | 2682573.4315 | 1240903.4993
141 | 2682702.2132 | 1241126.5834
142 | 2682699.36 | 1241032.816
143 | 2682716.892 | 1241040.2478
144 | 2682730.8279 | 1241043.9022
145 | 2682523.223 | 1240825.0338
146 | 2682513.2883 | 1240820.5592
147 | 2682754.135 | 1241130.3895
148 | 2682720.1596 | 1241128.8018
149 | 2682718.1435 | 1241128.6323
150 | 2682737.0784 | 1241044.415
151 | 2682740.9514 | 1241044.7328
152 | 2682492.0425 | 1240946.4876

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99793 | -0.039361 | 0.014488 | 0.003631
1 | 0.99588 | -0.078302 | 0 | 0
2 | 0.99912 | -0.016791 | 0 | 0
3 | 0.9957 | -0.081812 | 0.0080943 | 0.0020286
4 | 0.99378 | -0.11854 | 0.002921 | 0.00073206
5 | 1 | 0 | -0.62101 | -0.15924
6 | 0.99894 | -0.020223 | 0.0077571 | 0.0019441
7 | 0.9926 | -0.14114 | 0 | 0
8 | 0.99784 | -0.040744 | 0.0068855 | 0.0017257
9 | 0.99982 | -0.0033926 | 0.0084661 | 0.0021218
10 | 0.97292 | -0.52153 | 0.0043237 | 0.0010836
11 | 0.97296 | -0.52078 | 0.0031754 | 0.00079583
12 | 0.99155 | -0.16129 | 0.0029671 | 0.00074362
13 | 0.99146 | -0.16334 | 0 | 0
14 | 0.99661 | -0.063944 | 0 | 0
15 | 0.97478 | -0.48569 | 0.0071529 | 0.0017927
16 | 0.97477 | -0.4858 | 0.001537 | 0.00038522
17 | 0.97485 | -0.48432 | 0 | 0
18 | 0.97543 | -0.4729 | 0 | 0
19 | 0.97443 | -0.49263 | 0 | 0
20 | 0.97677 | -0.44584 | 0 | 0
21 | 0.97615 | -0.45798 | 0 | 0
22 | 0.97769 | -0.42781 | 0 | 0
23 | 0.97673 | -0.44646 | 0.0026154 | 0.00065549
24 | 0.97538 | -0.47393 | 0.0043287 | 0.0010849
25 | 0.97534 | -0.47462 | 0.0041627 | 0.0010433
26 | 0.97586 | -0.46451 | 0.0015289 | 0.00038317
27 | 0.98487 | -0.28811 | 0 | 0
28 | 0.98542 | -0.27756 | 0 | 0
29 | 0.98103 | -0.36261 | 0.0030793 | 0.00077175
30 | 0.97597 | -0.46141 | 0 | 0
31 | 0.97545 | -0.4717 | 0 | 0
32 | 0.97604 | -0.4601 | 0.0021383 | 0.0005359
33 | 0.97878 | -0.40632 | 0.0031532 | 0.00079027
34 | 0.97528 | -0.47498 | 0 | 0
35 | 0.97467 | -0.48708 | 0.0029052 | 0.00072811
36 | 0.99026 | -0.18476 | 0 | 0
37 | 0.99394 | -0.11451 | 0 | 0
38 | 0.98976 | -0.19438 | 0.010192 | 0.0025545
39 | 0.98921 | -0.20487 | 0 | 0
40 | 0.98853 | -0.21825 | 0.014215 | 0.0035625
41 | 0.97883 | -0.40614 | 0 | 0
42 | 0.97714 | -0.43932 | 0 | 0
43 | 0.97943 | -0.3945 | 0.019176 | 0.0048059
44 | 0.98761 | -0.23617 | 0 | 0
45 | 0.98701 | -0.24782 | 0 | 0
46 | 0.98868 | -0.21506 | 0 | 0
47 | 0.98551 | -0.27615 | 0.02293 | 0.0057467
48 | 0.98885 | -0.21162 | 0.0019058 | 0.00047763
49 | 0.98288 | -0.32883 | 0 | 0
50 | 0.98581 | -0.27188 | 0 | 0
51 | 0.98214 | -0.34336 | 0.010239 | 0.002566
52 | 0.97711 | -0.43993 | 0.0024499 | 0.00061399
53 | 0.97698 | -0.44242 | 0 | 0
54 | 0.97665 | -0.44887 | 0.0032961 | 0.00082607
55 | 0.98798 | -0.22995 | 0.0036519 | 0.00091526
56 | 0.98992 | -0.19314 | 0 | 0
57 | 0.98958 | -0.19971 | 0.0099984 | 0.0025058
58 | 0.9904 | -0.1838 | 0.0023141 | 0.00057996
59 | 0.9911 | -0.17031 | 0.0092061 | 0.0023073
60 | 0.99113 | -0.16975 | 0.0034472 | 0.00086395
61 | 0.98119 | -0.36188 | 0 | 0
62 | 0.98059 | -0.37369 | 0.0041577 | 0.001042
63 | 0.9735 | -0.51097 | 0.020055 | 0.0050262
64 | 0.97589 | -0.46314 | 0.0031284 | 0.00078405
65 | 0.97302 | -0.51957 | 0 | 0
66 | 0.97309 | -0.51827 | 0 | 0
67 | 0.97282 | -0.52352 | 0.0088509 | 0.0022182
68 | 0.97308 | -0.51836 | 0 | 0
69 | 0.97307 | -0.51861 | 0.0035035 | 0.00087806
70 | 0.97664 | -0.44825 | 0.0055966 | 0.0014026
71 | 0.97842 | -0.41358 | 0.0028563 | 0.00071585
72 | 0.97846 | -0.41283 | 0.0021165 | 0.00053046
73 | 0.97591 | -0.46261 | 0.0055465 | 0.0013901
74 | 0.97483 | -0.48382 | 0.006299 | 0.0015787
75 | 0.99508 | -0.092823 | 0.001475 | 0.00036966
76 | 0.97409 | -0.49845 | 0 | 0
77 | 0.99358 | -0.12157 | 0.0073063 | 0.0018311
78 | 0.98841 | -0.22038 | 0.0078386 | 0.0019645
79 | 0.98164 | -0.35132 | 0 | 0
80 | 0.98697 | -0.24853 | 0.02944 | 0.0073783
81 | 0.98695 | -0.24832 | 0.0078373 | 0.0019642
82 | 0.9769 | -0.44396 | 0.0044964 | 0.0011269
83 | 0.97695 | -0.44311 | 0.0025825 | 0.00064723
84 | 0.98948 | -0.20115 | 0.0027612 | 0.00069203
85 | 0.98944 | -0.20252 | 0.0071562 | 0.0017935
86 | 0.99045 | -0.18276 | 0.0022576 | 0.00056581
87 | 0.99067 | -0.17854 | 0.0035438 | 0.00088816
88 | 0.99065 | -0.17902 | 0.0028555 | 0.00071565
89 | 0.97987 | -0.38775 | 0.016168 | 0.004052
90 | 0.99035 | -0.18437 | 0.0025911 | 0.00064939
91 | 0.97348 | -0.51141 | 0.0026622 | 0.00066721
92 | 0.99046 | -0.18275 | 0.0033316 | 0.00083498
93 | 0.99055 | -0.18089 | 0 | 0
94 | 0.97584 | -0.46409 | 0.0036852 | 0.0009236
95 | 0.97348 | -0.51053 | 0.0029614 | 0.00074221
96 | 0.97016 | -0.57621 | 0.005286 | 0.0013248
97 | 0.97031 | -0.57324 | 0.0060702 | 0.0015213
98 | 0.97687 | -0.4445 | 0.0022868 | 0.00057314
99 | 0.99063 | -0.17938 | 0.010855 | 0.0027206
100 | 0.98128 | -0.35846 | 0.0088111 | 0.0022083
101 | 0.981 | -0.36386 | 0.0031273 | 0.00078377
102 | 0.9809 | -0.3659 | 0.0055277 | 0.0013854
103 | 0.97966 | -0.39182 | 0.0076229 | 0.0019105
104 | 0.9795 | -0.39509 | 0.017138 | 0.0042953
105 | 0.97944 | -0.39616 | 0.008446 | 0.0021168
106 | 0.97391 | -0.50208 | 0.0029393 | 0.00073665
107 | 0.97401 | -0.50002 | 0 | 0
108 | 0.97387 | -0.50283 | 0.0028986 | 0.00072647
109 | 0.97059 | -0.56755 | 0.0021655 | 0.00054273
110 | 0.97092 | -0.56102 | 0.0019598 | 0.00049117
111 | 0.97053 | -0.56886 | 0 | 0
112 | 0.97124 | -0.55486 | 0.0017603 | 0.00044117
113 | 0.97049 | -0.5696 | 0.0015696 | 0.00039339
114 | 0.97129 | -0.5537 | 0.0028073 | 0.00070357
115 | 0.97181 | -0.5434 | 0.0010314 | 0.0002585
116 | 0.98383 | -0.30847 | 0.0078391 | 0.0019647
117 | 0.97189 | -0.54189 | 0.0017371 | 0.00043535
118 | 0.97329 | -0.51421 | 0.0022078 | 0.00055333
119 | 0.97325 | -0.51514 | 0.0024861 | 0.00062308
120 | 0.97426 | -0.49511 | 0.0023627 | 0.00059214
121 | 0.97312 | -0.51765 | 0.0016023 | 0.00040157
122 | 0.97449 | -0.49072 | 0.0022893 | 0.00057374
123 | 0.9724 | -0.53178 | 0 | 0
124 | 0.97452 | -0.49015 | 0.002356 | 0.00059048
125 | 0.97177 | -0.54426 | 0.0010238 | 0.00025659
126 | 0.97231 | -0.53361 | 0.0025389 | 0.00063631
127 | 0.97559 | -0.46912 | 0.00201 | 0.00050377
128 | 0.97155 | -0.54869 | 0.0095152 | 0.0023847
129 | 0.98145 | -0.3546 | 0.0019755 | 0.0004951
130 | 0.98332 | -0.3183 | 0.0069978 | 0.0017538
131 | 0.98141 | -0.3554 | 0.0039326 | 0.00098561
132 | 0.9796 | -0.39063 | 0.0030868 | 0.00077363
133 | 0.97854 | -0.41135 | 0 | 0
134 | 0.97717 | -0.438 | 0.002493 | 0.00062481
135 | 0.97404 | -0.49943 | 0.0060864 | 0.0015254
136 | 0.97277 | -0.52445 | 0.026362 | 0.006607
137 | 0.97566 | -0.46767 | 0.002084 | 0.00052231
138 | 0.97591 | -0.46284 | 0.0023122 | 0.00057949
139 | 0.97681 | -0.44522 | 0 | 0
140 | 0.99346 | -0.1238 | 0.0080497 | 0.0020174
141 | 0.97149 | -0.54977 | 0.0013269 | 0.00033255
142 | 0.97658 | -0.44959 | 0.0021997 | 0.00055129
143 | 0.97636 | -0.45396 | 0.0031782 | 0.00079652
144 | 0.97624 | -0.45642 | 0.0050518 | 0.0012661
145 | 0.97371 | -0.50604 | 0.0018151 | 0.00045492
146 | 0.97357 | -0.50876 | 0.013584 | 0.0034044
147 | 0.97133 | -0.55299 | 0.0020113 | 0.00050409
148 | 0.97139 | -0.55172 | 0.001562 | 0.00039147
149 | 0.9714 | -0.55159 | 0.002524 | 0.00063257
150 | 0.97621 | -0.45691 | 0.0020614 | 0.00051663
151 | 0.9762 | -0.45706 | 0.0022003 | 0.00055146
152 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.14329 | 0.036513 | -0.14302 | -0.036342 | 0.0002687 | 0.00017115 | 0.21387 | 0.21387 | 0.21387 | 0.99793 | -0.039361 | 0.99588 | -0.078302 | 29.3778
1 | -0.15778 | -0.040144 | 0.15795 | 0.040252 | 0.00017183 | 0.00010824 | 0.23547 | 0.23547 | 0.23547 | 0.99793 | -0.039361 | 0.99912 | -0.016791 | 16.1726
2 | 0.0080956 | 0.0020292 | -0.0080943 | -0.0020286 | 1.3536e-06 | 5.4537e-07 | 0.012096 | 0.012096 | 0.012096 | 0.99588 | -0.078302 | 0.9957 | -0.081812 | 3.3232
3 | 0.13492 | 0.034312 | -0.13466 | -0.034146 | 0.00026104 | 0.00016685 | 0.20177 | 0.20177 | 0.20177 | 0.99588 | -0.078302 | 0.99378 | -0.11854 | 55.4326
4 | -0.16571 | -0.042197 | 0.16584 | 0.042281 | 0.00013431 | 8.4727e-05 | 0.24703 | 0.24703 | 0.24703 | 0.99912 | -0.016791 | 1 | 0 | 16.9662
5 | 0.0077583 | 0.0019446 | -0.0077571 | -0.0019441 | 1.2684e-06 | 4.8006e-07 | 0.011555 | 0.011555 | 0.011555 | 0.99912 | -0.016791 | 0.99894 | -0.020223 | 3.1744
6 | 0.13174 | 0.033414 | -0.1316 | -0.033322 | 0.00014295 | 9.1359e-05 | 0.1974 | 0.1974 | 0.1974 | 0.99378 | -0.11854 | 0.9926 | -0.14114 | 54.231
7 | 0.44505 | 0.11484 | -0.44417 | -0.11428 | 0.00088184 | 0.00056326 | 0.66341 | 0.66341 | 0.66341 | 1 | 0 | 0.99784 | -0.040744 | 45.5642
8 | 0.0084675 | 0.0021224 | -0.0084661 | -0.0021218 | 1.3685e-06 | 5.743e-07 | 0.0126 | 0.0126 | 0.0126 | 1 | 0 | 0.99982 | -0.0033926 | 3.4615
9 | 0.076519 | 0.019477 | -0.076445 | -0.01943 | 7.4258e-05 | 4.7331e-05 | 0.11482 | 0.11482 | 0.11482 | 0.9926 | -0.14114 | 0.99155 | -0.16129 | 31.5431
10 | 0.055079 | 0.013845 | -0.055021 | -0.013808 | 5.8323e-05 | 3.7032e-05 | 0.082584 | 0.082584 | 0.082584 | 0.9926 | -0.14114 | 0.99146 | -0.16334 | 22.688
11 | 0.43728 | 0.11255 | -0.43679 | -0.11224 | 0.00049281 | 0.00031476 | 0.65315 | 0.65315 | 0.65315 | 0.99784 | -0.040744 | 0.99661 | -0.063944 | 44.859
12 | -0.0043237 | -0.0010836 | 0.0043238 | 0.0010836 | 1.5383e-07 | -1.8051e-08 | 0.0066127 | 0.0066127 | 0.0066127 | 0.97292 | -0.52153 | 0.97296 | -0.52078 | 1.8167
13 | -0.0074992 | -0.0018794 | 0.0074996 | 0.0018796 | 4.3466e-07 | 1.6874e-07 | 0.011469 | 0.011469 | 0.011469 | 0.97296 | -0.52078 | 0.97302 | -0.51957 | 3.1508
14 | 0.073478 | 0.018686 | -0.073396 | -0.018634 | 8.1611e-05 | 5.2001e-05 | 0.11036 | 0.11036 | 0.11036 | 0.99155 | -0.16129 | 0.99035 | -0.18437 | 30.3199
15 | 0.026954 | 0.0067606 | -0.026945 | -0.006755 | 8.9523e-06 | 5.5414e-06 | 0.040455 | 0.040455 | 0.040455 | 0.99146 | -0.16334 | 0.9911 | -0.17031 | 11.1141
16 | 0.028067 | 0.0070476 | -0.028059 | -0.0070423 | 8.5753e-06 | 5.3221e-06 | 0.042129 | 0.042129 | 0.042129 | 0.99146 | -0.16334 | 0.99113 | -0.16975 | 11.5739
17 | 0.43679 | 0.11224 | -0.43618 | -0.11185 | 0.00061178 | 0.00039075 | 0.65315 | 0.65315 | 0.65315 | 0.99661 | -0.063944 | 0.99508 | -0.092823 | 44.859
18 | 0.001537 | 0.00038518 | -0.001537 | -0.00038522 | 7.956e-09 | -4.2949e-08 | 0.0023463 | 0.0023463 | 0.0023463 | 0.97478 | -0.48569 | 0.97477 | -0.4858 | 0.64459
19 | -0.0086899 | -0.0021779 | 0.0086905 | 0.0021781 | 5.6746e-07 | 2.5597e-07 | 0.013265 | 0.013265 | 0.013265 | 0.97478 | -0.48569 | 0.97485 | -0.48432 | 3.6443
20 | -0.031436 | -0.0078891 | 0.031453 | 0.0078998 | 1.7123e-05 | 1.0711e-05 | 0.047988 | 0.047988 | 0.047988 | 0.97485 | -0.48432 | 0.97543 | -0.4729 | 13.1836
21 | 0.022746 | 0.005711 | -0.022737 | -0.0057055 | 9.0092e-06 | 5.5175e-06 | 0.034723 | 0.034723 | 0.034723 | 0.97485 | -0.48432 | 0.97443 | -0.49263 | 9.5393
22 | 0.0043289 | 0.0010849 | -0.0043287 | -0.0010849 | 2.1167e-07 | -2.6085e-08 | 0.0066038 | 0.0066038 | 0.0066038 | 0.97543 | -0.4729 | 0.97538 | -0.47393 | 1.8142
23 | 0.004163 | 0.0010432 | -0.0041627 | -0.0010433 | 3.4114e-07 | -6.3198e-08 | 0.0063506 | 0.0063507 | 0.0063507 | 0.97543 | -0.4729 | 0.97534 | -0.47462 | 1.7447
24 | -0.039945 | -0.010028 | 0.039961 | 0.010038 | 1.6006e-05 | 1.0101e-05 | 0.060943 | 0.060943 | 0.060943 | 0.97543 | -0.4729 | 0.97586 | -0.46451 | 16.7425
25 | 0.022737 | 0.0057055 | -0.022717 | -0.0056933 | 1.9875e-05 | 1.2173e-05 | 0.034723 | 0.034723 | 0.034723 | 0.97443 | -0.49263 | 0.9735 | -0.51097 | 9.5394
26 | 0.10049 | 0.025292 | -0.10043 | -0.025255 | 5.8261e-05 | 3.7204e-05 | 0.15313 | 0.15313 | 0.15313 | 0.97677 | -0.44584 | 0.97615 | -0.45798 | 42.0673
27 | -0.1087 | -0.02735 | 0.1088 | 0.02741 | 9.3748e-05 | 5.9885e-05 | 0.16564 | 0.16564 | 0.16564 | 0.97677 | -0.44584 | 0.97769 | -0.42781 | 45.5046
28 | 0.0082128 | 0.0020583 | -0.0082125 | -0.0020582 | 2.4382e-07 | 1.0406e-07 | 0.012511 | 0.012511 | 0.012511 | 0.97677 | -0.44584 | 0.97673 | -0.44646 | 3.4372
29 | 0.0068154 | 0.0017081 | -0.0068143 | -0.0017078 | 1.1137e-06 | 3.6887e-07 | 0.010389 | 0.010389 | 0.010389 | 0.97615 | -0.45798 | 0.97597 | -0.46141 | 2.8542
30 | 0.085929 | 0.02162 | -0.085873 | -0.021584 | 5.6291e-05 | 3.5917e-05 | 0.13102 | 0.13102 | 0.13102 | 0.97615 | -0.45798 | 0.97545 | -0.4717 | 35.9943
31 | 0.0076862 | 0.0019264 | -0.0076854 | -0.0019261 | 7.765e-07 | 3.0843e-07 | 0.011717 | 0.011717 | 0.011717 | 0.97615 | -0.45798 | 0.97604 | -0.4601 | 3.2189
32 | -0.1088 | -0.02741 | 0.10891 | 0.027482 | 0.00011194 | 7.1505e-05 | 0.16564 | 0.16564 | 0.16564 | 0.97769 | -0.42781 | 0.97878 | -0.40632 | 45.5045
33 | 0.0055971 | 0.0014027 | -0.0055966 | -0.0014026 | 4.7742e-07 | 8.642e-08 | 0.008527 | 0.008527 | 0.008527 | 0.97673 | -0.44646 | 0.97664 | -0.44825 | 2.3426
34 | -0.04149 | -0.010421 | 0.041521 | 0.010441 | 3.0992e-05 | 1.9577e-05 | 0.063274 | 0.063274 | 0.063274 | 0.97586 | -0.46451 | 0.97665 | -0.44887 | 17.3829
35 | -0.11579 | -0.029458 | 0.11585 | 0.029496 | 5.8914e-05 | 3.7639e-05 | 0.1751 | 0.1751 | 0.1751 | 0.98487 | -0.28811 | 0.98542 | -0.27756 | 48.1046
36 | 0.11579 | 0.029458 | -0.11538 | -0.029194 | 0.00041411 | 0.00026457 | 0.1751 | 0.1751 | 0.1751 | 0.98487 | -0.28811 | 0.98103 | -0.36261 | 48.1046
37 | -0.11585 | -0.029496 | 0.11622 | 0.029731 | 0.00036967 | 0.00023495 | 0.1751 | 0.1751 | 0.1751 | 0.98542 | -0.27756 | 0.98885 | -0.21162 | 24.0523
38 | 0.1123 | 0.028422 | -0.11206 | -0.028272 | 0.00023506 | 0.00015017 | 0.17043 | 0.17043 | 0.17043 | 0.98103 | -0.36261 | 0.97878 | -0.40632 | 46.8215
39 | 0.0068143 | 0.0017078 | -0.0068137 | -0.0017076 | 5.6043e-07 | 1.8567e-07 | 0.010389 | 0.010389 | 0.010389 | 0.97597 | -0.46141 | 0.97589 | -0.46314 | 2.8542
40 | 0.038826 | 0.0097598 | -0.03882 | -0.009756 | 6.0835e-06 | 3.8357e-06 | 0.059238 | 0.059238 | 0.059238 | 0.97545 | -0.4717 | 0.97528 | -0.47498 | 16.2741
41 | 0.047048 | 0.011824 | -0.047013 | -0.011803 | 3.4525e-05 | 2.1873e-05 | 0.071782 | 0.071782 | 0.071782 | 0.97545 | -0.4717 | 0.97467 | -0.48708 | 19.7202
42 | 0.0055471 | 0.0013902 | -0.0055465 | -0.0013901 | 6.639e-07 | 1.1556e-07 | 0.0084569 | 0.008457 | 0.008457 | 0.97604 | -0.4601 | 0.97591 | -0.46261 | 2.3233
43 | 0.03882 | 0.009756 | -0.038803 | -0.0097457 | 1.6381e-05 | 1.0328e-05 | 0.059238 | 0.059238 | 0.059238 | 0.97528 | -0.47498 | 0.97483 | -0.48382 | 16.2741
44 | 0.044108 | 0.011074 | -0.044084 | -0.011059 | 2.3907e-05 | 1.5126e-05 | 0.067346 | 0.067346 | 0.067346 | 0.97467 | -0.48708 | 0.97409 | -0.49845 | 18.5017
45 | -0.41746 | -0.10643 | 0.41888 | 0.10733 | 0.0014209 | 0.00090741 | 0.62794 | 0.62794 | 0.62794 | 0.99026 | -0.18476 | 0.99394 | -0.11451 | 43.128
46 | 0.12847 | 0.032862 | -0.12841 | -0.032824 | 5.9818e-05 | 3.7405e-05 | 0.19329 | 0.19329 | 0.19329 | 0.99026 | -0.18476 | 0.98976 | -0.19438 | 13.2754
47 | 0.24522 | 0.062552 | -0.24498 | -0.0624 | 0.00023791 | 0.00015202 | 0.36887 | 0.36887 | 0.36887 | 0.99026 | -0.18476 | 0.98921 | -0.20487 | 50.6693
48 | 0.043767 | 0.011011 | -0.043697 | -0.010967 | 6.9923e-05 | 4.4197e-05 | 0.065781 | 0.065782 | 0.065782 | 0.99026 | -0.18476 | 0.98853 | -0.21825 | 18.0719
49 | 0.015362 | 0.0038519 | -0.015357 | -0.0038489 | 5.1671e-06 | 2.9694e-06 | 0.022999 | 0.022999 | 0.022999 | 0.99394 | -0.11451 | 0.99358 | -0.12157 | 6.3184
50 | -0.43425 | -0.11118 | 0.4347 | 0.11148 | 0.00045658 | 0.00029162 | 0.65094 | 0.65094 | 0.65094 | 0.99394 | -0.11451 | 0.99508 | -0.092823 | 44.7075
51 | 0.11822 | 0.03027 | -0.11812 | -0.030209 | 9.8612e-05 | 6.1406e-05 | 0.17797 | 0.17797 | 0.17797 | 0.98976 | -0.19438 | 0.98885 | -0.21162 | 12.2231
52 | 0.12773 | 0.032574 | -0.12767 | -0.032534 | 6.2794e-05 | 3.9956e-05 | 0.19234 | 0.19234 | 0.19234 | 0.98921 | -0.20487 | 0.98868 | -0.21506 | 26.42
53 | 0.11725 | 0.029826 | -0.11685 | -0.029569 | 0.00040124 | 0.00025636 | 0.17654 | 0.17654 | 0.17654 | 0.98921 | -0.20487 | 0.98551 | -0.27615 | 48.4988
54 | 0.029482 | 0.0074048 | -0.029457 | -0.0073891 | 2.5179e-05 | 1.5678e-05 | 0.044385 | 0.044385 | 0.044385 | 0.98853 | -0.21825 | 0.98761 | -0.23617 | 12.1937
55 | 0.056745 | 0.014299 | -0.056655 | -0.014241 | 8.9919e-05 | 5.7144e-05 | 0.086292 | 0.086292 | 0.086292 | 0.97883 | -0.40614 | 0.97714 | -0.43932 | 23.7065
56 | -0.056745 | -0.014299 | 0.056777 | 0.014319 | 3.1619e-05 | 2.0094e-05 | 0.086292 | 0.086292 | 0.086292 | 0.97883 | -0.40614 | 0.97943 | -0.3945 | 23.7065
57 | 0.0024499 | 0.00061387 | -0.0024499 | -0.00061399 | 7.1531e-08 | -1.2588e-07 | 0.0037308 | 0.0037308 | 0.0037308 | 0.97714 | -0.43932 | 0.97711 | -0.43993 | 1.025
58 | 0.0093677 | 0.0023478 | -0.0093663 | -0.0023472 | 1.3842e-06 | 6.5872e-07 | 0.014265 | 0.014266 | 0.014266 | 0.97714 | -0.43932 | 0.97698 | -0.44242 | 3.9191
59 | 0.044838 | 0.01128 | -0.044817 | -0.011267 | 2.044e-05 | 1.2935e-05 | 0.068296 | 0.068296 | 0.068296 | 0.97714 | -0.43932 | 0.97665 | -0.44887 | 18.7625
60 | -0.075953 | -0.019125 | 0.07611 | 0.019225 | 0.00015713 | 0.00010016 | 0.11542 | 0.11542 | 0.11542 | 0.97943 | -0.3945 | 0.98164 | -0.35132 | 31.7102
61 | 0.029457 | 0.0073891 | -0.029441 | -0.0073789 | 1.6361e-05 | 1.0188e-05 | 0.044385 | 0.044385 | 0.044385 | 0.98761 | -0.23617 | 0.98701 | -0.24782 | 12.1937
62 | 0.029441 | 0.0073789 | -0.02944 | -0.0073783 | 9.958e-07 | 6.2008e-07 | 0.044385 | 0.044385 | 0.044385 | 0.98701 | -0.24782 | 0.98697 | -0.24853 | 12.1937
63 | 0.11983 | 0.030569 | -0.11963 | -0.030446 | 0.00019218 | 0.0001228 | 0.18054 | 0.18054 | 0.18054 | 0.98868 | -0.21506 | 0.98695 | -0.24832 | 49.598
64 | 0.0078406 | 0.0019653 | -0.0078386 | -0.0019645 | 1.9886e-06 | 7.8452e-07 | 0.011801 | 0.011801 | 0.011801 | 0.98868 | -0.21506 | 0.98841 | -0.22038 | 3.242
65 | 0.093923 | 0.023823 | -0.093585 | -0.023607 | 0.00033814 | 0.00021584 | 0.14191 | 0.14191 | 0.14191 | 0.98551 | -0.27615 | 0.98164 | -0.35132 | 38.9876
66 | -0.063937 | -0.016088 | 0.064112 | 0.016199 | 0.00017449 | 0.00011104 | 0.096819 | 0.096819 | 0.096819 | 0.98288 | -0.32883 | 0.98581 | -0.27188 | 26.5987
67 | 0.063937 | 0.016088 | -0.063893 | -0.01606 | 4.4385e-05 | 2.8246e-05 | 0.096819 | 0.096819 | 0.096819 | 0.98288 | -0.32883 | 0.98214 | -0.34336 | 26.5987
68 | -0.064112 | -0.016199 | 0.064241 | 0.016281 | 0.00012915 | 8.2185e-05 | 0.096819 | 0.096819 | 0.096819 | 0.98581 | -0.27188 | 0.98798 | -0.22995 | 26.5986
69 | 0.053654 | 0.013493 | -0.053607 | -0.013463 | 4.7395e-05 | 3.0091e-05 | 0.081307 | 0.081307 | 0.081307 | 0.98214 | -0.34336 | 0.98119 | -0.36188 | 22.3371
70 | 0.0067838 | 0.0017001 | -0.0067833 | -0.0016999 | 4.9813e-07 | 1.63e-07 | 0.010332 | 0.010332 | 0.010332 | 0.97698 | -0.44242 | 0.9769 | -0.44396 | 2.8385
71 | 0.0025826 | 0.0006471 | -0.0025825 | -0.00064723 | 8.4529e-08 | -1.2833e-07 | 0.0039334 | 0.0039335 | 0.0039335 | 0.97698 | -0.44242 | 0.97695 | -0.44311 | 1.0806
72 | -0.067893 | -0.017196 | 0.067987 | 0.017256 | 9.4047e-05 | 5.9883e-05 | 0.10232 | 0.10232 | 0.10232 | 0.98798 | -0.22995 | 0.98948 | -0.20115 | 28.1096
73 | 0.017161 | 0.0043028 | -0.017156 | -0.0042997 | 5.3723e-06 | 3.1616e-06 | 0.025796 | 0.025797 | 0.025797 | 0.98992 | -0.19314 | 0.98958 | -0.19971 | 7.087
74 | -0.017161 | -0.0043028 | 0.017169 | 0.0043073 | 7.6453e-06 | 4.4989e-06 | 0.025796 | 0.025796 | 0.025796 | 0.98992 | -0.19314 | 0.9904 | -0.1838 | 7.0869
75 | 0.0071572 | 0.0017938 | -0.0071562 | -0.0017935 | 9.5547e-07 | 3.2893e-07 | 0.010762 | 0.010762 | 0.010762 | 0.98958 | -0.19971 | 0.98944 | -0.20252 | 2.9567
76 | -0.019483 | -0.0048873 | 0.019484 | 0.0048879 | 9.609e-07 | 5.7649e-07 | 0.029273 | 0.029273 | 0.029273 | 0.9904 | -0.1838 | 0.99045 | -0.18276 | 8.042
77 | 0.017739 | 0.0044478 | -0.017732 | -0.0044437 | 6.9491e-06 | 4.1109e-06 | 0.026633 | 0.026634 | 0.026634 | 0.9911 | -0.17031 | 0.99067 | -0.17854 | 7.3169
78 | 0.024611 | 0.0061784 | -0.024601 | -0.0061717 | 1.0882e-05 | 6.6907e-06 | 0.036954 | 0.036954 | 0.036954 | 0.99113 | -0.16975 | 0.99065 | -0.17902 | 10.1521
79 | 0.053607 | 0.013463 | -0.053577 | -0.013444 | 3.0193e-05 | 1.917e-05 | 0.081307 | 0.081307 | 0.081307 | 0.98119 | -0.36188 | 0.98059 | -0.37369 | 22.3371
80 | 0.049419 | 0.012402 | -0.049386 | -0.012381 | 3.3123e-05 | 2.1001e-05 | 0.074998 | 0.074998 | 0.074998 | 0.98059 | -0.37369 | 0.97987 | -0.38775 | 20.6038
81 | 0.0026622 | 0.00066713 | -0.0026622 | -0.00066721 | 5.5002e-08 | -7.4922e-08 | 0.0040693 | 0.0040693 | 0.0040693 | 0.9735 | -0.51097 | 0.97348 | -0.51141 | 1.1179
82 | 0.0036854 | 0.00092353 | -0.0036852 | -0.0009236 | 1.6662e-07 | -6.916e-08 | 0.0056193 | 0.0056194 | 0.0056194 | 0.97589 | -0.46314 | 0.97584 | -0.46409 | 1.5438
83 | -0.016352 | -0.0040986 | 0.016353 | 0.0040992 | 1.0074e-06 | 5.914e-07 | 0.025007 | 0.025007 | 0.025007 | 0.97302 | -0.51957 | 0.97309 | -0.51827 | 6.8701
84 | 0.0088525 | 0.002219 | -0.0088509 | -0.0022182 | 1.6673e-06 | 7.658e-07 | 0.013538 | 0.013538 | 0.013538 | 0.97302 | -0.51957 | 0.97282 | -0.52352 | 3.7193
85 | -0.019857 | -0.0049772 | 0.019864 | 0.0049816 | 7.3274e-06 | 4.4261e-06 | 0.030365 | 0.030364 | 0.030365 | 0.97309 | -0.51827 | 0.97348 | -0.51053 | 8.3419
86 | 0.0035035 | 0.00087803 | -0.0035035 | -0.00087803 | 1.3917e-08 | -7.1552e-09 | 0.0053575 | 0.0053575 | 0.0053575 | 0.97309 | -0.51827 | 0.97308 | -0.51836 | 1.4718
87 | 0.0035035 | 0.00087803 | -0.0035035 | -0.00087806 | 4.1811e-08 | -2.1495e-08 | 0.0053575 | 0.0053575 | 0.0053575 | 0.97308 | -0.51836 | 0.97307 | -0.51861 | 1.4718
88 | -0.0028563 | -0.00071585 | 0.0028564 | 0.00071573 | 1.026e-07 | -1.1645e-07 | 0.0043439 | 0.0043438 | 0.0043439 | 0.97842 | -0.41358 | 0.97846 | -0.41283 | 1.1934
89 | -0.0049729 | -0.0012462 | 0.0049733 | 0.0012462 | 3.5108e-07 | 1.9071e-08 | 0.0075626 | 0.0075625 | 0.0075626 | 0.97846 | -0.41283 | 0.97854 | -0.41135 | 2.0776
90 | 0.032504 | 0.008167 | -0.03248 | -0.0081519 | 2.4187e-05 | 1.5153e-05 | 0.049623 | 0.049623 | 0.049623 | 0.97483 | -0.48382 | 0.97404 | -0.49943 | 13.6327
91 | 0.025778 | 0.0064689 | -0.025774 | -0.0064661 | 4.4608e-06 | 2.7594e-06 | 0.039382 | 0.039382 | 0.039382 | 0.97409 | -0.49845 | 0.97391 | -0.50208 | 10.8192
92 | 0.018305 | 0.0045904 | -0.018304 | -0.0045896 | 1.3677e-06 | 8.1729e-07 | 0.027964 | 0.027964 | 0.027964 | 0.97409 | -0.49845 | 0.97401 | -0.50002 | 7.6825
93 | 0.0080506 | 0.0020178 | -0.0080497 | -0.0020174 | 8.5752e-07 | 3.4511e-07 | 0.012057 | 0.012057 | 0.012057 | 0.99358 | -0.12157 | 0.99346 | -0.1238 | 3.3123
94 | 0.017475 | 0.004382 | -0.017469 | -0.0043785 | 5.9392e-06 | 3.5159e-06 | 0.02649 | 0.02649 | 0.02649 | 0.98164 | -0.35132 | 0.98128 | -0.35846 | 7.2775
95 | 0.1118 | 0.028482 | -0.11147 | -0.028275 | 0.00032338 | 0.00020658 | 0.16872 | 0.16872 | 0.16872 | 0.98695 | -0.24832 | 0.98383 | -0.30847 | 46.3519
96 | 0.0022869 | 0.00057301 | -0.0022868 | -0.00057314 | 5.8384e-08 | -1.2328e-07 | 0.0034834 | 0.0034834 | 0.0034834 | 0.9769 | -0.44396 | 0.97687 | -0.4445 | 0.95698
97 | -0.070748 | -0.017948 | 0.070805 | 0.017985 | 5.7137e-05 | 3.6395e-05 | 0.10647 | 0.10647 | 0.10647 | 0.98948 | -0.20115 | 0.99035 | -0.18437 | 29.2504
98 | -0.021741 | -0.0054537 | 0.021745 | 0.005456 | 3.8786e-06 | 2.3575e-06 | 0.032665 | 0.032665 | 0.032665 | 0.99045 | -0.18276 | 0.99065 | -0.17902 | 8.9738
99 | 0.014188 | 0.0035555 | -0.014187 | -0.0035552 | 5.6782e-07 | 3.2048e-07 | 0.021311 | 0.021311 | 0.021311 | 0.99067 | -0.17854 | 0.99063 | -0.17938 | 5.8546
100 | 0.033218 | 0.0083292 | -0.033212 | -0.0083252 | 6.4459e-06 | 4.0403e-06 | 0.050446 | 0.050446 | 0.050446 | 0.97987 | -0.38775 | 0.97966 | -0.39182 | 13.8588
101 | -0.0033316 | -0.00083498 | 0.0033319 | 0.00083477 | 2.9448e-07 | -2.15e-07 | 0.0050053 | 0.0050051 | 0.0050053 | 0.99046 | -0.18275 | 0.99055 | -0.18089 | 1.3751
102 | -0.0033319 | -0.00083477 | 0.0033322 | 0.00083459 | 2.4026e-07 | -1.7548e-07 | 0.0050051 | 0.005005 | 0.0050051 | 0.99055 | -0.18089 | 0.99063 | -0.17938 | 1.375
103 | -0.022825 | -0.0057238 | 0.022835 | 0.0057295 | 9.1985e-06 | 5.6364e-06 | 0.034891 | 0.034891 | 0.034891 | 0.97348 | -0.51053 | 0.97391 | -0.50208 | 9.5855
104 | -0.005286 | -0.0013248 | 0.0052867 | 0.0013249 | 7.4774e-07 | 1.0392e-07 | 0.0081076 | 0.0081075 | 0.0081076 | 0.97016 | -0.57621 | 0.97031 | -0.57324 | 2.2274
105 | -0.011357 | -0.0028462 | 0.011359 | 0.0028475 | 2.3711e-06 | 1.2599e-06 | 0.017416 | 0.017416 | 0.017416 | 0.97031 | -0.57324 | 0.97053 | -0.56886 | 4.7847
106 | 0.0086578 | 0.0021702 | -0.0086555 | -0.0021692 | 2.2269e-06 | 9.9012e-07 | 0.013129 | 0.013129 | 0.013129 | 0.98128 | -0.35846 | 0.981 | -0.36386 | 3.6069
107 | 0.0055283 | 0.0013855 | -0.0055277 | -0.0013854 | 5.3844e-07 | 8.6822e-08 | 0.0083855 | 0.0083856 | 0.0083856 | 0.981 | -0.36386 | 0.9809 | -0.3659 | 2.3037
108 | 0.025589 | 0.0064147 | -0.025585 | -0.0064122 | 3.9847e-06 | 2.4616e-06 | 0.038867 | 0.038867 | 0.038867 | 0.97966 | -0.39182 | 0.9795 | -0.39509 | 10.6779
109 | 0.0084464 | 0.002117 | -0.008446 | -0.0021168 | 4.2771e-07 | 1.8655e-07 | 0.012832 | 0.012832 | 0.012832 | 0.9795 | -0.39509 | 0.97944 | -0.39616 | 3.5252
110 | 0.018304 | 0.0045896 | -0.018302 | -0.0045882 | 2.4507e-06 | 1.4644e-06 | 0.027964 | 0.027964 | 0.027964 | 0.97401 | -0.50002 | 0.97387 | -0.50283 | 7.6825
111 | 0.015403 | 0.0038617 | -0.015401 | -0.0038603 | 2.3547e-06 | 1.366e-06 | 0.023535 | 0.023535 | 0.023535 | 0.97387 | -0.50283 | 0.97371 | -0.50604 | 6.4658
112 | -0.015095 | -0.0037838 | 0.0151 | 0.0037865 | 4.7009e-06 | 2.7192e-06 | 0.023143 | 0.023143 | 0.023143 | 0.97059 | -0.56755 | 0.97092 | -0.56102 | 6.3579
113 | 0.01293 | 0.003241 | -0.012929 | -0.0032406 | 8.0381e-07 | 4.4702e-07 | 0.019823 | 0.019823 | 0.019823 | 0.97059 | -0.56755 | 0.97053 | -0.56886 | 5.4458
114 | -0.01706 | -0.0042777 | 0.017065 | 0.0042806 | 5.0112e-06 | 2.9653e-06 | 0.026146 | 0.026146 | 0.026146 | 0.97092 | -0.56102 | 0.97124 | -0.55486 | 7.183
115 | 0.0015697 | 0.0003931 | -0.0015696 | -0.00039339 | 5.5811e-08 | -2.8181e-07 | 0.0024065 | 0.0024067 | 0.0024067 | 0.97053 | -0.56886 | 0.97049 | -0.5696 | 0.66117
116 | -0.018825 | -0.0047218 | 0.018826 | 0.0047224 | 1.0344e-06 | 6.2096e-07 | 0.028843 | 0.028843 | 0.028843 | 0.97124 | -0.55486 | 0.97129 | -0.5537 | 7.9239
117 | -0.021633 | -0.005426 | 0.021644 | 0.0054325 | 1.0632e-05 | 6.4851e-06 | 0.033144 | 0.033144 | 0.033144 | 0.97129 | -0.5537 | 0.97181 | -0.5434 | 9.1054
118 | -0.022675 | -0.005691 | 0.022677 | 0.005692 | 1.6316e-06 | 9.9954e-07 | 0.034723 | 0.034723 | 0.034723 | 0.97181 | -0.5434 | 0.97189 | -0.54189 | 9.5393
119 | 0.10363 | 0.02631 | -0.10358 | -0.026279 | 4.8997e-05 | 3.1291e-05 | 0.15686 | 0.15686 | 0.15686 | 0.98383 | -0.30847 | 0.98332 | -0.3183 | 43.0946
120 | -0.024414 | -0.0061273 | 0.024424 | 0.0061333 | 9.6459e-06 | 5.9452e-06 | 0.037382 | 0.037382 | 0.037382 | 0.97189 | -0.54189 | 0.97231 | -0.53361 | 10.2699
121 | 0.04907 | 0.01233 | -0.049068 | -0.012329 | 2.1758e-06 | 1.3797e-06 | 0.075032 | 0.075032 | 0.075032 | 0.97329 | -0.51421 | 0.97325 | -0.51514 | 20.6132
122 | -0.051278 | -0.012884 | 0.051325 | 0.012913 | 4.6784e-05 | 2.9689e-05 | 0.078408 | 0.078407 | 0.078408 | 0.97329 | -0.51421 | 0.97426 | -0.49511 | 21.5405
123 | 0.046582 | 0.011706 | -0.046576 | -0.011702 | 5.5898e-06 | 3.541e-06 | 0.071231 | 0.071231 | 0.071231 | 0.97325 | -0.51514 | 0.97312 | -0.51765 | 19.569
124 | -0.053687 | -0.013505 | 0.053699 | 0.013513 | 1.1273e-05 | 7.159e-06 | 0.082016 | 0.082016 | 0.082016 | 0.97426 | -0.49511 | 0.97449 | -0.49072 | 22.5319
125 | 0.044974 | 0.011301 | -0.044944 | -0.011281 | 3.031e-05 | 1.9186e-05 | 0.068781 | 0.068781 | 0.068781 | 0.97312 | -0.51765 | 0.9724 | -0.53178 | 18.8959
126 | -0.055988 | -0.014086 | 0.055989 | 0.014087 | 1.5121e-06 | 9.6088e-07 | 0.085512 | 0.085512 | 0.085512 | 0.97449 | -0.49072 | 0.97452 | -0.49015 | 23.4922
127 | 0.017979 | 0.0045104 | -0.017968 | -0.004504 | 1.0688e-05 | 6.3735e-06 | 0.027513 | 0.027513 | 0.027513 | 0.9724 | -0.53178 | 0.97177 | -0.54426 | 7.5586
128 | 0.026965 | 0.006771 | -0.026963 | -0.0067696 | 2.3517e-06 | 1.4594e-06 | 0.041268 | 0.041268 | 0.041268 | 0.9724 | -0.53178 | 0.97231 | -0.53361 | 11.3373
129 | -0.058345 | -0.014678 | 0.058404 | 0.014715 | 5.869e-05 | 3.7316e-05 | 0.089109 | 0.089109 | 0.089109 | 0.97452 | -0.49015 | 0.97559 | -0.46912 | 24.4805
130 | 0.016944 | 0.0042475 | -0.01694 | -0.0042453 | 3.5804e-06 | 2.1158e-06 | 0.025946 | 0.025946 | 0.025946 | 0.97177 | -0.54426 | 0.97155 | -0.54869 | 7.128
131 | -0.060414 | -0.015219 | 0.060418 | 0.015221 | 4.2027e-06 | 2.6733e-06 | 0.092175 | 0.092175 | 0.092175 | 0.97559 | -0.46912 | 0.97566 | -0.46767 | 25.3228
132 | 0.0074253 | 0.0018606 | -0.0074249 | -0.0018605 | 3.7975e-07 | 1.4608e-07 | 0.011372 | 0.011372 | 0.011372 | 0.97155 | -0.54869 | 0.97149 | -0.54977 | 3.1243
133 | -0.096419 | -0.024418 | 0.096587 | 0.024525 | 0.00016842 | 0.00010752 | 0.14628 | 0.14628 | 0.14628 | 0.98145 | -0.3546 | 0.98332 | -0.3183 | 40.1855
134 | 0.094443 | 0.023923 | -0.094439 | -0.02392 | 3.6127e-06 | 2.3062e-06 | 0.14328 | 0.14328 | 0.14328 | 0.98145 | -0.3546 | 0.98141 | -0.3554 | 39.3627
135 | 0.090507 | 0.022935 | -0.090354 | -0.022837 | 0.0001529 | 9.7583e-05 | 0.13732 | 0.13732 | 0.13732 | 0.98141 | -0.3554 | 0.9796 | -0.39063 | 37.7246
136 | 0.087267 | 0.022064 | -0.087181 | -0.022008 | 8.6628e-05 | 5.5277e-05 | 0.13263 | 0.13263 | 0.13263 | 0.9796 | -0.39063 | 0.97854 | -0.41135 | 36.4364
137 | 0.082207 | 0.020762 | -0.082102 | -0.020695 | 0.00010486 | 6.6885e-05 | 0.12507 | 0.12507 | 0.12507 | 0.97854 | -0.41135 | 0.97717 | -0.438 | 34.3588
138 | 0.079609 | 0.02007 | -0.079582 | -0.020053 | 2.7474e-05 | 1.7521e-05 | 0.12127 | 0.12127 | 0.12127 | 0.97717 | -0.438 | 0.97681 | -0.44522 | 33.3159
139 | 0.026394 | 0.0066265 | -0.026362 | -0.006607 | 3.1462e-05 | 1.9494e-05 | 0.040325 | 0.040325 | 0.040325 | 0.97404 | -0.49943 | 0.97277 | -0.52445 | 11.0784
140 | -0.062502 | -0.015744 | 0.062517 | 0.015753 | 1.4425e-05 | 9.179e-06 | 0.095353 | 0.095353 | 0.095353 | 0.97566 | -0.46767 | 0.97591 | -0.46284 | 26.196
141 | -0.064829 | -0.016332 | 0.064884 | 0.016367 | 5.4702e-05 | 3.4823e-05 | 0.098879 | 0.098879 | 0.098879 | 0.97591 | -0.46284 | 0.97681 | -0.44522 | 27.1645
142 | 0.014698 | 0.0036856 | -0.014695 | -0.0036839 | 3.0663e-06 | 1.7583e-06 | 0.022391 | 0.022391 | 0.022391 | 0.97681 | -0.44522 | 0.97658 | -0.44959 | 6.1515
143 | 0.006098 | 0.0015279 | -0.0060975 | -0.0015278 | 5.2858e-07 | 1.3824e-07 | 0.00934 | 0.0093401 | 0.0093401 | 0.97149 | -0.54977 | 0.9714 | -0.55159 | 2.566
144 | 0.012495 | 0.0031326 | -0.012493 | -0.0031312 | 2.5986e-06 | 1.424e-06 | 0.01904 | 0.01904 | 0.01904 | 0.97658 | -0.44959 | 0.97636 | -0.45396 | 5.2307
145 | 0.0093147 | 0.0023346 | -0.0093136 | -0.0023341 | 1.0907e-06 | 5.1757e-07 | 0.014196 | 0.014196 | 0.014196 | 0.97636 | -0.45396 | 0.97624 | -0.45642 | 3.9
146 | 0.0042618 | 0.001068 | -0.0042617 | -0.0010681 | 9.9244e-08 | -1.4896e-08 | 0.006496 | 0.0064961 | 0.0064961 | 0.97624 | -0.45642 | 0.97621 | -0.45691 | 1.7846
147 | 0.013586 | 0.0034054 | -0.013584 | -0.0034044 | 1.7612e-06 | 9.9168e-07 | 0.020762 | 0.020762 | 0.020762 | 0.97371 | -0.50604 | 0.97357 | -0.50876 | 5.7038
148 | -0.0020113 | -0.00050409 | 0.0020115 | 0.00050374 | 1.2146e-07 | -3.446e-07 | 0.0030812 | 0.0030811 | 0.0030812 | 0.97133 | -0.55299 | 0.97139 | -0.55172 | 0.8465
149 | -0.0035735 | -0.00089522 | 0.0035735 | 0.00089521 | 2.2733e-08 | -1.0497e-08 | 0.0054738 | 0.0054738 | 0.0054738 | 0.97139 | -0.55172 | 0.9714 | -0.55159 | 1.5038
150 | 0.0022004 | 0.00055142 | -0.0022003 | -0.00055146 | 1.6393e-08 | -3.8094e-08 | 0.0033539 | 0.0033539 | 0.0033539 | 0.97621 | -0.45691 | 0.9762 | -0.45706 | 0.92141

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.62101 | 0.15924

## res_load
| p_mw | q_mvar
0 | 0.014488 | 0.003631
1 | 0.0080943 | 0.0020286
2 | 0.002921 | 0.00073206
3 | 0.0077571 | 0.0019441
4 | 0.0068855 | 0.0017257
5 | 0.0084661 | 0.0021218
6 | 0.0043237 | 0.0010836
7 | 0.0031754 | 0.00079583
8 | 0.0029671 | 0.00074362
9 | 0.0071529 | 0.0017927
10 | 0.001537 | 0.00038522
11 | 0.0026154 | 0.00065549
12 | 0.0043287 | 0.0010849
13 | 0.0041627 | 0.0010433
14 | 0.0015289 | 0.00038317
15 | 0.0030793 | 0.00077175
16 | 0.0021383 | 0.0005359
17 | 0.0031532 | 0.00079027
18 | 0.0029052 | 0.00072811
19 | 0.010192 | 0.0025545
20 | 0.014215 | 0.0035625
21 | 0.019176 | 0.0048059
22 | 0.02293 | 0.0057467
23 | 0.0019058 | 0.00047763
24 | 0.010239 | 0.002566
25 | 0.0024499 | 0.00061399
26 | 0.0032961 | 0.00082607
27 | 0.0036519 | 0.00091526
28 | 0.0099984 | 0.0025058
29 | 0.0023141 | 0.00057996
30 | 0.0092061 | 0.0023073
31 | 0.0034472 | 0.00086395
32 | 0.0041577 | 0.001042
33 | 0.020055 | 0.0050262
34 | 0.0031284 | 0.00078405
35 | 0.0088509 | 0.0022182
36 | 0.0035035 | 0.00087806
37 | 0.0055966 | 0.0014026
38 | 0.0028563 | 0.00071585
39 | 0.0021165 | 0.00053046
40 | 0.0055465 | 0.0013901
41 | 0.006299 | 0.0015787
42 | 0.001475 | 0.00036966
43 | 0.0073063 | 0.0018311
44 | 0.0078386 | 0.0019645
45 | 0.02944 | 0.0073783
46 | 0.0078373 | 0.0019642
47 | 0.0044964 | 0.0011269
48 | 0.0025825 | 0.00064723
49 | 0.0027612 | 0.00069203
50 | 0.0071562 | 0.0017935
51 | 0.0022576 | 0.00056581
52 | 0.0035438 | 0.00088816
53 | 0.0028555 | 0.00071565
54 | 0.016168 | 0.004052
55 | 0.0025911 | 0.00064939
56 | 0.0026622 | 0.00066721
57 | 0.0033316 | 0.00083498
58 | 0.0036852 | 0.0009236
59 | 0.0029614 | 0.00074221
60 | 0.005286 | 0.0013248
61 | 0.0060702 | 0.0015213
62 | 0.0022868 | 0.00057314
63 | 0.010855 | 0.0027206
64 | 0.0088111 | 0.0022083
65 | 0.0031273 | 0.00078377
66 | 0.0055277 | 0.0013854
67 | 0.0076229 | 0.0019105
68 | 0.017138 | 0.0042953
69 | 0.008446 | 0.0021168
70 | 0.0029393 | 0.00073665
71 | 0.0028986 | 0.00072647
72 | 0.0021655 | 0.00054273
73 | 0.0019598 | 0.00049117
74 | 0.0017603 | 0.00044117
75 | 0.0015696 | 0.00039339
76 | 0.0028073 | 0.00070357
77 | 0.0010314 | 0.0002585
78 | 0.0078391 | 0.0019647
79 | 0.0017371 | 0.00043535
80 | 0.0022078 | 0.00055333
81 | 0.0024861 | 0.00062308
82 | 0.0023627 | 0.00059214
83 | 0.0016023 | 0.00040157
84 | 0.0022893 | 0.00057374
85 | 0.002356 | 0.00059048
86 | 0.0010238 | 0.00025659
87 | 0.0025389 | 0.00063631
88 | 0.00201 | 0.00050377
89 | 0.0095152 | 0.0023847
90 | 0.0019755 | 0.0004951
91 | 0.0069978 | 0.0017538
92 | 0.0039326 | 0.00098561
93 | 0.0030868 | 0.00077363
94 | 0.002493 | 0.00062481
95 | 0.0060864 | 0.0015254
96 | 0.026362 | 0.006607
97 | 0.002084 | 0.00052231
98 | 0.0023122 | 0.00057949
99 | 0.0080497 | 0.0020174
100 | 0.0013269 | 0.00033255
101 | 0.0021997 | 0.00055129
102 | 0.0031782 | 0.00079652
103 | 0.0050518 | 0.0012661
104 | 0.0018151 | 0.00045492
105 | 0.013584 | 0.0034044
106 | 0.0020113 | 0.00050409
107 | 0.001562 | 0.00039147
108 | 0.002524 | 0.00063257
109 | 0.0020614 | 0.00051663
110 | 0.0022003 | 0.00055146

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1