## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_131-6_1_2_node_26 | 0.4 | n |  | TRUE
1 | bus_LV_131-6_1_2_node_47 | 0.4 | n |  | TRUE
2 | bus_LV_131-6_1_2_node_24 | 0.4 | n |  | TRUE
3 | bus_LV_131-6_1_2_node_25 | 0.4 | n |  | TRUE
4 | bus_LV_131-6_1_2_node_48 | 0.4 | n |  | TRUE
5 | bus_LV_131-6_1_2_node_19 | 0.4 | n |  | TRUE
6 | bus_LV_131-6_1_2_node_20 | 0.4 | n |  | TRUE
7 | bus_LV_131-6_1_2_node_18 | 0.4 | n |  | TRUE
8 | bus_LV_131-6_1_2_node_44 | 0.4 | n |  | TRUE
9 | bus_LV_131-6_1_2_node_32 | 0.4 | n |  | TRUE
10 | bus_LV_131-6_1_2_node_28 | 0.4 | n |  | TRUE
11 | bus_LV_131-6_1_2_node_34 | 0.4 | n |  | TRUE
12 | bus_LV_131-6_1_2_node_29 | 0.4 | n |  | TRUE
13 | bus_LV_131-6_1_2_node_30 | 0.4 | n |  | TRUE
14 | bus_LV_131-6_1_2_node_43 | 0.4 | n |  | TRUE
15 | bus_LV_131-6_1_2_node_31 | 0.4 | n |  | TRUE
16 | bus_LV_131-6_1_2_node_41 | 0.4 | n |  | TRUE
17 | bus_LV_131-6_1_2_node_39 | 0.4 | n |  | TRUE
18 | bus_LV_131-6_1_2_node_40 | 0.4 | n |  | TRUE
19 | bus_LV_131-6_1_2_node_33 | 0.4 | n |  | TRUE
20 | bus_LV_131-6_1_2_node_42 | 0.4 | n |  | TRUE
21 | bus_LV_131-6_1_2_node_50 | 0.4 | n |  | TRUE
22 | bus_LV_131-6_1_2_node_51 | 0.4 | n |  | TRUE
23 | bus_LV_131-6_1_2_node_53 | 0.4 | n |  | TRUE
24 | bus_MV_360_0_node_39 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_131-6_1_2_load_47 | 1 | 0.051745 | 0.012969 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_131-6_1_2_load_48 | 4 | 0.035417 | 0.0088764 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_131-6_1_2_load_18 | 7 | 0.0080678 | 0.002022 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_131-6_1_2_load_44 | 8 | 0.0075573 | 0.001894 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_131-6_1_2_load_32 | 9 | 0.0016576 | 0.00041543 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_131-6_1_2_load_28 | 10 | 0.00055078 | 0.00013804 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_131-6_1_2_load_34 | 11 | 0.010487 | 0.0026283 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_131-6_1_2_load_30 | 13 | 0.014967 | 0.0037512 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_131-6_1_2_load_43 | 14 | 0.0068821 | 0.0017248 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_131-6_1_2_load_41 | 16 | 0.0075196 | 0.0018846 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_131-6_1_2_load_39 | 17 | 0.0051775 | 0.0012976 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_131-6_1_2_load_33 | 19 | 0.021192 | 0.0053111 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_131-6_1_2_load_51 | 22 | 0.0051159 | 0.0012822 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_131-6_1_2_load_53 | 23 | 0.01349 | 0.0033809 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 14 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_131-6_1_2_line_0 |  | 0 | 1 | 0.057254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_131-6_1_2_line_1 |  | 0 | 2 | 0.068326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_131-6_1_2_line_2 |  | 0 | 3 | 0.11429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_131-6_1_2_line_3 |  | 2 | 4 | 0.039002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_131-6_1_2_line_4 |  | 3 | 8 | 0.020903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_131-6_1_2_line_5 |  | 5 | 6 | 0.050475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_131-6_1_2_line_6 |  | 5 | 7 | 0.014825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_131-6_1_2_line_7 |  | 6 | 9 | 0.028512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_131-6_1_2_line_8 |  | 6 | 10 | 0.0098152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_131-6_1_2_line_9 |  | 8 | 14 | 0.032456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_131-6_1_2_line_10 |  | 9 | 11 | 0.027157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_131-6_1_2_line_11 |  | 10 | 12 | 0.034346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_131-6_1_2_line_12 |  | 11 | 19 | 0.03532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_131-6_1_2_line_13 |  | 12 | 15 | 0.12346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_131-6_1_2_line_14 |  | 12 | 13 | 0.0085249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_131-6_1_2_line_15 |  | 14 | 16 | 0.02793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_131-6_1_2_line_16 |  | 15 | 16 | 0.020973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_131-6_1_2_line_17 |  | 15 | 17 | 0.039945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_131-6_1_2_line_18 |  | 17 | 18 | 0.031699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_131-6_1_2_line_19 |  | 18 | 20 | 0.017616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_131-6_1_2_line_20 |  | 20 | 21 | 0.016813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_131-6_1_2_line_21 |  | 20 | 22 | 0.015553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_131-6_1_2_line_22 |  | 21 | 23 | 0.011102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_131-6_1_2_trafo_43 | 0.63 MVA 20/0.4 kV | 24 | 14 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2682565.5878 | 1241819.626 | 2682622.8422 | 1241819.6468
1 | 2682574.1245 | 1241886.9265 | 2682572.9336 | 1241845.9249 | 2682565.5878 | 1241819.626
2 | 2682525.308 | 1241762.8362 | 2682515.046 | 1241799.3976 | 2682509.5648 | 1241818.9354 | 2682562.3442 | 1241819.6253 | 2682565.5878 | 1241819.626
3 | 2682574.1245 | 1241886.9265 | 2682601.1095 | 1241891.1939 | 2682612.7907 | 1241891.1135
4 | 2682525.308 | 1241762.8362 | 2682527.7924 | 1241748.3825 | 2682529.494 | 1241742.3821
5 | 2682447.3344 | 1241649.6157 | 2682439.7353 | 1241611.5606 | 2682437.0055 | 1241603.4169 | 2682434.5823 | 1241601.5041
6 | 2682434.5823 | 1241601.5041 | 2682437.536 | 1241586.9758
7 | 2682447.3344 | 1241649.6157 | 2682450.5146 | 1241644.9343 | 2682456.5582 | 1241622.8956
8 | 2682447.3344 | 1241649.6157 | 2682448.3633 | 1241659.3768
9 | 2682539.1105 | 1241711.3912 | 2682533.207 | 1241729.2885 | 2682529.494 | 1241742.3821
10 | 2682462.1791 | 1241596.3913 | 2682460.6934 | 1241607.8157 | 2682456.5582 | 1241622.8956
11 | 2682451.9637 | 1241693.5338 | 2682448.3633 | 1241659.3768
12 | 2682466.7338 | 1241561.3658 | 2682462.1791 | 1241596.3913
13 | 2682552.8071 | 1241664.4589 | 2682548.3302 | 1241665.0637 | 2682537.8868 | 1241665.7301 | 2682531.2118 | 1241687.9199 | 2682526.5273 | 1241693.67 | 2682520.0739 | 1241699.3844 | 2682513.1938 | 1241702.6245 | 2682500.1512 | 1241699.919 | 2682451.9637 | 1241693.5338
14 | 2682451.9637 | 1241693.5338 | 2682451.6497 | 1241702.0529
15 | 2682547.2282 | 1241684.6762 | 2682543.6742 | 1241697.5557 | 2682539.1105 | 1241711.3912
16 | 2682552.8071 | 1241664.4589 | 2682547.2282 | 1241684.6762
17 | 2682552.8071 | 1241664.4589 | 2682557.0869 | 1241651.3979 | 2682565.2276 | 1241626.4942
18 | 2682575.0768 | 1241596.3641 | 2682565.2276 | 1241626.4942
19 | 2682557.6518 | 1241595.0541 | 2682565.0434 | 1241596.9027 | 2682575.0768 | 1241596.3641
20 | 2682557.6518 | 1241595.0541 | 2682554.7065 | 1241578.5013
21 | 2682542.2047 | 1241597.2187 | 2682557.6518 | 1241595.0541
22 | 2682544.0606 | 1241581.7556 | 2682554.7065 | 1241578.5013

## bus_geodata
| x | y | coords
0 | 2682565.5878 | 1241819.626
1 | 2682622.8422 | 1241819.6468
2 | 2682574.1245 | 1241886.9265
3 | 2682525.308 | 1241762.8362
4 | 2682612.7907 | 1241891.1135
5 | 2682434.5823 | 1241601.5041
6 | 2682447.3344 | 1241649.6157
7 | 2682437.536 | 1241586.9758
8 | 2682529.494 | 1241742.3821
9 | 2682456.5582 | 1241622.8956
10 | 2682448.3633 | 1241659.3768
11 | 2682462.1791 | 1241596.3913
12 | 2682451.9637 | 1241693.5338
13 | 2682451.6497 | 1241702.053
14 | 2682539.1105 | 1241711.3912
15 | 2682552.8071 | 1241664.4589
16 | 2682547.2282 | 1241684.6762
17 | 2682565.2276 | 1241626.4942
18 | 2682575.0768 | 1241596.3641
19 | 2682466.7338 | 1241561.3658
20 | 2682557.6518 | 1241595.0541
21 | 2682554.7065 | 1241578.5013
22 | 2682542.2047 | 1241597.2187
23 | 2682544.0606 | 1241581.7556
24 | 2682552.8071 | 1241664.4589

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98629 | -0.26259 | 0 | 0
1 | 0.98356 | -0.31582 | 0.051745 | 0.012969
2 | 0.98406 | -0.30605 | 0 | 0
3 | 0.99548 | -0.085733 | 0 | 0
4 | 0.98278 | -0.33095 | 0.035417 | 0.0088764
5 | 0.98766 | -0.2372 | 0 | 0
6 | 0.98803 | -0.22992 | 0 | 0
7 | 0.98755 | -0.23933 | 0.0080678 | 0.002022
8 | 0.99716 | -0.053739 | 0.0075573 | 0.001894
9 | 0.98716 | -0.24691 | 0.0016576 | 0.00041543
10 | 0.98841 | -0.22267 | 0.00055078 | 0.00013804
11 | 0.98637 | -0.26231 | 0.010487 | 0.0026283
12 | 0.98973 | -0.19699 | 0 | 0
13 | 0.98961 | -0.19926 | 0.014967 | 0.0037512
14 | 1 | 0 | -0.18679 | -0.047243
15 | 0.99619 | -0.07274 | 0 | 0
16 | 0.99774 | -0.043053 | 0.0075196 | 0.0018846
17 | 0.99532 | -0.089442 | 0.0051775 | 0.0012976
18 | 0.99479 | -0.099826 | 0 | 0
19 | 0.98568 | -0.27573 | 0.021192 | 0.0053111
20 | 0.99449 | -0.1056 | 0 | 0
21 | 0.99428 | -0.1096 | 0 | 0
22 | 0.99441 | -0.107 | 0.0051159 | 0.0012822
23 | 0.99414 | -0.11224 | 0.01349 | 0.0033809
24 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.051877 | 0.013052 | -0.051745 | -0.012969 | 0.00013158 | 8.3483e-05 | 0.078284 | 0.078284 | 0.078284 | 0.98629 | -0.26259 | 0.98356 | -0.31582 | 21.5067
1 | 0.035533 | 0.0089491 | -0.035459 | -0.0089028 | 7.3679e-05 | 4.6284e-05 | 0.053624 | 0.053625 | 0.053625 | 0.98629 | -0.26259 | 0.98406 | -0.30605 | 14.732
2 | -0.08741 | -0.022001 | 0.088155 | 0.022477 | 0.00074576 | 0.00047581 | 0.13191 | 0.13191 | 0.13191 | 0.98629 | -0.26259 | 0.99548 | -0.085733 | 36.2386
3 | 0.035459 | 0.0089028 | -0.035417 | -0.0088764 | 4.2058e-05 | 2.6422e-05 | 0.053625 | 0.053625 | 0.053625 | 0.98406 | -0.30605 | 0.98278 | -0.33095 | 14.7321
4 | -0.088155 | -0.022477 | 0.088292 | 0.022564 | 0.00013639 | 8.7016e-05 | 0.13191 | 0.13191 | 0.13191 | 0.99548 | -0.085733 | 0.99716 | -0.053739 | 36.2385
5 | -0.0080687 | -0.0020223 | 0.0080715 | 0.0020235 | 2.7971e-06 | 1.1439e-06 | 0.012156 | 0.012156 | 0.012156 | 0.98766 | -0.2372 | 0.98803 | -0.22992 | 3.3397
6 | 0.0080687 | 0.0020223 | -0.0080678 | -0.002022 | 8.2158e-07 | 3.361e-07 | 0.012156 | 0.012156 | 0.012156 | 0.98766 | -0.2372 | 0.98755 | -0.23933 | 3.3397
7 | 0.0334 | 0.0083946 | -0.033373 | -0.0083776 | 2.7063e-05 | 1.6955e-05 | 0.05031 | 0.05031 | 0.05031 | 0.98803 | -0.22992 | 0.98716 | -0.24691 | 13.8215
8 | -0.041472 | -0.010418 | 0.041486 | 0.010427 | 1.4362e-05 | 9.0661e-06 | 0.062466 | 0.062466 | 0.062466 | 0.98803 | -0.22992 | 0.98841 | -0.22267 | 17.1611
9 | -0.095849 | -0.024458 | 0.096098 | 0.024617 | 0.00024953 | 0.00015927 | 0.14319 | 0.14318 | 0.14319 | 0.99716 | -0.053739 | 1 | 0 | 39.3366
10 | 0.031715 | 0.0079622 | -0.031692 | -0.0079476 | 2.328e-05 | 1.4552e-05 | 0.047812 | 0.047812 | 0.047812 | 0.98716 | -0.24691 | 0.98637 | -0.26231 | 13.1351
11 | -0.042037 | -0.010565 | 0.042088 | 0.010598 | 5.1601e-05 | 3.2584e-05 | 0.063296 | 0.063295 | 0.063296 | 0.98841 | -0.22267 | 0.98973 | -0.19699 | 17.3889
12 | 0.021205 | 0.0053194 | -0.021192 | -0.0053111 | 1.3556e-05 | 8.2252e-06 | 0.031991 | 0.031992 | 0.031992 | 0.98637 | -0.26231 | 0.98568 | -0.27573 | 8.7889
13 | -0.057057 | -0.01435 | 0.057398 | 0.014566 | 0.00034083 | 0.00021653 | 0.085801 | 0.0858 | 0.085801 | 0.98973 | -0.19699 | 0.99619 | -0.07274 | 23.5716
14 | 0.014969 | 0.0037521 | -0.014967 | -0.0037512 | 1.6192e-06 | 9.2672e-07 | 0.022505 | 0.022505 | 0.022505 | 0.98973 | -0.19699 | 0.98961 | -0.19926 | 6.1828
15 | 0.089039 | 0.022625 | -0.088855 | -0.022508 | 0.00018416 | 0.0001175 | 0.1326 | 0.1326 | 0.1326 | 1 | 0 | 0.99774 | -0.043053 | 36.4288
16 | -0.081219 | -0.02055 | 0.081335 | 0.020623 | 0.00011589 | 7.3893e-05 | 0.12139 | 0.12139 | 0.12139 | 0.99619 | -0.07274 | 0.99774 | -0.043053 | 33.3479
17 | 0.023821 | 0.0059832 | -0.023802 | -0.0059715 | 1.897e-05 | 1.1621e-05 | 0.035586 | 0.035587 | 0.035587 | 0.99619 | -0.07274 | 0.99532 | -0.089442 | 9.7765
18 | 0.018625 | 0.0046739 | -0.018615 | -0.0046685 | 9.2174e-06 | 5.4874e-06 | 0.027846 | 0.027846 | 0.027846 | 0.99532 | -0.089442 | 0.99479 | -0.099826 | 7.6501
19 | 0.018615 | 0.0046685 | -0.01861 | -0.0046654 | 5.1224e-06 | 3.0497e-06 | 0.027846 | 0.027846 | 0.027846 | 0.99479 | -0.099826 | 0.99449 | -0.1056 | 7.6501
20 | 0.013494 | 0.0033832 | -0.013492 | -0.0033818 | 2.5704e-06 | 1.427e-06 | 0.020191 | 0.020191 | 0.020191 | 0.99449 | -0.1056 | 0.99428 | -0.1096 | 5.5471
21 | 0.0051162 | 0.0012822 | -0.0051159 | -0.0012822 | 3.4179e-07 | 1.696e-08 | 0.0076552 | 0.0076552 | 0.0076552 | 0.99449 | -0.1056 | 0.99441 | -0.107 | 2.1031
22 | 0.013492 | 0.0033818 | -0.01349 | -0.0033809 | 1.6973e-06 | 9.4231e-07 | 0.020191 | 0.020191 | 0.020191 | 0.99428 | -0.1096 | 0.99414 | -0.11224 | 5.5471

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.19367 | 0.048968

## res_load
| p_mw | q_mvar
0 | 0.051745 | 0.012969
1 | 0.035417 | 0.0088764
2 | 0.0080678 | 0.002022
3 | 0.0075573 | 0.001894
4 | 0.0016576 | 0.00041543
5 | 0.00055078 | 0.00013804
6 | 0.010487 | 0.0026283
7 | 0.014967 | 0.0037512
8 | 0.0068821 | 0.0017248
9 | 0.0075196 | 0.0018846
10 | 0.0051775 | 0.0012976
11 | 0.021192 | 0.0053111
12 | 0.0051159 | 0.0012822
13 | 0.01349 | 0.0033809

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1